## Cover
North West Slopes PACR economic assessment
Legend applied throughout the model template
Table Row Name
Input Cell
Calculation cell
Parameter Cell
Output Cell

## Results
| Scenarios |  |  |  |  | S1 | S2 | S3
| General inputs and sensitivities |  |  |  | Unit | Central | Low | High
| Commercial discount rate |  |  |  | % | 5.5% | 7.5% | 1.96%
| VCR |  |  |  | $/MWh | 46882.8857 | 32818.02 | 60947.7513
| Cost inputs and sensitivities |  |  |  | Unit | Central | Low | High
| Network capital costs |  |  |  | Factor | 1 | 1.25 | 0.75
| NNO capital costs |  |  |  | Factor | 1 | 1.25 | 0.75
| Operating and maintenance costs |  |  |  | Factor | 1 | 1 | 1
| Market benefit inputs and sensitivities |  |  |  | Unit | Central | Low | High
| Avoided fuel consumption from generation dispatch |  |  |  | Factor | 1 | 1 | 1
| Avoided voluntary load curtailment |  |  |  | Factor | 1 | 1 | 1
| Avoided involuntary load shedding |  |  |  | Factor | 1 | 1 | 1
| Avoided costs for non RIT-T proponent parties |  |  |  | Factor | 1 | 1 | 1
| Avoided unrelated TNSP expenditure (wood pole replacement) |  |  |  | Factor | 1 | 1 | 1
| Avoided unrelated TNSP expenditure (market benefits) |  |  |  | Factor | 1 | 1 | 1
| Scenario weighting settings |  |  |  | Unit | Central | Low | High
| Scenario weighting |  |  |  | % | 52% | 30% | 18%
Value
| Opex | 1%
NPV results
|  |  | S1 | S2 | S3 |  |  |  |  | Central |  | Low |  | High
| Option | Unit | Central | Low | High | Weighted | Rank | % |  | Rank | % | Rank | % | Rank | %
1A | Option 1A | $NPV | 503.9399 | 9.5388 | 929.8148 | 432.277 | 8 | 84.19% |  | 8 | 81.49% | 1 | 100% | 8 | 87.04%
1B | Option 1B | $NPV | 531.9383 | 9.5388 | 956.7311 | 451.6812 | 7 | 87.97% |  | 7 | 86.02% | 1 | 100% | 5 | 89.56%
2A | Option 2A | $NPV | 242.2391 | -18.5593 | 478.8119 | 206.5827 | 9 | 40.24% |  | 9 | 39.17% | 8 | -194.6% | 9 | 44.82%
2B | Option 2B | $NPV | 227.0521 | -39.8093 | 440.6137 | 185.4347 | 11 | 36.12% |  | 10 | 36.72% | 11 | -417.3% | 11 | 41.24%
2C | Option 2C | $NPV | 211.9627 | -18.5593 | 461.8104 | 187.7787 | 10 | 36.57% |  | 11 | 34.28% | 8 | -194.6% | 10 | 43.23%
2D | Option 2D | $NPV | 183.8739 | -90.0414 | 440.1435 | 147.8278 | 12 | 28.79% |  | 12 | 29.73% | 12 | -944% | 12 | 41.2%
3A | Option 3A | $NPV | 572.908 | -4.7561 | 961.7645 | 469.6029 | 3 | 91.46% |  | 3 | 92.65% | 5 | -49.86% | 4 | 90.03%
3B | Option 3B | $NPV | 550.8331 | 5.1988 | 945.2784 | 458.143 | 4 | 89.23% |  | 5 | 89.08% | 3 | 54.5% | 7 | 88.48%
3C | Option 3C | $NPV | 544.3445 | -4.7561 | 945.8088 | 451.8779 | 6 | 88.01% |  | 6 | 88.03% | 5 | -49.86% | 6 | 88.53%
5A | Option 5A | $NPV | 552.9328 | -33.0784 | 968.6578 | 451.9599 | 5 | 88.03% |  | 4 | 89.42% | 10 | -346.8% | 3 | 90.67%
5B | Option 5B | $NPV | 618.3864 | -1.4016 | 1068.3079 | 513.4359 | 1 | 100% |  | 1 | 100% | 4 | -14.69% | 1 | 100%
5C | Option 5C | $NPV | 601.9586 | -18.2447 | 1048.3096 | 496.2408 | 2 | 96.65% |  | 2 | 97.34% | 7 | -191.3% | 2 | 98.13%
| S1 | Central | [12 empty] | S2 | Low | [11 empty] | S3 | High | [11 empty] | Weighted
| NPV result | Central | [12 empty] | NPV result | Low | [11 empty] | NPV result | High | [11 empty] | NPV result | Weighted
| NPV breakdown | Central | [12 empty] | NPV breakdown | Low | [11 empty] | NPV breakdown | High | [11 empty] | NPV breakdown | Weighted
| Option | Option 1A | Option 1B | Option 2A | Option 2B | Option 2C | Option 2D | Option 3A | Option 3B | Option 3C | Option 5A | Option 5B | Option 5C |  | Option | Option 1A | Option 1B | Option 2A | Option 2B | Option 2C | Option 2D | Option 3A | Option 3B | Option 3C | Option 5A | Option 5B | Option 5C | Option | Option 1A | Option 1B | Option 2A | Option 2B | Option 2C | Option 2D | Option 3A | Option 3B | Option 3C | Option 5A | Option 5B | Option 5C | Option | Option 1A | Option 1B | Option 2A | Option 2B | Option 2C | Option 2D | Option 3A | Option 3B | Option 3C | Option 5A | Option 5B | Option 5C
| TNSP capital costs | -175.4653 | -153.598 | -101.615 | -83.5968 | -130.8078 | -153.831 | -87.7325 | Redacted to preserve confidentiality | -115.4265 | Redacted to preserve confidentiality |  |  |  | TNSP capital costs | -72.0629 | -72.0629 | -57.4669 | -73.5809 | -57.4669 | -124.1659 | -79.2393 | Redacted to preserve confidentiality | -79.2393 | Redacted to preserve confidentiality |  |  | TNSP capital costs | -112.1602 | -94.0744 | -63.9243 | -50.3308 | -79.2043 | -93.4269 | -53.3074 | Redacted to preserve confidentiality | -67.7955 | Redacted to preserve confidentiality |  |  | TNSP capital costs | -133.0496 | -118.4232 | -81.5863 | -74.6041 | -99.5169 | -134.0587 | -78.988 | Redacted to preserve confidentiality | -95.9968 | Redacted to preserve confidentiality
| NNO capital costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  |  | NNO capital costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  | NNO capital costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  | NNO capital costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality
| TNSP operating expenditure | -22.9713 | -16.8402 | -11.6535 | -8.9201 | -12.7371 | -17.8027 | -12.8014 | Redacted to preserve confidentiality | -13.6709 | Redacted to preserve confidentiality |  |  |  | TNSP operating expenditure | -6.3312 | -6.3312 | -3.386 | -4.3375 | -3.386 | -8.1691 | -7.722 | Redacted to preserve confidentiality | -7.722 | Redacted to preserve confidentiality |  |  | TNSP operating expenditure | -33.5034 | -24.6729 | -17.344 | -13.2951 | -19.0656 | -26.5099 | -18.3769 | Redacted to preserve confidentiality | -19.8444 | Redacted to preserve confidentiality |  |  | TNSP operating expenditure | -19.8751 | -15.0974 | -10.1975 | -8.3328 | -11.0709 | -16.4799 | -12.2811 | Redacted to preserve confidentiality | -12.9974 | Redacted to preserve confidentiality
| TNSP payments to NNO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  |  | TNSP payments to NNO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  | TNSP payments to NNO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  | TNSP payments to NNO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality
| NNO operating expenditure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  |  | NNO operating expenditure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  | NNO operating expenditure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  | NNO operating expenditure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality
| Avoided fuel consumption from generation dispatch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  |  | Avoided fuel consumption from generation dispatch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  | Avoided fuel consumption from generation dispatch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  | Avoided fuel consumption from generation dispatch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality
| Avoided voluntary load curtailment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  |  | Avoided voluntary load curtailment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  | Avoided voluntary load curtailment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  | Avoided voluntary load curtailment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality
| Avoided involuntary load shedding outside of NW Slopes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  |  | Avoided involuntary load shedding outside of NW Slopes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  | Avoided involuntary load shedding outside of NW Slopes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  | Avoided involuntary load shedding outside of NW Slopes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality
| Avoided involuntary load shedding in NW Slopes | 702.3765 | 702.3765 | 355.5077 | 318.8109 | 355.5077 | 355.5077 | 672.6715 | Redacted to preserve confidentiality | 672.6715 | Redacted to preserve confidentiality |  |  |  | Avoided involuntary load shedding in NW Slopes | 87.9328 | 87.9328 | 42.2936 | 37.3788 | 42.2936 | 42.2936 | 81.4606 | Redacted to preserve confidentiality | 81.4606 | Redacted to preserve confidentiality |  |  | Avoided involuntary load shedding in NW Slopes | 1075.4784 | 1075.4784 | 560.0802 | 503.4975 | 560.0802 | 560.0802 | 1032.6983 | Redacted to preserve confidentiality | 1032.6983 | Redacted to preserve confidentiality |  |  | Avoided involuntary load shedding in NW Slopes | 585.2017 | 585.2017 | 298.3665 | 267.6248 | 298.3665 | 298.3665 | 560.1131 | Redacted to preserve confidentiality | 560.1131 | Redacted to preserve confidentiality
| Avoided costs for non RIT-T proponent parties | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  |  | Avoided costs for non RIT-T proponent parties | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  | Avoided costs for non RIT-T proponent parties | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  | Avoided costs for non RIT-T proponent parties | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality
| Avoided unrelated TNSP expenditure (wood pole replacement) | 0 | 0 | 0 | 0.75808 | 0 | 0 | 0.77033 | Redacted to preserve confidentiality | 0.77033 | Redacted to preserve confidentiality |  |  |  | Avoided unrelated TNSP expenditure (wood pole replacement) | 0 | 0 | 0 | 0.73027 | 0 | 0 | 0.74461 | Redacted to preserve confidentiality | 0.74461 | Redacted to preserve confidentiality |  |  | Avoided unrelated TNSP expenditure (wood pole replacement) | 0 | 0 | 0 | 0.74203 | 0 | 0 | 0.75035 | Redacted to preserve confidentiality | 0.75035 | Redacted to preserve confidentiality |  |  | Avoided unrelated TNSP expenditure (wood pole replacement) | 0 | 0 | 0 | 0.74685 | 0 | 0 | 0.75902 | Redacted to preserve confidentiality | 0.75902 | Redacted to preserve confidentiality
| Avoided unrelated TNSP expenditure (market benefits) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  |  | Avoided unrelated TNSP expenditure (market benefits) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  | Avoided unrelated TNSP expenditure (market benefits) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  | Avoided unrelated TNSP expenditure (market benefits) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality
| NNO receipts received from TNSP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  |  | NNO receipts received from TNSP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  | NNO receipts received from TNSP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality |  |  | NNO receipts received from TNSP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality | 0 | Redacted to preserve confidentiality
| NPV | 503.9399 | 531.9383 | 242.2391 | 227.0521 | 211.9627 | 183.8739 | 572.908 | 550.8331 | 544.3445 | 552.9328 | 618.3864 | 601.9586 |  | NPV | 9.5388 | 9.5388 | -18.5593 | -39.8093 | -18.5593 | -90.0414 | -4.7561 | 5.1988 | -4.7561 | -33.0784 | -1.4016 | -18.2447 | NPV | 929.8148 | 956.7311 | 478.8119 | 440.6137 | 461.8104 | 440.1435 | 961.7645 | 945.2784 | 945.8088 | 968.6578 | 1068.3079 | 1048.3096 | NPV | 432.277 | 451.6812 | 206.5827 | 185.4347 | 187.7787 | 147.8278 | 469.6029 | 458.143 | 451.8779 | 451.9599 | 513.4359 | 496.2408
| Benefit time series | Central | [12 empty] | Benefit time series | Low | [11 empty] | Benefit time series | High | [11 empty] | Benefit time series | Weighted
Tiled chart
Sensitivities
High discount rate (central scenario)
|  | 1A | 443.8085
|  | 1B | 470.3207
|  | 2A | 206.9658
|  | 2B | 193.6005
|  | 2C | 175.2017
|  | 2D | 146.9101
|  | 3A | 513.3773
|  | 3B | 492.4145
|  | 3C | 483.5266
|  | 5A | 500.7991
|  | 5B | 553.4902
|  | 5C | 539.0737
Low discount rate (central scenario)
|  | 1A | 644.2407
|  | 1B | 677.1857
|  | 2A | 328.2545
|  | 2B | 307.645
|  | 2C | 306.1597
|  | 2D | 279.7519
|  | 3A | 705.6803
|  | 3B | 682.053
|  | 3C | 684.8952
|  | 5A | 668.4449
|  | 5B | 763.1998
|  | 5C | 742.2879

## Chart tables (hidden)
Chart tables
First ranked option |  | Option 5B
Real
Option 5B | Central |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Avoided fuel consumption from generation dispatch |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Avoided voluntary load curtailment |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Avoided involuntary load shedding |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Avoided costs for non RIT-T proponent parties |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Avoided unrelated TNSP expenditure (market benefits) |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Option 5B | Low |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Avoided fuel consumption from generation dispatch |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided voluntary load curtailment |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided involuntary load shedding |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided costs for non RIT-T proponent parties |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (market benefits) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Option 5B | High |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Avoided fuel consumption from generation dispatch |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided voluntary load curtailment |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided involuntary load shedding |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided costs for non RIT-T proponent parties |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (market benefits) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Option 5B | #REF! |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Avoided fuel consumption from generation dispatch |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided voluntary load curtailment |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided involuntary load shedding |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided costs for non RIT-T proponent parties |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (market benefits) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Discounted |  |  | 1 | 0.94787 | 0.89845 | 0.85161 | 0.80722 | 0.76513 | 0.72525 | 0.68744 | 0.6516 | 0.61763 | 0.58543 | 0.55491 | 0.52598 | 0.49856 | 0.47257 | 0.44793 | 0.42458 | 0.40245 | 0.38147 | 0.36158 | 0.34273 | 0.32486 | 0.30793 | 0.29187 | 0.27666 | 0.26223 | 0.24856 | 0.2356 | 0.22332 | 0.21168
Option 5B | Central |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Avoided fuel consumption from generation dispatch |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Avoided voluntary load curtailment |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Avoided involuntary load shedding |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Avoided costs for non RIT-T proponent parties |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Avoided unrelated TNSP expenditure (market benefits) |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Option 5B | Low |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Avoided fuel consumption from generation dispatch |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided voluntary load curtailment |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided involuntary load shedding |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided costs for non RIT-T proponent parties |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (market benefits) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Option 5B | High |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Avoided fuel consumption from generation dispatch |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided voluntary load curtailment |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided involuntary load shedding |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided costs for non RIT-T proponent parties |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (market benefits) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Option 5B | #REF! |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Avoided fuel consumption from generation dispatch |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided voluntary load curtailment |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided involuntary load shedding |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided costs for non RIT-T proponent parties |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (market benefits) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Discounted |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5B | Central |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Avoided fuel consumption from generation dispatch |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Avoided voluntary load curtailment |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Avoided involuntary load shedding |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Avoided costs for non RIT-T proponent parties |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Avoided unrelated TNSP expenditure (market benefits) |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Option 5B | Low |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Avoided fuel consumption from generation dispatch |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided voluntary load curtailment |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided involuntary load shedding |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided costs for non RIT-T proponent parties |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (market benefits) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Option 5B | High |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Avoided fuel consumption from generation dispatch |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided voluntary load curtailment |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided involuntary load shedding |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided costs for non RIT-T proponent parties |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (market benefits) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Option 5B | #REF! |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Avoided fuel consumption from generation dispatch |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided voluntary load curtailment |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided involuntary load shedding |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided costs for non RIT-T proponent parties |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (market benefits) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## General inputs
General parameters and options inputs
General parameters
Parameter | Unit | Value
First year of analysis | Year | 2023
Discount year | Year | 2023
Analysis period | Years | 20
Option inputs
Options | Stage | Short description
Base |  | No investment
Option 1A | 1 | 3rd Narrabri Tx
Option 1A | 1 | Upgrade 969 line to 160 MVA rating
Option 1A | 1 | 50 MVAr SVC Gunnedah
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating
Option 1A | 1 | Upgrade 968 line to 160 MVA rating
Option 1A | 2 | 60 MVAr SVC at Narrabri
Option 1B | 1 | 3rd Narrabri Tx
Option 1B | 1 | Upgrade 969 line to 160 MVA rating
Option 1B | 1 | 50 MVAr SVC Gunnedah
Option 1B | 1 | Upgrade 9UH line to 100 MVA rating
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri
Option 2A | 1 | 3rd Narrabri Tx
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah
Option 2A | 1 | Upgrade 969 line to 135 MVA rating
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating
Option 2A | 2 | 50 MVAr SVC Narrabri 132
Option 2B | 1 | 3rd Narrabri Tx
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating
Option 2B | 2 | 50 MVAr SVC Narrabri 132
Option 2C | 1 | 3rd Narrabri Tx
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri
Option 2D | 1 | 3rd Narrabri Tx
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV
Option 2D | 1 | Upgrade 969 line to 135 MVA rating
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating
Option 2D | 2 | 50 MVAr SVC Narrabri 132
Option 3A | 1 | 3rd Narrabri Tx
Option 3A | 1 | Rebuild 969 line as double circuit
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating
Option 3A | 2 | 60 MVAr SVC at Narrabri 132
Option 3B | 1 | 3rd Narrabri Tx
Option 3B | 1 | Rebuild 969 line as double circuit
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating
Option 3B | 2 | Install 50 MW / 50 MWh BESS at Narrabri 132
Option 3C | 1 | 3rd Narrabri Tx
Option 3C | 1 | Rebuild 969 line as double circuit
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri
Option 5A | 1 | 3rd Narrabri Tx
Option 5A | 1 | BESS at Gunnedah
Option 5A
Option 5A
Option 5A
Option 5A | 2 | Rebuild 969 line as double circuit
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating
Option 5B | 1 | 3rd Narrabri Tx
Option 5B | 1 | BESS near Gunnedah
Option 5B | 2 | Rebuild 969 line as double circuit
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating
Option 5C | 1 | 3rd Narrabri Tx
Option 5C | 1 | BESS at Gunnedah
Option 5C
Option 5C | 2 | Rebuild 969 line as double circuit
Option 5C | 2 | Upgrade 9UH line to 100 MVA rating
Cost and benefit categories |  |  | Scenarios
Cost categories |  |  | Scenario | Name
Capital costs |  |  | S1 | Central
Operating and maintenance costs |  |  | S2 | Low
|  |  | S3 | High
Benefit categories
Avoided fuel consumption from generation dispatch
Avoided voluntary load curtailment
Avoided involuntary load shedding
Avoided costs for non RIT-T proponent parties
Avoided unrelated TNSP expenditure (wood pole replacement)
Avoided unrelated TNSP expenditure (market benefits)
NNO receipts received from TNSP

## CBA inputs
CBA cost inputs
All years in the input sheet are expressed as financial years. ie 2023 refers to FY2022/23 that covers the period from 1 July 2022 to 30 June 2023
Capital costs |  |  | S1 | S2 | S3
Option name | Stage | Capex component | Commission year - central | Commission year - low | Commission year - high | Asset life | 1 if TNSP owns asset | Amount | Build year 1 | Build year 2 | Build year 3 | Build year 4 | Build year 5 | Build year 6 | Build year 7 | Build year 8 | Build year 9 | Build year 10 | Build year 11 | Build year 12 | Build year 13 | Build year 14 | Build year 15 | Build year 16 | Build year 17 | Build year 18 | Build year 19 | Build year 20
Option 1A | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 562958.6578 | 3286846.5899 | 4322374.4822
Option 1A | 1 | Upgrade 969 line to 160 MVA rating | 2026 | 2026 | 2026 | 35 | 1 | 50949682.23 | 466189.595 | 1313773.949 | 49169718.686
Option 1A | 1 | 50 MVAr SVC Gunnedah | 2026 | 2026 | 2026 | 40 | 1 | 18433159.02 | 1270571.3167 | 6682283.4849 | 10480304.2184
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating | 2029 | #N/A | 2029 | 35 | 1 | 27991844.69 | 176326.0359 | 302125.5852 | 916273.6337 | 10037009.3916 | 16560110.0435
Option 1A | 1 | Upgrade 968 line to 160 MVA rating | 2028 | #N/A | 2028 | 35 | 1 | 148683015.7 | 906966.4008 | 1440809.2298 | 2842677.6499 | 97336044.2365 | 46156518.1829
Option 1A | 2 | 60 MVAr SVC at Narrabri | 2030 | #N/A | 2030 | 40 | 1 | 19661063.47 | 1047577.2064 | 6968417.1091 | 11645069.1544
Option 1B | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 562958.6578 | 3286846.5899 | 4322374.4822
Option 1B | 1 | Upgrade 969 line to 160 MVA rating | 2026 | 2026 | 2026 | 35 | 1 | 50949682.23 | 466189.595 | 1313773.949 | 49169718.686
Option 1B | 1 | 50 MVAr SVC Gunnedah | 2026 | 2026 | 2026 | 40 | 1 | 18433159.02 | 1270571.3167 | 6682283.4849 | 10480304.2184
Option 1B | 1 | Upgrade 9UH line to 100 MVA rating | 2027 | #N/A | 2027 | 35 | 1 | 27991844.69 | 176326.0359 | 302125.5852 | 916273.6337 | 10037009.3916 | 16560110.0435
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 102474742.77 | 291443.7217 | 538986.4355 | 1694034.4788 | 17053922.7396 | 30893655.2791 | 52002700.1153
Option 2A | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 562958.6578 | 3286846.5899 | 4322374.4822
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 2029 | 2029 | 2029 | 50 | 1 | 45979704.8847 | 304770.178 | 540678.4002 | 1838846.5297 | 15373872.4983 | 27921537.2786
Option 2A | 1 | Upgrade 969 line to 135 MVA rating | 2028 | #N/A | 2028 | 35 | 1 | 50949682.21 | 290073.5228 | 384387.0441 | 909168.7657 | 11910563.8167 | 37455489.0607
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating | 2029 | #N/A | 2029 | 35 | 1 | 27991844.69 | 176326.0359 | 302125.5852 | 916273.6337 | 10037009.3916 | 16560110.0435
Option 2A | 2 | 50 MVAr SVC Narrabri 132 | 2030 | #N/A | 2030 | 40 | 1 | 19661063 | 1047577 | 6968417 | 11645069
Option 2B | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 562958.6578 | 3286846.5899 | 4322374.4822
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 2029 | 2029 | 2029 | 50 | 1 | 62070491.37 | 320034.0032 | 571518.4188 | 1782611.1821 | 15944119.0011 | 38721538.8356 | 4730669.9292
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating | 2028 | #N/A | 2028 | 35 | 1 | 27991844.69 | 176326.0359 | 302125.5852 | 916273.6337 | 10037009.3916 | 16560110.0435
Option 2B | 2 | 50 MVAr SVC Narrabri 132 | 2030 | #N/A | 2030 | 40 | 1 | 19661063 | 1047577 | 6968417 | 11645069
Option 2C | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 562958.6578 | 3286846.5899 | 4322374.4822
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 2029 | 2029 | 2029 | 50 | 1 | 45979704.8847 | 304770.178 | 540678.4002 | 1838846.5297 | 15373872.4983 | 27921537.2786
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating | 2028 | #N/A | 2028 | 35 | 1 | 50949682.21 | 290073.5228 | 384387.0441 | 909168.7657 | 11910563.8167 | 37455489.0607
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 67112099.47 | 280164.9931 | 581512.839 | 2019198.3822 | 19947050.7231 | 42769235.622 | 1514936.9106
Option 2D | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 562958.6578 | 3286846.5899 | 4322374.4822
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 2029 | 2029 | 2029 | 50 | 1 | 126867927.18 | 367611.5549 | 900058.0332 | 3182788.6187 | 20107254.8947 | 99355949.4593 | 2954264.6191
Option 2D | 1 | Upgrade 969 line to 135 MVA rating | 2028 | #N/A | 2028 | 35 | 1 | 50949682.21 | 290073.5228 | 384387.0441 | 909168.7657 | 11910563.8167 | 37455489.0607
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating | 2028 | #N/A | 2028 | 35 | 1 | 27991844.69 | 176326.0359 | 302125.5852 | 916273.6337 | 10037009.3916 | 16560110.0435
Option 2D | 2 | 50 MVAr SVC Narrabri 132 | 2030 | #N/A | 2030 | 40 | 1 | 19661063 | 1047577 | 6968417 | 11645069
Option 3A | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 562958.6578 | 3286846.5899 | 4322374.4822
Option 3A | 1 | Rebuild 969 line as double circuit | 2026 | 2026 | 2026 | 50 | 1 | 86418857.86 | 1041254.0248 | 2755096.888 | 21687177.713 | 60935329.2341
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating | 2028 | #N/A | 2028 | 35 | 1 | 27991844.69 | 176326.0359 | 302125.5852 | 916273.6337 | 10037009.3916 | 16560110.0435
Option 3A | 2 | 60 MVAr SVC at Narrabri 132 | 2030 | #N/A | 2030 | 40 | 1 | 19661063 | 1047577 | 6968417 | 11645069
Option 3B | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 562958.6578 | 3286846.5899 | 4322374.4822
Option 3B | 1 | Rebuild 969 line as double circuit | 2026 | 2026 | 2026 | 50 | 1 | 86418857.86 | 1041254.0248 | 2755096.888 | 21687177.713 | 60935329.2341
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating | 2028 | #N/A | 2028 | 35 | 1 | 27991844.69 | 176326.0359 | 302125.5852 | 916273.6337 | 10037009.3916 | 16560110.0435
Option 3B | 2 | Install 50 MW / 50 MWh BESS at Narrabri 132 | 2030 | #N/A | 2030 | 20 | 1 |  | Redacted to preserve confidentiality
Option 3C | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 562958.6578 | 3286846.5899 | 4322374.4822
Option 3C | 1 | Rebuild 969 line as double circuit | 2026 | 2026 | 2026 | 50 | 1 | 86418857.86 | 1041254.0248 | 2755096.888 | 21687177.713 | 60935329.2341
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 67112099.47 | 280164.9931 | 581512.839 | 2019198.3822 | 19947050.7231 | 42769235.622 | 1514936.9106
Option 5A | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 562958.6578 | 3286846.5899 | 4322374.4822
Option 5A | 1 | BESS at Gunnedah | Redacted to preserve confidentiality |  |  |  | 0 |  | Redacted to preserve confidentiality
Option 5A | 2 | Rebuild 969 line as double circuit | 2030 | #N/A | 2030 | 50 | 1 | 86418857.86 | 1041254.0248 | 2755096.888 | 21687177.713 | 60935329.2341
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating | 2030 | #N/A | 2030 | 35 | 1 | 27991844.69 | 176326.0359 | 302125.5852 | 916273.6337 | 10037009.3916 | 16560110.0435
Option 5B | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 562958.6578 | 3286846.5899 | 4322374.4822
Option 5B | 1 | BESS near Gunnedah | Redacted to preserve confidentiality |  |  |  | 0 |  | Redacted to preserve confidentiality
Option 5B | 2 | Rebuild 969 line as double circuit | 2030 | #N/A | 2030 | 50 | 1 | 86418857.86 | 1041254.0248 | 2755096.888 | 21687177.713 | 60935329.2341
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating | 2030 | #N/A | 2030 | 35 | 1 | 27991844.69 | 176326.0359 | 302125.5852 | 916273.6337 | 10037009.3916 | 16560110.0435
Option 5C | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 562958.6578 | 3286846.5899 | 4322374.4822
Option 5C | 1 | BESS at Gunnedah | Redacted to preserve confidentiality |  |  |  | 0 |  | Redacted to preserve confidentiality
Option 5C | 2 | Rebuild 969 line as double circuit | 2030 | #N/A | 2030 | 50 | 1 | 86418857.86 | 1041254.0248 | 2755096.888 | 21687177.713 | 60935329.2341
Option 5C | 2 | Upgrade 9UH line to 100 MVA rating | 2030 | #N/A | 2030 | 35 | 1 | 27991844.69 | 176326.0359 | 302125.5852 | 916273.6337 | 10037009.3916 | 16560110.0435
Biodiversity offset costs
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 12600000 | 0 | 0 | 0 | 12600000 | 0 | 0
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 2029 | 2029 | 2029 | 50 | 1 | 8100000 | 0 | 0 | 0 | 8100000 | 0
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 2029 | 2029 | 2029 | 50 | 1 | 8100000 | 0 | 0 | 0 | 8100000 | 0 | 0
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 2029 | 2029 | 2029 | 50 | 1 | 8100000 | 0 | 0 | 0 | 8100000 | 0
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 15800000 | 0 | 0 | 0 | 15800000 | 0 | 0
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 2029 | 2029 | 2029 | 50 | 1 | 8100000 | 0 | 0 | 0 | 8100000 | 0 | 0
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 15800000 | 0 | 0 | 0 | 15800000 | 0 | 0
Property allowances
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 44720000 | 0 | 0 | 0 | 35000000 | 9720000 | 0
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 2029 | 2029 | 2029 | 50 | 1 | 19200000 | 0 | 0 | 0 | 10000000 | 9200000
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 2029 | 2029 | 2029 | 50 | 1 | 19200000 | 0 | 0 | 0 | 10000000 | 9200000 | 0
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 2029 | 2029 | 2029 | 50 | 1 | 19200000 | 0 | 0 | 0 | 10000000 | 9200000
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 23140000 | 0 | 0 | 0 | 10000000 | 13140000 | 0
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 2029 | 2029 | 2029 | 50 | 1 | 24340000 | 0 | 0 | 0 | 15000000 | 9340000 | 0
Option 3A | 1 | Rebuild 969 line as double circuit | 2026 | 2026 | 2026 | 50 | 1 | 333278 | 0 | 0 | 333278 | 0
Option 3B | 1 | Rebuild 969 line as double circuit | 2026 | 2026 | 2026 | 50 | 1 | 333278 | 0 | 0 | 333278 | 0
Option 3C | 1 | Rebuild 969 line as double circuit | 2026 | 2026 | 2026 | 50 | 1 | 333278 | 0 | 0 | 333278 | 0
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 23140000 | 0 | 0 | 0 | 10000000 | 13140000 | 0
Option 5A | 2 | Rebuild 969 line as double circuit | 2030 | #N/A | 2030 | 50 | 1 | 333278 | 0 | 0 | 333278 | 0
Option 5B | 2 | Rebuild 969 line as double circuit | 2030 | #N/A | 2030 | 50 | 1 | 333278 | 0 | 0 | 333278 | 0
Option 5C | 2 | Rebuild 969 line as double circuit | 2030 | #N/A | 2030 | 50 | 1 | 333278 | 0 | 0 | 333278 | 0
Operating and maintenance costs
Option | Stage | Capex component |  | TNSP owned |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | 1 | 3rd Narrabri Tx |  | 1 |  | $ | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973
Option 1A | 1 | Upgrade 969 line to 160 MVA rating |  | 1 |  | $ | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223
Option 1A | 1 | 50 MVAr SVC Gunnedah |  | 1 |  | $ | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating |  | 1 |  | $ | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469
Option 1A | 1 | Upgrade 968 line to 160 MVA rating |  | 1 |  | $ | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157
Option 1A | 2 | 60 MVAr SVC at Narrabri |  | 1 |  | $ | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347
Option 1B | 1 | 3rd Narrabri Tx |  | 1 |  | $ | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973
Option 1B | 1 | Upgrade 969 line to 160 MVA rating |  | 1 |  | $ | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223
Option 1B | 1 | 50 MVAr SVC Gunnedah |  | 1 |  | $ | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902
Option 1B | 1 | Upgrade 9UH line to 100 MVA rating |  | 1 |  | $ | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri |  | 1 |  | $ | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277
Option 2A | 1 | 3rd Narrabri Tx |  | 1 |  | $ | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah |  | 1 |  | $ | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488
Option 2A | 1 | Upgrade 969 line to 135 MVA rating |  | 1 |  | $ | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating |  | 1 |  | $ | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469
Option 2A | 2 | 50 MVAr SVC Narrabri 132 |  | 1 |  | $ | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63
Option 2B | 1 | 3rd Narrabri Tx |  | 1 |  | $ | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line |  | 1 |  | $ | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating |  | 1 |  | $ | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469
Option 2B | 2 | 50 MVAr SVC Narrabri 132 |  | 1 |  | $ | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63
Option 2C | 1 | 3rd Narrabri Tx |  | 1 |  | $ | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah |  | 1 |  | $ | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating |  | 1 |  | $ | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri |  | 1 |  | $ | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947
Option 2D | 1 | 3rd Narrabri Tx |  | 1 |  | $ | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV |  | 1 |  | $ | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718
Option 2D | 1 | Upgrade 969 line to 135 MVA rating |  | 1 |  | $ | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating |  | 1 |  | $ | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469
Option 2D | 2 | 50 MVAr SVC Narrabri 132 |  | 1 |  | $ | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63
Option 3A | 1 | 3rd Narrabri Tx |  | 1 |  | $ | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973
Option 3A | 1 | Rebuild 969 line as double circuit |  | 1 |  | $ | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating |  | 1 |  | $ | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469
Option 3A | 2 | 60 MVAr SVC at Narrabri 132 |  | 1 |  | $ | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63
Option 3B | 1 | 3rd Narrabri Tx |  | 1 |  | $ | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973
Option 3B | 1 | Rebuild 969 line as double circuit |  | 1 |  | $ | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating |  | 1 |  | $ | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469
Option 3B | 2 | Install 50 MW / 50 MWh BESS at Narrabri 132 |  | 1 |  | $ | Redacted to preserve confidentiality
Option 3C | 1 | 3rd Narrabri Tx |  | 1 |  | $ | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973
Option 3C | 1 | Rebuild 969 line as double circuit |  | 1 |  | $ | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri |  | 1 |  | $ | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947
Option 5A | 1 | 3rd Narrabri Tx |  | 1 |  | $ | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973
Option 5A | 1 | BESS at Gunnedah |  | 0 |  | $ | Redacted to preserve confidentiality
Option 5A | 2 | Rebuild 969 line as double circuit |  | 1 |  | $ | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating |  | 1 |  | $ | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469
Option 5B | 1 | 3rd Narrabri Tx |  | 1 |  | $ | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973
Option 5B | 1 | BESS near Gunnedah |  | 0 |  | $ | Redacted to preserve confidentiality
Option 5B | 2 | Rebuild 969 line as double circuit |  | 1 |  | $ | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating |  | 1 |  | $ | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469
Option 5C | 1 | 3rd Narrabri Tx |  | 1 |  | $ | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973
Option 5C | 1 | BESS at Gunnedah |  | 0 |  | $ | Redacted to preserve confidentiality
Option 5C | 2 | Rebuild 969 line as double circuit |  | 1 |  | $ | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786
Option 5C | 2 | Upgrade 9UH line to 100 MVA rating |  | 1 |  | $ | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469
Biodiversity offset costs
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Property allowances
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | 1 | Rebuild 969 line as double circuit |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | 1 | Rebuild 969 line as double circuit |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 1 | Rebuild 969 line as double circuit |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | 2 | Rebuild 969 line as double circuit |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5B | 2 | Rebuild 969 line as double circuit |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5C | 2 | Rebuild 969 line as double circuit |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSNP network service payments to NNO proponents (opex)
Option | [5 empty] | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $
Option 3C | [5 empty] | $
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
NNO receipts received from TNSP
Option | [5 empty] | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $
Option 3C | [5 empty] | $
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
CBA benefit inputs
Avoided fuel consumption from generation dispatch
Option name |  | S1 | Central |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Option name |  | S2 | Low |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Option name |  | S3 | High |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Avoided voluntary load curtailment
Option name |  | S1 | Central |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Option name |  | S2 | Low |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Option name |  | S3 | High |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Avoided involuntary load shedding outside of NW Slopes
Option name |  | S1 | Central |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Option name |  | S2 | Low |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Option name |  | S3 | High |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Avoided involuntary load shedding in NW Slopes
Option name |  | S1 | Central |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 5236 | 6550 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1A | [5 empty] | MWh | 0 | 0 | 253 | 935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B | [5 empty] | MWh | 0 | 0 | 253 | 935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | [5 empty] | MWh | 0 | 0 | 253 | 1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | [5 empty] | MWh | Redacted to preserve confidentiality
Option 3C | [5 empty] | MWh | 0 | 0 | 253 | 1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | [5 empty] | MWh | Redacted to preserve confidentiality
Option 5B | [5 empty] | MWh | Redacted to preserve confidentiality
Option 5C | [5 empty] | MWh | Redacted to preserve confidentiality
Option name |  | S2 | Low |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | MWh | 0 | 0 | 0 | 577 | 1036 | 1068 | 1073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1A | [5 empty] | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B | [5 empty] | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | [5 empty] | MWh | 0 | 0 | 0 | 577 | 1036 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | [5 empty] | MWh | 0 | 0 | 0 | 577 | 1036 | 431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | [5 empty] | MWh | 0 | 0 | 0 | 577 | 1036 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | [5 empty] | MWh | 0 | 0 | 0 | 577 | 1036 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | [5 empty] | MWh | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | [5 empty] | MWh | Redacted to preserve confidentiality
Option 3C | [5 empty] | MWh | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | [5 empty] | MWh | Redacted to preserve confidentiality
Option 5B | [5 empty] | MWh | Redacted to preserve confidentiality
Option 5C | [5 empty] | MWh | Redacted to preserve confidentiality
Option name |  | S3 | High |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 5236 | 6550 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1A | [5 empty] | MWh | 0 | 0 | 253 | 935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B | [5 empty] | MWh | 0 | 0 | 253 | 935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | [5 empty] | MWh | 0 | 0 | 253 | 1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | [5 empty] | MWh | Redacted to preserve confidentiality
Option 3C | [5 empty] | MWh | 0 | 0 | 253 | 1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | [5 empty] | MWh | Redacted to preserve confidentiality
Option 5B | [5 empty] | MWh | Redacted to preserve confidentiality
Option 5C | [5 empty] | MWh | Redacted to preserve confidentiality
Avoided costs for non RIT-T proponent parties
Option name |  | S1 | Central |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Option name |  | S2 | Low |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Option name |  | S3 | High |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (wood pole replacement)
Option name |  | S1 | Central |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 1A | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 1B | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 2A | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 2B | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 2D | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 3A | [5 empty] | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Option name |  | S2 | Low |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $ | 0 | 0 | 0 | 0 | 9925.0392 | 9925.0392 | 9925.0392 | 9925.0392 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 466476.8436 | 466476.8436
Option 1A | [5 empty] | $ | 0 | 0 | 0 | 0 | 9925.0392 | 9925.0392 | 9925.0392 | 9925.0392 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 466476.8436 | 466476.8436
Option 1B | [5 empty] | $ | 0 | 0 | 0 | 0 | 9925.0392 | 9925.0392 | 9925.0392 | 9925.0392 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 466476.8436 | 466476.8436
Option 2A | [5 empty] | $ | 0 | 0 | 0 | 0 | 9925.0392 | 9925.0392 | 9925.0392 | 9925.0392 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 466476.8436 | 466476.8436
Option 2B | [5 empty] | $ | 0 | 0 | 0 | 0 | 9925.0392 | 9925.0392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | [5 empty] | $ | 0 | 0 | 0 | 0 | 9925.0392 | 9925.0392 | 9925.0392 | 9925.0392 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 466476.8436 | 466476.8436
Option 2D | [5 empty] | $ | 0 | 0 | 0 | 0 | 9925.0392 | 9925.0392 | 9925.0392 | 9925.0392 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 466476.8436 | 466476.8436
Option 3A | [5 empty] | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Option name |  | S3 | High |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $ | 0 | 0 | 0 | 0 | 4537.474 | 4537.474 | 4537.474 | 4537.474 | 31762.3182 | 31762.3182 | 31762.3182 | 31762.3182 | 31762.3182 | 81674.5324 | 81674.5324 | 81674.5324 | 81674.5324 | 81674.5324 | 213261.2791 | 213261.2791
Option 1A | [5 empty] | $ | 0 | 0 | 0 | 0 | 4537.474 | 4537.474 | 4537.474 | 4537.474 | 31762.3182 | 31762.3182 | 31762.3182 | 31762.3182 | 31762.3182 | 81674.5324 | 81674.5324 | 81674.5324 | 81674.5324 | 81674.5324 | 213261.2791 | 213261.2791
Option 1B | [5 empty] | $ | 0 | 0 | 0 | 0 | 4537.474 | 4537.474 | 4537.474 | 4537.474 | 31762.3182 | 31762.3182 | 31762.3182 | 31762.3182 | 31762.3182 | 81674.5324 | 81674.5324 | 81674.5324 | 81674.5324 | 81674.5324 | 213261.2791 | 213261.2791
Option 2A | [5 empty] | $ | 0 | 0 | 0 | 0 | 4537.474 | 4537.474 | 4537.474 | 4537.474 | 31762.3182 | 31762.3182 | 31762.3182 | 31762.3182 | 31762.3182 | 81674.5324 | 81674.5324 | 81674.5324 | 81674.5324 | 81674.5324 | 213261.2791 | 213261.2791
Option 2B | [5 empty] | $ | 0 | 0 | 0 | 0 | 4537.474 | 4537.474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | [5 empty] | $ | 0 | 0 | 0 | 0 | 4537.474 | 4537.474 | 4537.474 | 4537.474 | 31762.3182 | 31762.3182 | 31762.3182 | 31762.3182 | 31762.3182 | 81674.5324 | 81674.5324 | 81674.5324 | 81674.5324 | 81674.5324 | 213261.2791 | 213261.2791
Option 2D | [5 empty] | $ | 0 | 0 | 0 | 0 | 4537.474 | 4537.474 | 4537.474 | 4537.474 | 31762.3182 | 31762.3182 | 31762.3182 | 31762.3182 | 31762.3182 | 81674.5324 | 81674.5324 | 81674.5324 | 81674.5324 | 81674.5324 | 213261.2791 | 213261.2791
Option 3A | [5 empty] | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (market benefits)
Option name |  | S1 | Central |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Option name |  | S2 | Low |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Option name |  | S3 | High |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Full involuntary load shedding forecast (zeroed out after 2027/28 in NPV assessment - see above, see PACR section 6.1)
Avoided involuntary load shedding in NW Slopes
Option name |  | S1 | Central |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 5236 | 6550 | 12553 | 16394 | 15307 | 15288 | 16185 | 16565 | 15953 | 15560 | 15661 | 15493 | 13403 | 12450 | 13116
Option 1A | [5 empty] | MWh | 0 | 0 | 253 | 935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B | [5 empty] | MWh | 0 | 0 | 253 | 935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | [5 empty] | MWh | 0 | 0 | 253 | 1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | [5 empty] | MWh | Redacted to preserve confidentiality
Option 3C | [5 empty] | MWh | 0 | 0 | 253 | 1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | [5 empty] | MWh | Redacted to preserve confidentiality
Option 5B | [5 empty] | MWh | Redacted to preserve confidentiality
Option 5C | [5 empty] | MWh | Redacted to preserve confidentiality
Option name |  | S2 | Low |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | MWh | 0 | 0 | 0 | 577 | 1036 | 1068 | 1073 | 1077 | 1081 | 1084 | 1086 | 1088 | 1091 | 1094 | 1097 | 1099 | 1102 | 1106 | 1109 | 1110
Option 1A | [5 empty] | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B | [5 empty] | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | [5 empty] | MWh | 0 | 0 | 0 | 577 | 1036 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | [5 empty] | MWh | 0 | 0 | 0 | 577 | 1036 | 431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | [5 empty] | MWh | 0 | 0 | 0 | 577 | 1036 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | [5 empty] | MWh | 0 | 0 | 0 | 577 | 1036 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | [5 empty] | MWh | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | [5 empty] | MWh | Redacted to preserve confidentiality
Option 3C | [5 empty] | MWh | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | [5 empty] | MWh | Redacted to preserve confidentiality
Option 5B | [5 empty] | MWh | Redacted to preserve confidentiality
Option 5C | [5 empty] | MWh | Redacted to preserve confidentiality
Option name |  | S3 | High |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 5236 | 6550 | 12553 | 16394 | 15307 | 15288 | 16185 | 16565 | 15953 | 15560 | 15661 | 15493 | 13403 | 12450 | 13116
Option 1A | [5 empty] | MWh | 0 | 0 | 253 | 935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B | [5 empty] | MWh | 0 | 0 | 253 | 935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | [5 empty] | MWh | 0 | 0 | 253 | 1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | [5 empty] | MWh | Redacted to preserve confidentiality
Option 3C | [5 empty] | MWh | 0 | 0 | 253 | 1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | [5 empty] | MWh | Redacted to preserve confidentiality
Option 5B | [5 empty] | MWh | Redacted to preserve confidentiality
Option 5C | [5 empty] | MWh | Redacted to preserve confidentiality
Note on K60: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Zeroes such that build period matches the above
Note on B432: Liam Hickey: decommissions existing line, builds new in 2029
Note on B435: Liam Hickey: 3A, 3B and 3C rebuild 969 in 2026

## Line 969 costs
Line 969 costs - calculation of avoided involuntary load shedding (wood pole replacement)
|  |  |  | Annualised cost |  |  | Central
Optimal year of wood pole replacement | Mid point | Quantity | Replacement Cost (based on $125k/pole) | Central (S1) | Low (S2) | High (S3) | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
2026-2028 | 2027 | 1 | 125000 | -7790.0429 | -9925.0392 | -4537.474 |  |  |  |  | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429
2029-2033 | 2031 | 6 | 750000 | -46740.2575 | -59550.2354 | -27224.8441 | [8 empty] | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575
2034-2038 | 2036 | 11 | 1375000 | -85690.4721 | -109175.4315 | -49912.2143 | Central 2036: -85690.4721; Central 2037: -85690.4721; Central 2038: -85690.4721; Central 2039: -85690.4721; Central 2040: -85690.4721; Central 2041: -85690.4721; Central 2042: -85690.4721
2039-2043 | 2041 | 29 | 3625000 | -225911.2447 | -287826.1375 | -131586.7467 | Central 2041: -225911.2447; Central 2042: -225911.2447
2044-2046 | 2045 | 19 | 2375000 | -148010.8155 | -188575.7453 | -86212.0065
Total |  | 66 | 8250000 | -514142.8327 | -655052.5889 | -299473.2856 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Asset life of wood poles | [6 empty] | Central 2023: Low
40 | [6 empty] | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
[11 empty] | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392
[15 empty] | -59550.2354 | -59550.2354 | -59550.2354 | -59550.2354 | -59550.2354 | -59550.2354 | -59550.2354 | -59550.2354 | -59550.2354 | -59550.2354 | -59550.2354 | -59550.2354
[20 empty] | -109175.4315 | -109175.4315 | -109175.4315 | -109175.4315 | -109175.4315 | -109175.4315 | -109175.4315
[25 empty] | -287826.1375 | -287826.1375
[7 empty] | 0 | 0 | 0 | 0 | 9925.0392 | 9925.0392 | 9925.0392 | 9925.0392 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 466476.8436 | 466476.8436
High
[7 empty] | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
[11 empty] | -4537.474 | -4537.474 | -4537.474 | -4537.474 | -4537.474 | -4537.474 | -4537.474 | -4537.474 | -4537.474 | -4537.474 | -4537.474 | -4537.474 | -4537.474 | -4537.474 | -4537.474 | -4537.474
[15 empty] | -27224.8441 | -27224.8441 | -27224.8441 | -27224.8441 | -27224.8441 | -27224.8441 | -27224.8441 | -27224.8441 | -27224.8441 | -27224.8441 | -27224.8441 | -27224.8441
[20 empty] | -49912.2143 | -49912.2143 | -49912.2143 | -49912.2143 | -49912.2143 | -49912.2143 | -49912.2143
[25 empty] | -131586.7467 | -131586.7467
[7 empty] | 0 | 0 | 0 | 0 | 4537.474 | 4537.474 | 4537.474 | 4537.474 | 31762.3182 | 31762.3182 | 31762.3182 | 31762.3182 | 31762.3182 | 81674.5324 | 81674.5324 | 81674.5324 | 81674.5324 | 81674.5324 | 213261.2791 | 213261.2791

## S1
S1 |  | Central
NPV results
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 503939889.9156 | -3206685.9703 | -12900039.2896 | -67117200.6217 | 2895525.3298 | 195994819.4777 | 219687881.7602 | 292895533.0597 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | 153789901.9645
Option 1B |  |  |  | $ | 531938318.8578 | -2476045.6055 | -11876473.3307 | -65427657.4559 | 89416799.3296 | 171741973.0287 | 203809665.3439 | 254024732.2558 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | 172864229.8967
Option 2A |  |  |  | $ | 242239119.9542 | -853032.1806 | -4152329.8479 | -6074347.2333 | -14747405.7774 | -82095669.7479 | 112319159.7463 | 294106897.9127 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | 115113274.5756
Option 2B |  |  |  | $ | 227052073.845 | -1059318.697 | -4160490.5939 | -7021259.298 | -44162850.1901 | -65610947.6764 | 113538523.4912 | 294463276.9129 | -1171165.745 | -1124425.4875 | -1124425.4875 | -1124425.4875 | -1124425.4875 | -1124425.4875 | -1038735.0153 | -1038735.0153 | -1038735.0153 | -1038735.0153 | -1038735.0153 | -812823.7707 | 97499490.7084
Option 2C |  |  |  | $ | 211962726.5646 | -853032.1806 | -4256168.8051 | -6353734.4871 | -15850330.5259 | -116758134.0794 | 79938451.1678 | 304516948.449 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | 163330911.9266
Option 2D |  |  |  | $ | 183873937.0658 | -1396969.7715 | -4873417.2524 | -9330605.5004 | -65236549.9004 | -163840847.3608 | 162766624.0024 | 293298015.6897 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | 175444945.4141
Option 3A |  |  |  | $ | 572907952.1158 | -1780538.7186 | -6344069.0631 | -27259103.829 | -4875722.5177 | 235465667.092 | 237292333.4998 | 294219793.248 | -1414649.4099 | -1367909.1524 | -1367909.1524 | -1367909.1524 | -1367909.1524 | -1367909.1524 | -1282218.6802 | -1282218.6802 | -1282218.6802 | -1282218.6802 | -1282218.6802 | -1056307.4356 | 90165662.9247
Option 3B |  |  |  | $ | 550833103.1123 | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 544344453.2184 | -1604212.6826 | -6322108.4711 | -26924343.0342 | 3142088.4918 | 207326303.4124 | 188631433.3247 | 304629843.7843 | -1609241.3277 | -1562501.0702 | -1562501.0702 | -1562501.0702 | -1562501.0702 | -1562501.0702 | -1476810.598 | -1476810.598 | -1476810.598 | -1476810.598 | -1476810.598 | -1250899.3534 | 139183067.2668
Option 5A |  |  |  | $ | 552932769.8407 | Redacted to preserve confidentiality
Option 5B |  |  |  | $ | 618386432.423 | Redacted to preserve confidentiality
Option 5C |  |  |  | $ | 601958595.6965 | Redacted to preserve confidentiality
S1 |  | Calculation
Capital cost calculation
Option | Stage | Components | TNSP | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | Terminal value | Years in analysis period | Annual depreciation
Option 1A | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 1A | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -36413780.2249 | -466189.595 | -1313773.949 | -49169718.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26202693.7183 | 26202693.7183 | 17 | 1455705.2066
Option 1A | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -13188143.5144 | -1270571.3167 | -6682283.4849 | -10480304.2184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10599066.4365 | 10599066.4365 | 17 | 460828.9755
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -15918882.5506 | 0 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16795106.814 | 16795106.814 | 14 | 799766.9911
Option 1A | 1 | Upgrade 968 line to 160 MVA rating | 1 | $ | -94257312.8162 | -906966.4008 | -1440809.2298 | -2842677.6499 | -97336044.2365 | -46156518.1829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84961723.2571 | 84961723.2571 | 15 | 4248086.1629
Option 1A | 2 | 60 MVAr SVC at Narrabri | 1 | $ | -9824340.639 | 0 | 0 | 0 | 0 | -1047577.2064 | -6968417.1091 | -11645069.1544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13271217.8423 | 13271217.8423 | 13 | 491526.5867
Option 1B | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 1B | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -36413780.2249 | -466189.595 | -1313773.949 | -49169718.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26202693.7183 | 26202693.7183 | 17 | 1455705.2066
Option 1B | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -13188143.5144 | -1270571.3167 | -6682283.4849 | -10480304.2184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10599066.4365 | 10599066.4365 | 17 | 460828.9755
Option 1B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -17706780.8168 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15195572.8317 | 15195572.8317 | 16 | 799766.9911
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | -49902903.6746 | 0 | -291443.7217 | -538986.4355 | -1694034.4788 | -17053922.7396 | -30893655.2791 | -52002700.1153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75831309.6498 | 75831309.6498 | 13 | 2049494.8554
Option 2A | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -24144202.2277 | 0 | -304770.178 | -540678.4002 | -1838846.5297 | -15373872.4983 | -27921537.2786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33105387.517 | 33105387.517 | 14 | 919594.0977
Option 2A | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | -31322112.8055 | -290073.5228 | -384387.0441 | -909168.7657 | -11910563.8167 | -37455489.0607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29114104.12 | 29114104.12 | 15 | 1455705.206
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -15918882.5506 | 0 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16795106.814 | 16795106.814 | 14 | 799766.9911
Option 2A | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -9824340.3916 | 0 | 0 | 0 | 0 | -1047577 | -6968417 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13271217.525 | 13271217.525 | 13 | 491526.575
Option 2B | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -34758610.5245 | -320034.0032 | -571518.4188 | -1782611.1821 | -15944119.0011 | -38721538.8356 | -4730669.9292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44690753.7864 | 44690753.7864 | 14 | 1241409.8274
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -17417601.8228 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15995339.8229 | 15995339.8229 | 15 | 799766.9911
Option 2B | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -9824340.3916 | 0 | 0 | 0 | 0 | -1047577 | -6968417 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13271217.525 | 13271217.525 | 13 | 491526.575
Option 2C | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -24144202.2277 | 0 | -304770.178 | -540678.4002 | -1838846.5297 | -15373872.4983 | -27921537.2786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33105387.517 | 33105387.517 | 14 | 919594.0977
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating | 1 | $ | -31322112.8055 | -290073.5228 | -384387.0441 | -909168.7657 | -11910563.8167 | -37455489.0607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29114104.12 | 29114104.12 | 15 | 1455705.206
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -34475020.3507 | 0 | -280164.9931 | -581512.839 | -2019198.3822 | -19947050.7231 | -42769235.622 | -1514936.9106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49662953.6078 | 49662953.6078 | 13 | 1342241.9894
Option 2D | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -70637734.0949 | -367611.5549 | -900058.0332 | -3182788.6187 | -20107254.8947 | -99355949.4593 | -2954264.6191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91344907.5696 | 91344907.5696 | 14 | 2537358.5436
Option 2D | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | -31322112.8055 | -290073.5228 | -384387.0441 | -909168.7657 | -11910563.8167 | -37455489.0607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29114104.12 | 29114104.12 | 15 | 1455705.206
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -17417601.8228 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15995339.8229 | 15995339.8229 | 15 | 799766.9911
Option 2D | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -9824340.3916 | 0 | 0 | 0 | 0 | -1047577 | -6968417 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13271217.525 | 13271217.525 | 13 | 491526.575
Option 3A | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | -54407792.0951 | -1041254.0248 | -2755096.888 | -21687177.713 | -60935329.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57036446.1876 | 57036446.1876 | 17 | 1728377.1572
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -17417601.8228 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15995339.8229 | 15995339.8229 | 15 | 799766.9911
Option 3A | 2 | 60 MVAr SVC at Narrabri 132 | 1 | $ | -9824340.3916 | 0 | 0 | 0 | 0 | -1047577 | -6968417 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13271217.525 | 13271217.525 | 13 | 491526.575
Option 3B | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | -54407792.0951 | -1041254.0248 | -2755096.888 | -21687177.713 | -60935329.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57036446.1876 | 57036446.1876 | 17 | 1728377.1572
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -17417601.8228 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15995339.8229 | 15995339.8229 | 15 | 799766.9911
Option 3B | 2 | Install 50 MW / 50 MWh BESS at Narrabri 132 | 1 | $ |  | Redacted to preserve confidentiality | [19 empty] | Redacted to preserve confidentiality
Option 3C | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | -54407792.0951 | -1041254.0248 | -2755096.888 | -21687177.713 | -60935329.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57036446.1876 | 57036446.1876 | 17 | 1728377.1572
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -34475020.3507 | 0 | -280164.9931 | -581512.839 | -2019198.3822 | -19947050.7231 | -42769235.622 | -1514936.9106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49662953.6078 | 49662953.6078 | 13 | 1342241.9894
Option 5A | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 5A | 1 | BESS at Gunnedah | 0 | $ |  | Redacted to preserve confidentiality | [19 empty] | Redacted to preserve confidentiality
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | -40774440.4963 | 0 | 0 | 0 | -1041254.0248 | -2755096.888 | -21687177.713 | -60935329.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63949954.8164 | 63949954.8164 | 13 | 1728377.1572
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -14483219.8806 | 0 | 0 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17594873.8051 | 17594873.8051 | 13 | 799766.9911
Option 5B | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 5B | 1 | BESS near Gunnedah | 0 | $ |  | Redacted to preserve confidentiality | [19 empty] | Redacted to preserve confidentiality
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | -40774440.4963 | 0 | 0 | 0 | -1041254.0248 | -2755096.888 | -21687177.713 | -60935329.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63949954.8164 | 63949954.8164 | 13 | 1728377.1572
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -14483219.8806 | 0 | 0 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17594873.8051 | 17594873.8051 | 13 | 799766.9911
Option 5C | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 5C | 1 | BESS at Gunnedah | 0 | $ |  | Redacted to preserve confidentiality | [19 empty] | Redacted to preserve confidentiality
Option 5C | 2 | Rebuild 969 line as double circuit | 1 | $ | -40774440.4963 | 0 | 0 | 0 | -1041254.0248 | -2755096.888 | -21687177.713 | -60935329.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63949954.8164 | 63949954.8164 | 13 | 1728377.1572
Option 5C | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -14483219.8806 | 0 | 0 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17594873.8051 | 17594873.8051 | 13 | 799766.9911
Biodiversity offset costs
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | -6799567.8446 | 0 | 0 | 0 | 0 | -12600000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9324000 | 9324000 | 13 | 252000
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -4429726.5643 | 0 | 0 | 0 | 0 | -8100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5832000 | 5832000 | 14 | 162000
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -4789341.6235 | 0 | 0 | 0 | -8100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5832000 | 5832000 | 14 | 162000
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -4429726.5643 | 0 | 0 | 0 | 0 | -8100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5832000 | 5832000 | 14 | 162000
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -8526442.2178 | 0 | 0 | 0 | 0 | -15800000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11692000 | 11692000 | 13 | 316000
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -4789341.6235 | 0 | 0 | 0 | -8100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5832000 | 5832000 | 14 | 162000
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -8526442.2178 | 0 | 0 | 0 | 0 | -15800000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11692000 | 11692000 | 13 | 316000
Property allowances
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | -23724028.5402 | 0 | 0 | 0 | 0 | -35000000 | -9720000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33092800 | 33092800 | 13 | 894400
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -10112934.6139 | 0 | 0 | 0 | 0 | -10000000 | -9200000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13824000 | 13824000 | 14 | 384000
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -10944061.8058 | 0 | 0 | 0 | -10000000 | -9200000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13824000 | 13824000 | 14 | 384000
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -10112934.6139 | 0 | 0 | 0 | 0 | -10000000 | -9200000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13824000 | 13824000 | 14 | 384000
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -11934497.7138 | 0 | 0 | 0 | 0 | -10000000 | -13140000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17123600 | 17123600 | 13 | 462800
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -13977008.6991 | 0 | 0 | 0 | -15000000 | -9340000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17524800 | 17524800 | 14 | 486800
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | -219900.2367 | 0 | 0 | -333278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219963.48 | 219963.48 | 17 | 6665.56
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | -219900.2367 | 0 | 0 | -333278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219963.48 | 219963.48 | 17 | 6665.56
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | -219900.2367 | 0 | 0 | -333278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219963.48 | 219963.48 | 17 | 6665.56
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -11934497.7138 | 0 | 0 | 0 | 0 | -10000000 | -13140000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17123600 | 17123600 | 13 | 462800
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | -165827.7521 | 0 | 0 | 0 | 0 | 0 | -333278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246625.72 | 246625.72 | 13 | 6665.56
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | -165827.7521 | 0 | 0 | 0 | 0 | 0 | -333278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246625.72 | 246625.72 | 13 | 6665.56
Option 5C | 2 | Rebuild 969 line as double circuit | 1 | $ | -165827.7521 | 0 | 0 | 0 | 0 | 0 | -333278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246625.72 | 246625.72 | 13 | 6665.56
TNSP capital costs
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | -175465299.4012 | -3206685.9703 | -12900039.2896 | -67117200.6217 | -98252317.8702 | -57241104.781 | -23528527.1527 | -11645069.1544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156528811.4129
Option 1B |  |  |  | $ | -153598044.2715 | -2476045.6055 | -11876473.3307 | -65427657.4559 | -11731043.8705 | -81214032.7831 | -40613655.2791 | -52002700.1153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174944445.9811
Option 2A |  |  |  | $ | -101615038.8097 | -853032.1806 | -4152329.8479 | -6074347.2333 | -14665683.9801 | -82013947.9506 | -60650064.3221 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116640819.3207
Option 2B |  |  |  | $ | -83596795.8243 | -1059318.697 | -4160490.5939 | -7021259.298 | -44081128.3928 | -65529225.8791 | -11699086.9292 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98312314.479
Option 2C |  |  |  | $ | -130807776.1498 | -853032.1806 | -4256168.8051 | -6353734.4871 | -15768608.7286 | -116676412.2821 | -93030772.9006 | -1514936.9106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165053048.5895
Option 2D |  |  |  | $ | -153830979.0935 | -1396969.7715 | -4873417.2524 | -9330605.5004 | -65154828.1031 | -163759125.5635 | -9922681.6191 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177781372.3822
Option 3A |  |  |  | $ | -87732474.2023 | -1780538.7186 | -6344069.0631 | -27259103.829 | -70972338.6258 | -17607687.0435 | -6968417 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91221970.3602
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | -115426492.2702 | -1604212.6826 | -6322108.4711 | -26924343.0342 | -62954527.6163 | -45747050.7231 | -55909235.622 | -1514936.9106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140433966.6202
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
NNO capital costs
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Operating cost calculation
Option | Stage | Component | TNSP | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 1A | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -4973368.5562 | 0 | 0 | 0 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223
Option 1A | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -1799322.1832 | 0 | 0 | 0 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -2053864.9477 | 0 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 1A | 1 | Upgrade 968 line to 160 MVA rating | 1 | $ | -12047046.402 | 0 | 0 | 0 | 0 | 0 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157
Option 1A | 2 | 60 MVAr SVC at Narrabri | 1 | $ | -1300013.7416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347
Option 1B | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 1B | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -4973368.5562 | 0 | 0 | 0 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223
Option 1B | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -1799322.1832 | 0 | 0 | 0 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902
Option 1B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -2493995.0248 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | -6775756.2541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277
Option 2A | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -3373700.6336 | 0 | 0 | 0 | 0 | 0 | 0 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488
Option 2A | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | -4128199.7333 | 0 | 0 | 0 | 0 | 0 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -2053864.9477 | 0 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 2A | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -1300013.7105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63
Option 2B | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -4554341.0205 | 0 | 0 | 0 | 0 | 0 | 0 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -2268040.1677 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 2B | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -1300013.7105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63
Option 2C | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -3373700.6336 | 0 | 0 | 0 | 0 | 0 | 0 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating | 1 | $ | -4128199.7333 | 0 | 0 | 0 | 0 | 0 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -4437534.7078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947
Option 2D | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -9308768.0182 | 0 | 0 | 0 | 0 | 0 | 0 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718
Option 2D | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | -4128199.7333 | 0 | 0 | 0 | 0 | 0 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -2268040.1677 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 2D | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -1300013.7105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63
Option 3A | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | -8435633.1882 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -2268040.1677 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 3A | 2 | 60 MVAr SVC at Narrabri 132 | 1 | $ | -1300013.7105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63
Option 3B | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | -8435633.1882 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -2268040.1677 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 3B | 2 | Install 50 MW / 50 MWh BESS at Narrabri 132 | 1 | $ |  | Redacted to preserve confidentiality
Option 3C | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | -8435633.1882 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -4437534.7078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947
Option 5A | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 5A | 1 | BESS at Gunnedah | 0 | $ |  | Redacted to preserve confidentiality
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | -5714121.3609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -1850855.2605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 5B | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 5B | 1 | BESS near Gunnedah | 0 | $ |  | Redacted to preserve confidentiality
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | -5714121.3609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -1850855.2605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 5C | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 5C | 1 | BESS at Gunnedah | 0 | $ |  | Redacted to preserve confidentiality
Option 5C | 2 | Rebuild 969 line as double circuit | 1 | $ | -5714121.3609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 5C | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -1850855.2605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Biodiversity offset costs
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Property allowances
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5C | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TNSP operating expenditure
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | -22971329.5735 | 0 | 0 | 0 | -775550.2098 | -775550.2098 | -2262380.3668 | -2542298.8137 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484
Option 1B |  |  |  | $ | -16840155.7611 | 0 | 0 | 0 | -775550.2098 | -1055468.6567 | -1055468.6567 | -1055468.6567 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844
Option 2A |  |  |  | $ | -11653492.7679 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -591218.6194 | -1330934.1151 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451
Option 2B |  |  |  | $ | -8920108.6415 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -361640.2442 | -982345.1579 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879
Option 2C |  |  |  | $ | -12737148.8174 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -591218.6194 | -1051015.6682 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629
Option 2D |  |  |  | $ | -17802735.3724 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -871137.0663 | -2139816.3381 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681
Option 3A |  |  |  | $ | -12801400.8092 | 0 | 0 | 0 | -945910.3759 | -945910.3759 | -1225828.8228 | -1225828.8228 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | -13670881.6387 | 0 | 0 | 0 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
TSNP network service payments to NNO proponents
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
NNO operating expenditure
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided fuel consumption from generation dispatch
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided voluntary load curtailment
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding outside of NW Slopes
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding in NW Slopes
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 702376518.8904 | 0 | 0 | 0 | 101923393.4099 | 254011474.4685 | 245478789.2797 | 307082901.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 702376518.8904 | 0 | 0 | 0 | 101923393.4099 | 254011474.4685 | 245478789.2797 | 307082901.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 355507651.5318 | 0 | 0 | 0 | 0 | 0 | 173560442.6878 | 307082901.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 318810895.8638 | 0 | 0 | 0 | 0 | 0 | 125599250.6647 | 307082901.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 355507651.5318 | 0 | 0 | 0 | 0 | 0 | 173560442.6878 | 307082901.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 355507651.5318 | 0 | 0 | 0 | 0 | 0 | 173560442.6878 | 307082901.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 672671495.9977 | 0 | 0 | 0 | 67042526.4839 | 254011474.4685 | 245478789.2797 | 307082901.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 672671495.9977 | 0 | 0 | 0 | 67042526.4839 | 254011474.4685 | 245478789.2797 | 307082901.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided costs for non RIT-T proponent parties
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (wood pole replacement)
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 758082.447 | 0 | 0 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 770331.1296 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 770331.1296 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (market benefits)
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
NNO receipts received from TNSP
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Payback analysis
PV gross benefits
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ |  | 0 | 0 | 0 | 86799354.5278 | 205042315.1819 | 187824254.8171 | 222710594.3635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ |  | 0 | 0 | 0 | 86799354.5278 | 205042315.1819 | 187824254.8171 | 222710594.3635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 132797057.1683 | 222710594.3635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 96100301.5002 | 222716244.0597 | 5355.1622 | 35531.8822 | 33679.5092 | 31923.7054 | 30259.4364 | 28681.9302 | 69908.5638 | 66264.0416 | 62809.5181 | 59535.0882 | 56431.3632 | 139666.8811 | 132385.6693
Option 2C |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 132797057.1683 | 222710594.3635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 132797057.1683 | 222710594.3635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ |  | 0 | 0 | 0 | 57094331.6351 | 205048603.4349 | 187830215.2466 | 222716244.0597 | 5355.1622 | 35531.8822 | 33679.5092 | 31923.7054 | 30259.4364 | 28681.9302 | 69908.5638 | 66264.0416 | 62809.5181 | 59535.0882 | 56431.3632 | 139666.8811 | 132385.6693
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ |  | 0 | 0 | 0 | 57094331.6351 | 205048603.4349 | 187830215.2466 | 222716244.0597 | 5355.1622 | 35531.8822 | 33679.5092 | 31923.7054 | 30259.4364 | 28681.9302 | 69908.5638 | 66264.0416 | 62809.5181 | 59535.0882 | 56431.3632 | 139666.8811 | 132385.6693
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Cumulative PV gross benefits
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ |  | 0 | 0 | 0 | 86799354.5278 | 291841669.7097 | 479665924.5268 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904
Option 1B |  |  |  | $ |  | 0 | 0 | 0 | 86799354.5278 | 291841669.7097 | 479665924.5268 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904
Option 2A |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 132797057.1683 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318
Option 2B |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 96100301.5002 | 318816545.5599 | 318821900.7222 | 318857432.6044 | 318891112.1135 | 318923035.8189 | 318953295.2553 | 318981977.1855 | 319051885.7494 | 319118149.7909 | 319180959.309 | 319240494.3972 | 319296925.7604 | 319436592.6415 | 319568978.3108
Option 2C |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 132797057.1683 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318
Option 2D |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 132797057.1683 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318
Option 3A |  |  |  | $ |  | 0 | 0 | 0 | 57094331.6351 | 262142935.0701 | 449973150.3167 | 672689394.3764 | 672694749.5386 | 672730281.4208 | 672763960.93 | 672795884.6354 | 672826144.0718 | 672854826.002 | 672924734.5658 | 672990998.6074 | 673053808.1254 | 673113343.2137 | 673169774.5769 | 673309441.458 | 673441827.1273
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ |  | 0 | 0 | 0 | 57094331.6351 | 262142935.0701 | 449973150.3167 | 672689394.3764 | 672694749.5386 | 672730281.4208 | 672763960.93 | 672795884.6354 | 672826144.0718 | 672854826.002 | 672924734.5658 | 672990998.6074 | 673053808.1254 | 673113343.2137 | 673169774.5769 | 673309441.458 | 673441827.1273
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Total cost
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ |  | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747
Option 1B |  |  |  | $ |  | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326
Option 2A |  |  |  | $ |  | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776
Option 2B |  |  |  | $ |  | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658
Option 2C |  |  |  | $ |  | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673
Option 2D |  |  |  | $ |  | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466
Option 3A |  |  |  | $ |  | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ |  | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Payback
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 1B |  |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2A |  |  |  | $ |  | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2B |  |  |  | $ |  | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2C |  |  |  | $ |  | NO | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2D |  |  |  | $ |  | NO | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 3A |  |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 3B |  |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 3C |  |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 5A |  |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 5B |  |  |  | $ |  | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 5C |  |  |  | $ |  | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES

## S2
S2 |  | Low
NPV results
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 9538761.1013 | -2874649.4619 | -14103630.0298 | -79965496.7333 | 18160447.3055 | 33223918.4658 | 34274095.1045 | 34438185.2042 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | 51100404.1646
Option 1B |  |  |  | $ | 9538761.1013 | -2874649.4619 | -14103630.0298 | -79965496.7333 | 18160447.3055 | 33223918.4658 | 34274095.1045 | 34438185.2042 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | 51100404.1646
Option 2A |  |  |  | $ | -18559272.1993 | -703698.3223 | -4489520.9599 | -6078816.103 | -2380279.9594 | -41924062.4201 | -18522690.392 | 34672216.5679 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | 71283969.731
Option 2B |  |  |  | $ | -39809332.5559 | -1103740.8263 | -4822956.2609 | -7631232.0804 | -42636870.5487 | -59983645.3417 | 14910019.5039 | 34521233.7423 | -692501.6718 | -632951.4364 | -632951.4364 | -632951.4364 | -632951.4364 | -632951.4364 | -523776.0049 | -523776.0049 | -523776.0049 | -523776.0049 | -523776.0049 | -235949.8674 | 86071246.5465
Option 2C |  |  |  | $ | -18559272.1993 | -703698.3223 | -4489520.9599 | -6078816.103 | -2380279.9594 | -41924062.4201 | -18522690.392 | 34672216.5679 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | 71283969.731
Option 2D |  |  |  | $ | -90041409.8888 | -1163212.766 | -5233630.7789 | -9381453.8762 | -54090790.4157 | -135951658.6214 | 24186400.4323 | 33863334.3449 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | 147900487.5738
Option 3A |  |  |  | $ | -4756063.3638 | -2005265.8533 | -7552429.3474 | -32928537.7441 | -66219489.2928 | 33063483.339 | 34113659.9776 | 34277750.0774 | -935985.3367 | -876435.1013 | -876435.1013 | -876435.1013 | -876435.1013 | -876435.1013 | -767259.6698 | -767259.6698 | -767259.6698 | -767259.6698 | -767259.6698 | -479433.5323 | 76964832.7331
Option 3B |  |  |  | $ | 5198826.8909 | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | -4756063.3638 | -2005265.8533 | -7552429.3474 | -32928537.7441 | -66219489.2928 | 33063483.339 | 34113659.9776 | 34277750.0774 | -935985.3367 | -876435.1013 | -876435.1013 | -876435.1013 | -876435.1013 | -876435.1013 | -767259.6698 | -767259.6698 | -767259.6698 | -767259.6698 | -767259.6698 | -479433.5323 | 76964832.7331
Option 5A |  |  |  | $ | -33078421.6132 | Redacted to preserve confidentiality
Option 5B |  |  |  | $ | -1401631.0301 | Redacted to preserve confidentiality
Option 5C |  |  |  | $ | -18244681.2835 | Redacted to preserve confidentiality
S2 |  | Calculation
Capital cost calculation
Option | Stage | Components | TNSP | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | Terminal value | Years in analysis period | Annual depreciation
Option 1A | 1 | 3rd Narrabri Tx | 1 | $ | -7714511.579 | -703698.3223 | -4108558.2374 | -5402968.1028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5873754.1809 | 5873754.1809 | 17 | 255380.6166
Option 1A | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -47006716.2464 | -582736.9937 | -1642217.4363 | -61462148.3575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32753367.1479 | 32753367.1479 | 17 | 1819631.5082
Option 1A | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -17341626.7965 | -1588214.1459 | -8352854.3561 | -13100380.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13248833.0456 | 13248833.0456 | 17 | 576036.2194
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 999708.7389
Option 1A | 1 | Upgrade 968 line to 160 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 5310107.7036
Option 1A | 2 | 60 MVAr SVC at Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 614408.2334
Option 1B | 1 | 3rd Narrabri Tx | 1 | $ | -7714511.579 | -703698.3223 | -4108558.2374 | -5402968.1028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5873754.1809 | 5873754.1809 | 17 | 255380.6166
Option 1B | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -47006716.2464 | -582736.9937 | -1642217.4363 | -61462148.3575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32753367.1479 | 32753367.1479 | 17 | 1819631.5082
Option 1B | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -17341626.7965 | -1588214.1459 | -8352854.3561 | -13100380.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13248833.0456 | 13248833.0456 | 17 | 576036.2194
Option 1B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 999708.7389
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 2561868.5693
Option 2A | 1 | 3rd Narrabri Tx | 1 | $ | -7714511.579 | -703698.3223 | -4108558.2374 | -5402968.1028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5873754.1809 | 5873754.1809 | 17 | 255380.6166
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -31018215.8508 | 0 | -380962.7225 | -675848.0002 | -2298558.1621 | -19217340.6228 | -34901921.5982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41381734.3962 | 41381734.3962 | 14 | 1149492.6221
Option 2A | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 1819631.5075
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 999708.7389
Option 2A | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 614408.2188
Option 2B | 1 | 3rd Narrabri Tx | 1 | $ | -7714511.579 | -703698.3223 | -4108558.2374 | -5402968.1028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5873754.1809 | 5873754.1809 | 17 | 255380.6166
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -45260831.4376 | -400042.504 | -714398.0235 | -2228263.9776 | -19930148.7514 | -48401923.5444 | -5913337.4116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55863442.233 | 55863442.233 | 14 | 1551762.2843
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 999708.7389
Option 2B | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 614408.2188
Option 2C | 1 | 3rd Narrabri Tx | 1 | $ | -7714511.579 | -703698.3223 | -4108558.2374 | -5402968.1028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5873754.1809 | 5873754.1809 | 17 | 255380.6166
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -31018215.8508 | 0 | -380962.7225 | -675848.0002 | -2298558.1621 | -19217340.6228 | -34901921.5982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41381734.3962 | 41381734.3962 | 14 | 1149492.6221
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 1819631.5075
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 1677802.4868
Option 2D | 1 | 3rd Narrabri Tx | 1 | $ | -7714511.579 | -703698.3223 | -4108558.2374 | -5402968.1028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5873754.1809 | 5873754.1809 | 17 | 255380.6166
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -91854528.0347 | -459514.4437 | -1125072.5415 | -3978485.7734 | -25134068.6184 | -124194936.8241 | -3692830.7739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114181134.462 | 114181134.462 | 14 | 3171698.1795
Option 2D | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 1819631.5075
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 999708.7389
Option 2D | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 614408.2188
Option 3A | 1 | 3rd Narrabri Tx | 1 | $ | -7714511.579 | -703698.3223 | -4108558.2374 | -5402968.1028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5873754.1809 | 5873754.1809 | 17 | 255380.6166
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | -71233912.8301 | -1301567.531 | -3443871.1101 | -27108972.1413 | -76169161.5427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71295557.7345 | 71295557.7345 | 17 | 2160471.4465
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 999708.7389
Option 3A | 2 | 60 MVAr SVC at Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 614408.2188
Option 3B | 1 | 3rd Narrabri Tx | 1 | $ | -7714511.579 | -703698.3223 | -4108558.2374 | -5402968.1028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5873754.1809 | 5873754.1809 | 17 | 255380.6166
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | -71233912.8301 | -1301567.531 | -3443871.1101 | -27108972.1413 | -76169161.5427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71295557.7345 | 71295557.7345 | 17 | 2160471.4465
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 999708.7389
Option 3B | 2 | Install 50 MW / 50 MWh BESS at Narrabri 132 | 1 | $ |  | Redacted to preserve confidentiality | [19 empty] | Redacted to preserve confidentiality
Option 3C | 1 | 3rd Narrabri Tx | 1 | $ | -7714511.579 | -703698.3223 | -4108558.2374 | -5402968.1028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5873754.1809 | 5873754.1809 | 17 | 255380.6166
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | -71233912.8301 | -1301567.531 | -3443871.1101 | -27108972.1413 | -76169161.5427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71295557.7345 | 71295557.7345 | 17 | 2160471.4465
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 1677802.4868
Option 5A | 1 | 3rd Narrabri Tx | 1 | $ | -7714511.579 | -703698.3223 | -4108558.2374 | -5402968.1028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5873754.1809 | 5873754.1809 | 17 | 255380.6166
Option 5A | 1 | BESS at Gunnedah | 0 | $ |  | Redacted to preserve confidentiality | [19 empty] | Redacted to preserve confidentiality
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 2160471.4465
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 999708.7389
Option 5B | 1 | 3rd Narrabri Tx | 1 | $ | -7714511.579 | -703698.3223 | -4108558.2374 | -5402968.1028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5873754.1809 | 5873754.1809 | 17 | 255380.6166
Option 5B | 1 | BESS near Gunnedah | 0 | $ |  | Redacted to preserve confidentiality | [19 empty] | Redacted to preserve confidentiality
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 2160471.4465
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 999708.7389
Option 5C | 1 | 3rd Narrabri Tx | 1 | $ | -7714511.579 | -703698.3223 | -4108558.2374 | -5402968.1028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5873754.1809 | 5873754.1809 | 17 | 255380.6166
Option 5C | 1 | BESS at Gunnedah | 0 | $ |  | Redacted to preserve confidentiality | [19 empty] | Redacted to preserve confidentiality
Option 5C | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 2160471.4465
Option 5C | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 999708.7389
Biodiversity offset costs
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 315000
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -5736731.3759 | 0 | 0 | 0 | 0 | -10125000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7290000 | 7290000 | 14 | 202500
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -6305351.7782 | 0 | 0 | 0 | -10125000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7290000 | 7290000 | 14 | 202500
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -5736731.3759 | 0 | 0 | 0 | 0 | -10125000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7290000 | 7290000 | 14 | 202500
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 395000
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -6305351.7782 | 0 | 0 | 0 | -10125000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7290000 | 7290000 | 14 | 202500
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 395000
Property allowances
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 1118000
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -12997396.2559 | 0 | 0 | 0 | 0 | -12500000 | -11500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17280000 | 17280000 | 14 | 480000
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -14300178.5729 | 0 | 0 | 0 | -12500000 | -11500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17280000 | 17280000 | 14 | 480000
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -12997396.2559 | 0 | 0 | 0 | 0 | -12500000 | -11500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17280000 | 17280000 | 14 | 480000
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 578500
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -18291524.4104 | 0 | 0 | 0 | -18750000 | -11675000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21906000 | 21906000 | 14 | 608500
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | -290912.9436 | 0 | 0 | -416597.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274954.35 | 274954.35 | 17 | 8331.95
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | -290912.9436 | 0 | 0 | -416597.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274954.35 | 274954.35 | 17 | 8331.95
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | -290912.9436 | 0 | 0 | -416597.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 274954.35 | 274954.35 | 17 | 8331.95
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 578500
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 8331.95
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 8331.95
Option 5C | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 8331.95
TNSP capital costs
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | -72062854.622 | -2874649.4619 | -14103630.0298 | -79965496.7333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51875954.3744
Option 1B |  |  |  | $ | -72062854.622 | -2874649.4619 | -14103630.0298 | -79965496.7333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51875954.3744
Option 2A |  |  |  | $ | -57466855.0616 | -703698.3223 | -4489520.9599 | -6078816.103 | -2298558.1621 | -41842340.6228 | -46401921.5982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71825488.5772
Option 2B |  |  |  | $ | -73580873.3678 | -1103740.8263 | -4822956.2609 | -7631232.0804 | -42555148.7514 | -59901923.5444 | -5913337.4116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86307196.4139
Option 2C |  |  |  | $ | -57466855.0616 | -703698.3223 | -4489520.9599 | -6078816.103 | -2298558.1621 | -41842340.6228 | -46401921.5982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71825488.5772
Option 2D |  |  |  | $ | -124165915.8024 | -1163212.766 | -5233630.7789 | -9381453.8762 | -54009068.6184 | -135869936.8241 | -3692830.7739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149250888.6429
Option 3A |  |  |  | $ | -79239337.3527 | -2005265.8533 | -7552429.3474 | -32928537.7441 | -76169161.5427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77444266.2654
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | -79239337.3527 | -2005265.8533 | -7552429.3474 | -32928537.7441 | -76169161.5427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77444266.2654
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
NNO capital costs
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Operating cost calculation
Option | Stage | Component | TNSP | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A | 1 | 3rd Narrabri Tx | 1 | $ | -667136.958 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 1A | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -4159283.9531 | 0 | 0 | 0 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223
Option 1A | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -1504793.3404 | 0 | 0 | 0 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1A | 1 | Upgrade 968 line to 160 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1A | 2 | 60 MVAr SVC at Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B | 1 | 3rd Narrabri Tx | 1 | $ | -667136.958 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 1B | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -4159283.9531 | 0 | 0 | 0 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223
Option 1B | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -1504793.3404 | 0 | 0 | 0 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902
Option 1B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | 3rd Narrabri Tx | 1 | $ | -667136.958 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -2718868.8328 | 0 | 0 | 0 | 0 | 0 | 0 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488
Option 2A | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | 1 | 3rd Narrabri Tx | 1 | $ | -667136.958 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -3670348.1426 | 0 | 0 | 0 | 0 | 0 | 0 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 1 | 3rd Narrabri Tx | 1 | $ | -667136.958 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -2718868.8328 | 0 | 0 | 0 | 0 | 0 | 0 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | 3rd Narrabri Tx | 1 | $ | -667136.958 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -7501945.7814 | 0 | 0 | 0 | 0 | 0 | 0 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718
Option 2D | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | 1 | 3rd Narrabri Tx | 1 | $ | -667136.958 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | -7054814.7311 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | 2 | 60 MVAr SVC at Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | 1 | 3rd Narrabri Tx | 1 | $ | -667136.958 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | -7054814.7311 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | 2 | Install 50 MW / 50 MWh BESS at Narrabri 132 | 1 | $ |  | Redacted to preserve confidentiality
Option 3C | 1 | 3rd Narrabri Tx | 1 | $ | -667136.958 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | -7054814.7311 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | 1 | 3rd Narrabri Tx | 1 | $ | -667136.958 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 5A | 1 | BESS at Gunnedah | 0 | $ |  | Redacted to preserve confidentiality
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5B | 1 | 3rd Narrabri Tx | 1 | $ | -667136.958 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 5B | 1 | BESS near Gunnedah | 0 | $ |  | Redacted to preserve confidentiality
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5C | 1 | 3rd Narrabri Tx | 1 | $ | -667136.958 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 5C | 1 | BESS at Gunnedah | 0 | $ |  | Redacted to preserve confidentiality
Option 5C | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5C | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Biodiversity offset costs
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Property allowances
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5C | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TNSP operating expenditure
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | -6331214.2515 | 0 | 0 | 0 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098
Option 1B |  |  |  | $ | -6331214.2515 | 0 | 0 | 0 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098
Option 2A |  |  |  | $ | -3386005.7908 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461
Option 2B |  |  |  | $ | -4337485.1006 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -702426.711 | -702426.711 | -702426.711 | -702426.711 | -702426.711 | -702426.711 | -702426.711 | -702426.711 | -702426.711 | -702426.711 | -702426.711 | -702426.711 | -702426.711 | -702426.711
Option 2C |  |  |  | $ | -3386005.7908 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461
Option 2D |  |  |  | $ | -8169082.7394 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691
Option 3A |  |  |  | $ | -7721951.6891 | 0 | 0 | 0 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | -7721951.6891 | 0 | 0 | 0 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
TSNP network service payments to NNO proponents
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
NNO operating expenditure
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided fuel consumption from generation dispatch
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided voluntary load curtailment
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding outside of NW Slopes
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding in NW Slopes
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 87932829.9747 | 0 | 0 | 0 | 18935997.5153 | 33999468.6756 | 35049645.3143 | 35213735.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 87932829.9747 | 0 | 0 | 0 | 18935997.5153 | 33999468.6756 | 35049645.3143 | 35213735.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 42293588.6531 | 0 | 0 | 0 | 0 | 0 | 27960953.0035 | 35213735.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 37378758.507 | 0 | 0 | 0 | 0 | 0 | 20905078.7127 | 35213735.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 42293588.6531 | 0 | 0 | 0 | 0 | 0 | 27960953.0035 | 35213735.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 42293588.6531 | 0 | 0 | 0 | 0 | 0 | 27960953.0035 | 35213735.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 81460613.0262 | 0 | 0 | 0 | 10895582.6258 | 33999468.6756 | 35049645.3143 | 35213735.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 81460613.0262 | 0 | 0 | 0 | 10895582.6258 | 33999468.6756 | 35049645.3143 | 35213735.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided costs for non RIT-T proponent parties
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (wood pole replacement)
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 730267.4054 | 0 | 0 | 0 | 0 | 0 | 0 | 9925.0392 | 9925.0392 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 466476.8436 | 466476.8436
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 744612.6518 | 0 | 0 | 0 | 0 | 9925.0392 | 9925.0392 | 9925.0392 | 9925.0392 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 466476.8436 | 466476.8436
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 744612.6518 | 0 | 0 | 0 | 0 | 9925.0392 | 9925.0392 | 9925.0392 | 9925.0392 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 466476.8436 | 466476.8436
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (market benefits)
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
NNO receipts received from TNSP
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Payback analysis
PV gross benefits
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ |  | 0 | 0 | 0 | 15242731.3441 | 25458820.1564 | 24414133.0045 | 22817145.4697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ |  | 0 | 0 | 0 | 15242731.3441 | 25458820.1564 | 24414133.0045 | 22817145.4697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 19476443.1833 | 22817145.4697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 14561613.0373 | 22823576.5132 | 5982.366 | 38954.9416 | 36237.155 | 33708.9814 | 31357.192 | 29169.4809 | 69774.1736 | 64906.208 | 60377.8679 | 56165.4585 | 52246.9382 | 126904.7077 | 118050.8909
Option 2C |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 19476443.1833 | 22817145.4697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 19476443.1833 | 22817145.4697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ |  | 0 | 0 | 0 | 8770514.3956 | 25466252.0311 | 24421046.3762 | 22823576.5132 | 5982.366 | 38954.9416 | 36237.155 | 33708.9814 | 31357.192 | 29169.4809 | 69774.1736 | 64906.208 | 60377.8679 | 56165.4585 | 52246.9382 | 126904.7077 | 118050.8909
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ |  | 0 | 0 | 0 | 8770514.3956 | 25466252.0311 | 24421046.3762 | 22823576.5132 | 5982.366 | 38954.9416 | 36237.155 | 33708.9814 | 31357.192 | 29169.4809 | 69774.1736 | 64906.208 | 60377.8679 | 56165.4585 | 52246.9382 | 126904.7077 | 118050.8909
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Cumulative PV gross benefits
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ |  | 0 | 0 | 0 | 15242731.3441 | 40701551.5006 | 65115684.505 | 87932829.9747 | 87932829.9747 | 87932829.9747 | 87932829.9747 | 87932829.9747 | 87932829.9747 | 87932829.9747 | 87932829.9747 | 87932829.9747 | 87932829.9747 | 87932829.9747 | 87932829.9747 | 87932829.9747 | 87932829.9747
Option 1B |  |  |  | $ |  | 0 | 0 | 0 | 15242731.3441 | 40701551.5006 | 65115684.505 | 87932829.9747 | 87932829.9747 | 87932829.9747 | 87932829.9747 | 87932829.9747 | 87932829.9747 | 87932829.9747 | 87932829.9747 | 87932829.9747 | 87932829.9747 | 87932829.9747 | 87932829.9747 | 87932829.9747 | 87932829.9747
Option 2A |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 19476443.1833 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531
Option 2B |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 14561613.0373 | 37385189.5505 | 37391171.9165 | 37430126.8582 | 37466364.0132 | 37500072.9946 | 37531430.1865 | 37560599.6675 | 37630373.8411 | 37695280.0491 | 37755657.9171 | 37811823.3756 | 37864070.3138 | 37990975.0215 | 38109025.9125
Option 2C |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 19476443.1833 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531
Option 2D |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 19476443.1833 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531 | 42293588.6531
Option 3A |  |  |  | $ |  | 0 | 0 | 0 | 8770514.3956 | 34236766.4266 | 58657812.8029 | 81481389.3161 | 81487371.6821 | 81526326.6237 | 81562563.7787 | 81596272.7601 | 81627629.9521 | 81656799.433 | 81726573.6067 | 81791479.8147 | 81851857.6826 | 81908023.1412 | 81960270.0794 | 82087174.7871 | 82205225.678
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ |  | 0 | 0 | 0 | 8770514.3956 | 34236766.4266 | 58657812.8029 | 81481389.3161 | 81487371.6821 | 81526326.6237 | 81562563.7787 | 81596272.7601 | 81627629.9521 | 81656799.433 | 81726573.6067 | 81791479.8147 | 81851857.6826 | 81908023.1412 | 81960270.0794 | 82087174.7871 | 82205225.678
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Total cost
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ |  | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734
Option 1B |  |  |  | $ |  | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734 | 78394068.8734
Option 2A |  |  |  | $ |  | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524
Option 2B |  |  |  | $ |  | 77918358.4684 | 77918358.4684 | 77918358.4684 | 77918358.4684 | 77918358.4684 | 77918358.4684 | 77918358.4684 | 77918358.4684 | 77918358.4684 | 77918358.4684 | 77918358.4684 | 77918358.4684 | 77918358.4684 | 77918358.4684 | 77918358.4684 | 77918358.4684 | 77918358.4684 | 77918358.4684 | 77918358.4684 | 77918358.4684
Option 2C |  |  |  | $ |  | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524 | 60852860.8524
Option 2D |  |  |  | $ |  | 132334998.5418 | 132334998.5418 | 132334998.5418 | 132334998.5418 | 132334998.5418 | 132334998.5418 | 132334998.5418 | 132334998.5418 | 132334998.5418 | 132334998.5418 | 132334998.5418 | 132334998.5418 | 132334998.5418 | 132334998.5418 | 132334998.5418 | 132334998.5418 | 132334998.5418 | 132334998.5418 | 132334998.5418 | 132334998.5418
Option 3A |  |  |  | $ |  | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ |  | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418 | 86961289.0418
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Payback
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ |  | NO | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 1B |  |  |  | $ |  | NO | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2A |  |  |  | $ |  | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO
Option 2B |  |  |  | $ |  | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO
Option 2C |  |  |  | $ |  | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO
Option 2D |  |  |  | $ |  | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO
Option 3A |  |  |  | $ |  | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO
Option 3B |  |  |  | $ |  | NO | NO | NO | NO | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 3C |  |  |  | $ |  | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO
Option 5A |  |  |  | $ |  | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO
Option 5B |  |  |  | $ |  | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO
Option 5C |  |  |  | $ |  | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO

## S3
S3 |  | High
NPV results
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 929814760.6724 | -2405014.4777 | -9675029.4672 | -50337900.4663 | 58035622.8203 | 286508538.0135 | 299213650.3323 | 387931670.6567 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | 114657699.1113
Option 1B |  |  |  | $ | 956731144.7407 | -1857034.2041 | -8907354.998 | -49070743.0919 | 122926578.3202 | 268248923.565 | 287606715.9476 | 359150277.593 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | 129128118.4014
Option 2A |  |  |  | $ | 478811915.7718 | -639774.1355 | -3114247.3859 | -4555760.425 | -11080984.7824 | -61592182.7602 | 179549808.6331 | 389143035.471 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | 85953069.7454
Option 2B |  |  |  | $ | 440613650.2976 | -794489.0227 | -3120367.9454 | -5265944.4735 | -33142568.0919 | -49228641.2066 | 154143070.4229 | 389496161.9023 | -1174418.3139 | -1147193.4697 | -1147193.4697 | -1147193.4697 | -1147193.4697 | -1147193.4697 | -1097281.2555 | -1097281.2555 | -1097281.2555 | -1097281.2555 | -1097281.2555 | -965694.5088 | 72768541.3505
Option 2C |  |  |  | $ | 461810395.8645 | -639774.1355 | -3192126.6038 | -4765300.8653 | -11908178.3437 | -87589031.0089 | 155264277.1993 | 397020552.985 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | 122067649.7792
Option 2D |  |  |  | $ | 440143454.134 | -1047727.3287 | -3655062.9393 | -6997954.1253 | -48947842.8746 | -122901065.9699 | 217315427.2135 | 388334153.2481 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | 130999602.3186
Option 3A |  |  |  | $ | 961764468.6489 | -1335404.0389 | -4758051.7973 | -20444327.8717 | 32980120.0839 | 316067778.6245 | 312674821.9648 | 389252678.2374 | -1417901.9788 | -1390677.1346 | -1390677.1346 | -1390677.1346 | -1390677.1346 | -1390677.1346 | -1340764.9204 | -1340764.9204 | -1340764.9204 | -1340764.9204 | -1340764.9204 | -1209178.1737 | 67207299.5965
Option 3B |  |  |  | $ | 945278363.0623 | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 945808757.2927 | -1203159.512 | -4741581.3533 | -20193257.2757 | 38993478.341 | 294963255.8649 | 276249126.4452 | 397130195.7514 | -1612493.8966 | -1585269.0524 | -1585269.0524 | -1585269.0524 | -1585269.0524 | -1585269.0524 | -1535356.8382 | -1535356.8382 | -1535356.8382 | -1535356.8382 | -1535356.8382 | -1403770.0915 | 103921704.8736
Option 5A |  |  |  | $ | 968657768.5522 | Redacted to preserve confidentiality
Option 5B |  |  |  | $ | 1068307927.6386 | Redacted to preserve confidentiality
Option 5C |  |  |  | $ | 1048309619.2179 | Redacted to preserve confidentiality
S3 |  | Calculation
Capital cost calculation
Option | Stage | Components | TNSP | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | Terminal value | Years in analysis period | Annual depreciation
Option 1A | 1 | 3rd Narrabri Tx | 1 | $ | -3521058.6458 | -422218.9934 | -2465134.9424 | -3241780.8617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3524252.5086 | 3524252.5086 | 17 | 153228.3699
Option 1A | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -23198488.6244 | -349642.1962 | -985330.4618 | -36877289.0145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19652020.2887 | 19652020.2887 | 17 | 1091778.9049
Option 1A | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -7931773.5835 | -952928.4875 | -5011712.6137 | -7860228.1638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7949299.8274 | 7949299.8274 | 17 | 345621.7316
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -10521551.413 | 0 | -132244.527 | -226594.1889 | -687205.2253 | -7527757.0437 | -12420082.5327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12596330.1105 | 12596330.1105 | 14 | 599825.2434
Option 1A | 1 | Upgrade 968 line to 160 MVA rating | 1 | $ | -60627215.1471 | -680224.8006 | -1080606.9224 | -2132008.2374 | -73002033.1774 | -34617388.6372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63721292.4429 | 63721292.4429 | 15 | 3186064.6221
Option 1A | 2 | 60 MVAr SVC at Narrabri | 1 | $ | -6360116.6386 | 0 | 0 | 0 | 0 | -785682.9048 | -5226312.8318 | -8733801.8658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9953413.3817 | 9953413.3817 | 13 | 368644.9401
Option 1B | 1 | 3rd Narrabri Tx | 1 | $ | -3521058.6458 | -422218.9934 | -2465134.9424 | -3241780.8617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3524252.5086 | 3524252.5086 | 17 | 153228.3699
Option 1B | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -23198488.6244 | -349642.1962 | -985330.4618 | -36877289.0145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19652020.2887 | 19652020.2887 | 17 | 1091778.9049
Option 1B | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -7931773.5835 | -952928.4875 | -5011712.6137 | -7860228.1638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7949299.8274 | 7949299.8274 | 17 | 345621.7316
Option 1B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -11728149.9149 | -132244.527 | -226594.1889 | -687205.2253 | -7527757.0437 | -12420082.5327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11396679.6238 | 11396679.6238 | 16 | 599825.2434
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | -30046574.3708 | 0 | -218582.7912 | -404239.8267 | -1270525.8591 | -12790442.0547 | -23170241.4593 | -39002025.0865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56873482.2374 | 56873482.2374 | 13 | 1537121.1416
Option 2A | 1 | 3rd Narrabri Tx | 1 | $ | -3521058.6458 | -422218.9934 | -2465134.9424 | -3241780.8617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3524252.5086 | 3524252.5086 | 17 | 153228.3699
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -14417783.641 | 0 | -228577.6335 | -405508.8001 | -1379134.8973 | -11530404.3737 | -20941152.9589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24829040.6377 | 24829040.6377 | 14 | 689695.5733
Option 2A | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | -20476149.6954 | -217555.1421 | -288290.2831 | -681876.5743 | -8932922.8625 | -28091616.7955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21835578.09 | 21835578.09 | 15 | 1091778.9045
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -10521551.413 | 0 | -132244.527 | -226594.1889 | -687205.2253 | -7527757.0437 | -12420082.5327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12596330.1105 | 12596330.1105 | 14 | 599825.2434
Option 2A | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -6360116.4826 | 0 | 0 | 0 | 0 | -785682.75 | -5226312.75 | -8733801.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9953413.1438 | 9953413.1438 | 13 | 368644.9313
Option 2B | 1 | 3rd Narrabri Tx | 1 | $ | -3521058.6458 | -422218.9934 | -2465134.9424 | -3241780.8617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3524252.5086 | 3524252.5086 | 17 | 153228.3699
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -20139689.2881 | -240025.5024 | -428638.8141 | -1336958.3866 | -11958089.2508 | -29041154.1267 | -3548002.4469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33518065.3398 | 33518065.3398 | 14 | 931057.3706
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -11313331.498 | -132244.527 | -226594.1889 | -687205.2253 | -7527757.0437 | -12420082.5327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11996504.8671 | 11996504.8671 | 15 | 599825.2434
Option 2B | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -6360116.4826 | 0 | 0 | 0 | 0 | -785682.75 | -5226312.75 | -8733801.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9953413.1438 | 9953413.1438 | 13 | 368644.9313
Option 2C | 1 | 3rd Narrabri Tx | 1 | $ | -3521058.6458 | -422218.9934 | -2465134.9424 | -3241780.8617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3524252.5086 | 3524252.5086 | 17 | 153228.3699
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -14417783.641 | 0 | -228577.6335 | -405508.8001 | -1379134.8973 | -11530404.3737 | -20941152.9589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24829040.6377 | 24829040.6377 | 14 | 689695.5733
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating | 1 | $ | -20476149.6954 | -217555.1421 | -288290.2831 | -681876.5743 | -8932922.8625 | -28091616.7955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21835578.09 | 21835578.09 | 15 | 1091778.9045
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -20259539.4219 | 0 | -210123.7449 | -436134.6292 | -1514398.7866 | -14960288.0423 | -32076926.7165 | -1136202.6829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37247215.2058 | 37247215.2058 | 13 | 1006681.4921
Option 2D | 1 | 3rd Narrabri Tx | 1 | $ | -3521058.6458 | -422218.9934 | -2465134.9424 | -3241780.8617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3524252.5086 | 3524252.5086 | 17 | 153228.3699
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -41044119.4222 | -275708.6662 | -675043.5249 | -2387091.464 | -15080441.171 | -74516962.0945 | -2215698.4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68508680.6772 | 68508680.6772 | 14 | 1903018.9077
Option 2D | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | -20476149.6954 | -217555.1421 | -288290.2831 | -681876.5743 | -8932922.8625 | -28091616.7955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21835578.09 | 21835578.09 | 15 | 1091778.9045
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -11313331.498 | -132244.527 | -226594.1889 | -687205.2253 | -7527757.0437 | -12420082.5327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11996504.8671 | 11996504.8671 | 15 | 599825.2434
Option 2D | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -6360116.4826 | 0 | 0 | 0 | 0 | -785682.75 | -5226312.75 | -8733801.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9953413.1438 | 9953413.1438 | 13 | 368644.9313
Option 3A | 1 | 3rd Narrabri Tx | 1 | $ | -3521058.6458 | -422218.9934 | -2465134.9424 | -3241780.8617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3524252.5086 | 3524252.5086 | 17 | 153228.3699
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | -31986508.9499 | -780940.5186 | -2066322.666 | -16265383.2848 | -45701496.9256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42777334.6407 | 42777334.6407 | 17 | 1296282.8679
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -11313331.498 | -132244.527 | -226594.1889 | -687205.2253 | -7527757.0437 | -12420082.5327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11996504.8671 | 11996504.8671 | 15 | 599825.2434
Option 3A | 2 | 60 MVAr SVC at Narrabri 132 | 1 | $ | -6360116.4826 | 0 | 0 | 0 | 0 | -785682.75 | -5226312.75 | -8733801.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9953413.1438 | 9953413.1438 | 13 | 368644.9313
Option 3B | 1 | 3rd Narrabri Tx | 1 | $ | -3521058.6458 | -422218.9934 | -2465134.9424 | -3241780.8617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3524252.5086 | 3524252.5086 | 17 | 153228.3699
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | -31986508.9499 | -780940.5186 | -2066322.666 | -16265383.2848 | -45701496.9256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42777334.6407 | 42777334.6407 | 17 | 1296282.8679
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -11313331.498 | -132244.527 | -226594.1889 | -687205.2253 | -7527757.0437 | -12420082.5327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11996504.8671 | 11996504.8671 | 15 | 599825.2434
Option 3B | 2 | Install 50 MW / 50 MWh BESS at Narrabri 132 | 1 | $ |  | Redacted to preserve confidentiality | [19 empty] | Redacted to preserve confidentiality
Option 3C | 1 | 3rd Narrabri Tx | 1 | $ | -3521058.6458 | -422218.9934 | -2465134.9424 | -3241780.8617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3524252.5086 | 3524252.5086 | 17 | 153228.3699
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | -31986508.9499 | -780940.5186 | -2066322.666 | -16265383.2848 | -45701496.9256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42777334.6407 | 42777334.6407 | 17 | 1296282.8679
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -20259539.4219 | 0 | -210123.7449 | -436134.6292 | -1514398.7866 | -14960288.0423 | -32076926.7165 | -1136202.6829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37247215.2058 | 37247215.2058 | 13 | 1006681.4921
Option 5A | 1 | 3rd Narrabri Tx | 1 | $ | -3521058.6458 | -422218.9934 | -2465134.9424 | -3241780.8617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3524252.5086 | 3524252.5086 | 17 | 153228.3699
Option 5A | 1 | BESS at Gunnedah | 0 | $ |  | Redacted to preserve confidentiality | [19 empty] | Redacted to preserve confidentiality
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | -24917757.5398 | 0 | 0 | 0 | -780940.5186 | -2066322.666 | -16265383.2848 | -45701496.9256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47962466.1123 | 47962466.1123 | 13 | 1296282.8679
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -9737017.7469 | 0 | 0 | -132244.527 | -226594.1889 | -687205.2253 | -7527757.0437 | -12420082.5327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13196155.3539 | 13196155.3539 | 13 | 599825.2434
Option 5B | 1 | 3rd Narrabri Tx | 1 | $ | -3521058.6458 | -422218.9934 | -2465134.9424 | -3241780.8617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3524252.5086 | 3524252.5086 | 17 | 153228.3699
Option 5B | 1 | BESS near Gunnedah | 0 | $ |  | Redacted to preserve confidentiality | [19 empty] | Redacted to preserve confidentiality
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | -24917757.5398 | 0 | 0 | 0 | -780940.5186 | -2066322.666 | -16265383.2848 | -45701496.9256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47962466.1123 | 47962466.1123 | 13 | 1296282.8679
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -9737017.7469 | 0 | 0 | -132244.527 | -226594.1889 | -687205.2253 | -7527757.0437 | -12420082.5327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13196155.3539 | 13196155.3539 | 13 | 599825.2434
Option 5C | 1 | 3rd Narrabri Tx | 1 | $ | -3521058.6458 | -422218.9934 | -2465134.9424 | -3241780.8617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3524252.5086 | 3524252.5086 | 17 | 153228.3699
Option 5C | 1 | BESS at Gunnedah | 0 | $ |  | Redacted to preserve confidentiality | [19 empty] | Redacted to preserve confidentiality
Option 5C | 2 | Rebuild 969 line as double circuit | 1 | $ | -24917757.5398 | 0 | 0 | 0 | -780940.5186 | -2066322.666 | -16265383.2848 | -45701496.9256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47962466.1123 | 47962466.1123 | 13 | 1296282.8679
Option 5C | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -9737017.7469 | 0 | 0 | -132244.527 | -226594.1889 | -687205.2253 | -7527757.0437 | -12420082.5327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13196155.3539 | 13196155.3539 | 13 | 599825.2434
Biodiversity offset costs
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | -3907930.1408 | 0 | 0 | 0 | 0 | -9450000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6993000 | 6993000 | 13 | 189000
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -2596266.0075 | 0 | 0 | 0 | 0 | -6075000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4374000 | 4374000 | 14 | 121500
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -2706441.0043 | 0 | 0 | 0 | -6075000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4374000 | 4374000 | 14 | 121500
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -2596266.0075 | 0 | 0 | 0 | 0 | -6075000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4374000 | 4374000 | 14 | 121500
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -4900420.3353 | 0 | 0 | 0 | 0 | -11850000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8769000 | 8769000 | 13 | 237000
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -2706441.0043 | 0 | 0 | 0 | -6075000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4374000 | 4374000 | 14 | 121500
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -4900420.3353 | 0 | 0 | 0 | 0 | -11850000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8769000 | 8769000 | 13 | 237000
Property allowances
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | -13740381.9743 | 0 | 0 | 0 | 0 | -26250000 | -7290000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24819600 | 24819600 | 13 | 670800
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -6031380.5217 | 0 | 0 | 0 | 0 | -7500000 | -6900000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10368000 | 10368000 | 14 | 288000
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -6290130.5323 | 0 | 0 | 0 | -7500000 | -6900000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10368000 | 10368000 | 14 | 288000
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -6031380.5217 | 0 | 0 | 0 | 0 | -7500000 | -6900000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10368000 | 10368000 | 14 | 288000
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -7001652.1256 | 0 | 0 | 0 | 0 | -7500000 | -9855000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12842700 | 12842700 | 13 | 347100
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -8005646.861 | 0 | 0 | 0 | -11250000 | -7005000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13143600 | 13143600 | 14 | 365100
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | -126351.4929 | 0 | 0 | -249958.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164972.61 | 164972.61 | 17 | 4999.17
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | -126351.4929 | 0 | 0 | -249958.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164972.61 | 164972.61 | 17 | 4999.17
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | -126351.4929 | 0 | 0 | -249958.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164972.61 | 164972.61 | 17 | 4999.17
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -7001652.1256 | 0 | 0 | 0 | 0 | -7500000 | -9855000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12842700 | 12842700 | 13 | 347100
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | -98921.1783 | 0 | 0 | 0 | 0 | 0 | -249958.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184969.29 | 184969.29 | 13 | 4999.17
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | -98921.1783 | 0 | 0 | 0 | 0 | 0 | -249958.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184969.29 | 184969.29 | 13 | 4999.17
Option 5C | 2 | Rebuild 969 line as double circuit | 1 | $ | -98921.1783 | 0 | 0 | 0 | 0 | 0 | -249958.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184969.29 | 184969.29 | 13 | 4999.17
TNSP capital costs
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | -112160204.0524 | -2405014.4777 | -9675029.4672 | -50337900.4663 | -73689238.4027 | -42930828.5858 | -17646395.3645 | -8733801.8658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117396608.5597
Option 1B |  |  |  | $ | -94074357.2545 | -1857034.2041 | -8907354.998 | -49070743.0919 | -8798282.9028 | -60910524.5873 | -30460241.4593 | -39002025.0865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131208334.4858
Option 2A |  |  |  | $ | -63924306.407 | -639774.1355 | -3114247.3859 | -4555760.425 | -10999262.9851 | -61510460.9629 | -45487548.2416 | -8733801.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87480614.4905
Option 2B |  |  |  | $ | -50330767.4509 | -794489.0227 | -3120367.9454 | -5265944.4735 | -33060846.2946 | -49146919.4093 | -8774315.1969 | -8733801.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73734235.8593
Option 2C |  |  |  | $ | -79204250.3942 | -639774.1355 | -3192126.6038 | -4765300.8653 | -11826456.5464 | -87507309.2116 | -69773079.6754 | -1136202.6829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123789786.4421
Option 2D |  |  |  | $ | -93426863.6092 | -1047727.3287 | -3655062.9393 | -6997954.1253 | -48866121.0773 | -122819344.1726 | -7442011.2143 | -8733801.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133336029.2867
Option 3A |  |  |  | $ | -53307367.0691 | -1335404.0389 | -4758051.7973 | -20444327.8717 | -53229253.9693 | -13205765.2827 | -5226312.75 | -8733801.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68416477.7702
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | -67795530.9714 | -1203159.512 | -4741581.3533 | -20193257.2757 | -47215895.7122 | -34310288.0423 | -41931926.7165 | -1136202.6829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105325474.9651
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
NNO capital costs
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Operating cost calculation
Option | Stage | Component | TNSP | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A | 1 | 3rd Narrabri Tx | 1 | $ | -1127250.5774 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 1A | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -7027875.1334 | 0 | 0 | 0 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223
Option 1A | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -2542625.081 | 0 | 0 | 0 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -3084007.0526 | 0 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 1A | 1 | Upgrade 968 line to 160 MVA rating | 1 | $ | -17730492.3251 | 0 | 0 | 0 | 0 | 0 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157
Option 1A | 2 | 60 MVAr SVC at Narrabri | 1 | $ | -1991165.607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347
Option 1B | 1 | 3rd Narrabri Tx | 1 | $ | -1127250.5774 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 1B | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -7027875.1334 | 0 | 0 | 0 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223
Option 1B | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -2542625.081 | 0 | 0 | 0 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902
Option 1B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -3597042.9428 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | -10378084.7716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277
Option 2A | 1 | 3rd Narrabri Tx | 1 | $ | -1127250.5774 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -5065823.125 | 0 | 0 | 0 | 0 | 0 | 0 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488
Option 2A | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | -6075764.2367 | 0 | 0 | 0 | 0 | 0 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -3084007.0526 | 0 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 2A | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -1991165.5594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63
Option 2B | 1 | 3rd Narrabri Tx | 1 | $ | -1127250.5774 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -6838628.7244 | 0 | 0 | 0 | 0 | 0 | 0 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -3338035.5188 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 2B | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -1991165.5594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63
Option 2C | 1 | 3rd Narrabri Tx | 1 | $ | -1127250.5774 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -5065823.125 | 0 | 0 | 0 | 0 | 0 | 0 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating | 1 | $ | -6075764.2367 | 0 | 0 | 0 | 0 | 0 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -6796748.5321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947
Option 2D | 1 | 3rd Narrabri Tx | 1 | $ | -1127250.5774 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -13977699.0945 | 0 | 0 | 0 | 0 | 0 | 0 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718
Option 2D | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | -6075764.2367 | 0 | 0 | 0 | 0 | 0 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -3338035.5188 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 2D | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -1991165.5594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63
Option 3A | 1 | 3rd Narrabri Tx | 1 | $ | -1127250.5774 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | -11920406.8726 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -3338035.5188 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 3A | 2 | 60 MVAr SVC at Narrabri 132 | 1 | $ | -1991165.5594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63
Option 3B | 1 | 3rd Narrabri Tx | 1 | $ | -1127250.5774 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | -11920406.8726 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -3338035.5188 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 3B | 2 | Install 50 MW / 50 MWh BESS at Narrabri 132 | 1 | $ |  | Redacted to preserve confidentiality
Option 3C | 1 | 3rd Narrabri Tx | 1 | $ | -1127250.5774 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | -11920406.8726 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -6796748.5321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947
Option 5A | 1 | 3rd Narrabri Tx | 1 | $ | -1127250.5774 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 5A | 1 | BESS at Gunnedah | 0 | $ |  | Redacted to preserve confidentiality
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | -8752032.0471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -2834861.8328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 5B | 1 | 3rd Narrabri Tx | 1 | $ | -1127250.5774 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 5B | 1 | BESS near Gunnedah | 0 | $ |  | Redacted to preserve confidentiality
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | -8752032.0471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -2834861.8328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 5C | 1 | 3rd Narrabri Tx | 1 | $ | -1127250.5774 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 5C | 1 | BESS at Gunnedah | 0 | $ |  | Redacted to preserve confidentiality
Option 5C | 2 | Rebuild 969 line as double circuit | 1 | $ | -8752032.0471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 5C | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -2834861.8328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Biodiversity offset costs
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Property allowances
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5C | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TNSP operating expenditure
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | -33503415.7766 | 0 | 0 | 0 | -775550.2098 | -775550.2098 | -2262380.3668 | -2542298.8137 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484
Option 1B |  |  |  | $ | -24672878.5062 | 0 | 0 | 0 | -775550.2098 | -1055468.6567 | -1055468.6567 | -1055468.6567 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844
Option 2A |  |  |  | $ | -17344010.5511 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -591218.6194 | -1330934.1151 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451
Option 2B |  |  |  | $ | -13295080.3799 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -361640.2442 | -982345.1579 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879
Option 2C |  |  |  | $ | -19065586.4712 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -591218.6194 | -1051015.6682 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629
Option 2D |  |  |  | $ | -26509914.9867 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -871137.0663 | -2139816.3381 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681
Option 3A |  |  |  | $ | -18376858.5282 | 0 | 0 | 0 | -945910.3759 | -945910.3759 | -1225828.8228 | -1225828.8228 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | -19844405.9821 | 0 | 0 | 0 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
TSNP network service payments to NNO proponents
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
NNO operating expenditure
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided fuel consumption from generation dispatch
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided voluntary load curtailment
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding outside of NW Slopes
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding in NW Slopes
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 1075478380.5014 | 0 | 0 | 0 | 132500411.4328 | 330214916.8091 | 319122426.0636 | 399207771.3362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 1075478380.5014 | 0 | 0 | 0 | 132500411.4328 | 330214916.8091 | 319122426.0636 | 399207771.3362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 560080232.7299 | 0 | 0 | 0 | 0 | 0 | 225628575.4941 | 399207771.3362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 503497465.0304 | 0 | 0 | 0 | 0 | 0 | 163279025.8641 | 399207771.3362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 560080232.7299 | 0 | 0 | 0 | 0 | 0 | 225628575.4941 | 399207771.3362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 560080232.7299 | 0 | 0 | 0 | 0 | 0 | 225628575.4941 | 399207771.3362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 1032698344.8437 | 0 | 0 | 0 | 87155284.4291 | 330214916.8091 | 319122426.0636 | 399207771.3362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 1032698344.8437 | 0 | 0 | 0 | 87155284.4291 | 330214916.8091 | 319122426.0636 | 399207771.3362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided costs for non RIT-T proponent parties
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (wood pole replacement)
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 742033.0981 | 0 | 0 | 0 | 0 | 0 | 0 | 4537.474 | 4537.474 | 31762.3182 | 31762.3182 | 31762.3182 | 31762.3182 | 31762.3182 | 81674.5324 | 81674.5324 | 81674.5324 | 81674.5324 | 81674.5324 | 213261.2791 | 213261.2791
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 750349.4025 | 0 | 0 | 0 | 0 | 4537.474 | 4537.474 | 4537.474 | 4537.474 | 31762.3182 | 31762.3182 | 31762.3182 | 31762.3182 | 31762.3182 | 81674.5324 | 81674.5324 | 81674.5324 | 81674.5324 | 81674.5324 | 213261.2791 | 213261.2791
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 750349.4025 | 0 | 0 | 0 | 0 | 4537.474 | 4537.474 | 4537.474 | 4537.474 | 31762.3182 | 31762.3182 | 31762.3182 | 31762.3182 | 31762.3182 | 81674.5324 | 81674.5324 | 81674.5324 | 81674.5324 | 81674.5324 | 213261.2791 | 213261.2791
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (market benefits)
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
NNO receipts received from TNSP
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Payback analysis
PV gross benefits
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ |  | 0 | 0 | 0 | 125005104.1933 | 305546547.3407 | 289606423.9242 | 355320305.0432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ |  | 0 | 0 | 0 | 125005104.1933 | 305546547.3407 | 289606423.9242 | 355320305.0432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 204759927.6867 | 355320305.0432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 148177159.9872 | 355324343.6837 | 3961.0048 | 27194.0303 | 26671.2734 | 26158.5655 | 25655.7135 | 25162.5279 | 63459.8306 | 62239.928 | 61043.4759 | 59870.0234 | 58719.1285 | 150374.8224 | 147484.1334
Option 2C |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 204759927.6867 | 355320305.0432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 204759927.6867 | 355320305.0432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ |  | 0 | 0 | 0 | 82225068.5356 | 305550745.8473 | 289610541.722 | 355324343.6837 | 3961.0048 | 27194.0303 | 26671.2734 | 26158.5655 | 25655.7135 | 25162.5279 | 63459.8306 | 62239.928 | 61043.4759 | 59870.0234 | 58719.1285 | 150374.8224 | 147484.1334
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ |  | 0 | 0 | 0 | 82225068.5356 | 305550745.8473 | 289610541.722 | 355324343.6837 | 3961.0048 | 27194.0303 | 26671.2734 | 26158.5655 | 25655.7135 | 25162.5279 | 63459.8306 | 62239.928 | 61043.4759 | 59870.0234 | 58719.1285 | 150374.8224 | 147484.1334
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Cumulative PV gross benefits
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ |  | 0 | 0 | 0 | 125005104.1933 | 430551651.534 | 720158075.4582 | 1075478380.5014 | 1075478380.5014 | 1075478380.5014 | 1075478380.5014 | 1075478380.5014 | 1075478380.5014 | 1075478380.5014 | 1075478380.5014 | 1075478380.5014 | 1075478380.5014 | 1075478380.5014 | 1075478380.5014 | 1075478380.5014 | 1075478380.5014
Option 1B |  |  |  | $ |  | 0 | 0 | 0 | 125005104.1933 | 430551651.534 | 720158075.4582 | 1075478380.5014 | 1075478380.5014 | 1075478380.5014 | 1075478380.5014 | 1075478380.5014 | 1075478380.5014 | 1075478380.5014 | 1075478380.5014 | 1075478380.5014 | 1075478380.5014 | 1075478380.5014 | 1075478380.5014 | 1075478380.5014 | 1075478380.5014
Option 2A |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 204759927.6867 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299
Option 2B |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 148177159.9872 | 503501503.6708 | 503505464.6756 | 503532658.7059 | 503559329.9793 | 503585488.5448 | 503611144.2583 | 503636306.7862 | 503699766.6168 | 503762006.5448 | 503823050.0207 | 503882920.0442 | 503941639.1727 | 504092013.9951 | 504239498.1285
Option 2C |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 204759927.6867 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299
Option 2D |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 204759927.6867 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299 | 560080232.7299
Option 3A |  |  |  | $ |  | 0 | 0 | 0 | 82225068.5356 | 387775814.3829 | 677386356.1049 | 1032710699.7886 | 1032714660.7934 | 1032741854.8237 | 1032768526.097 | 1032794684.6625 | 1032820340.376 | 1032845502.904 | 1032908962.7346 | 1032971202.6626 | 1033032246.1385 | 1033092116.1619 | 1033150835.2905 | 1033301210.1128 | 1033448694.2462
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ |  | 0 | 0 | 0 | 82225068.5356 | 387775814.3829 | 677386356.1049 | 1032710699.7886 | 1032714660.7934 | 1032741854.8237 | 1032768526.097 | 1032794684.6625 | 1032820340.376 | 1032845502.904 | 1032908962.7346 | 1032971202.6626 | 1033032246.1385 | 1033092116.1619 | 1033150835.2905 | 1033301210.1128 | 1033448694.2462
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Total cost
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ |  | 145663619.829 | 145663619.829 | 145663619.829 | 145663619.829 | 145663619.829 | 145663619.829 | 145663619.829 | 145663619.829 | 145663619.829 | 145663619.829 | 145663619.829 | 145663619.829 | 145663619.829 | 145663619.829 | 145663619.829 | 145663619.829 | 145663619.829 | 145663619.829 | 145663619.829 | 145663619.829
Option 1B |  |  |  | $ |  | 118747235.7607 | 118747235.7607 | 118747235.7607 | 118747235.7607 | 118747235.7607 | 118747235.7607 | 118747235.7607 | 118747235.7607 | 118747235.7607 | 118747235.7607 | 118747235.7607 | 118747235.7607 | 118747235.7607 | 118747235.7607 | 118747235.7607 | 118747235.7607 | 118747235.7607 | 118747235.7607 | 118747235.7607 | 118747235.7607
Option 2A |  |  |  | $ |  | 81268316.9581 | 81268316.9581 | 81268316.9581 | 81268316.9581 | 81268316.9581 | 81268316.9581 | 81268316.9581 | 81268316.9581 | 81268316.9581 | 81268316.9581 | 81268316.9581 | 81268316.9581 | 81268316.9581 | 81268316.9581 | 81268316.9581 | 81268316.9581 | 81268316.9581 | 81268316.9581 | 81268316.9581 | 81268316.9581
Option 2B |  |  |  | $ |  | 63625847.8309 | 63625847.8309 | 63625847.8309 | 63625847.8309 | 63625847.8309 | 63625847.8309 | 63625847.8309 | 63625847.8309 | 63625847.8309 | 63625847.8309 | 63625847.8309 | 63625847.8309 | 63625847.8309 | 63625847.8309 | 63625847.8309 | 63625847.8309 | 63625847.8309 | 63625847.8309 | 63625847.8309 | 63625847.8309
Option 2C |  |  |  | $ |  | 98269836.8654 | 98269836.8654 | 98269836.8654 | 98269836.8654 | 98269836.8654 | 98269836.8654 | 98269836.8654 | 98269836.8654 | 98269836.8654 | 98269836.8654 | 98269836.8654 | 98269836.8654 | 98269836.8654 | 98269836.8654 | 98269836.8654 | 98269836.8654 | 98269836.8654 | 98269836.8654 | 98269836.8654 | 98269836.8654
Option 2D |  |  |  | $ |  | 119936778.5959 | 119936778.5959 | 119936778.5959 | 119936778.5959 | 119936778.5959 | 119936778.5959 | 119936778.5959 | 119936778.5959 | 119936778.5959 | 119936778.5959 | 119936778.5959 | 119936778.5959 | 119936778.5959 | 119936778.5959 | 119936778.5959 | 119936778.5959 | 119936778.5959 | 119936778.5959 | 119936778.5959 | 119936778.5959
Option 3A |  |  |  | $ |  | 71684225.5973 | 71684225.5973 | 71684225.5973 | 71684225.5973 | 71684225.5973 | 71684225.5973 | 71684225.5973 | 71684225.5973 | 71684225.5973 | 71684225.5973 | 71684225.5973 | 71684225.5973 | 71684225.5973 | 71684225.5973 | 71684225.5973 | 71684225.5973 | 71684225.5973 | 71684225.5973 | 71684225.5973 | 71684225.5973
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ |  | 87639936.9535 | 87639936.9535 | 87639936.9535 | 87639936.9535 | 87639936.9535 | 87639936.9535 | 87639936.9535 | 87639936.9535 | 87639936.9535 | 87639936.9535 | 87639936.9535 | 87639936.9535 | 87639936.9535 | 87639936.9535 | 87639936.9535 | 87639936.9535 | 87639936.9535 | 87639936.9535 | 87639936.9535 | 87639936.9535
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Payback
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 1B |  |  |  | $ |  | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2A |  |  |  | $ |  | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2B |  |  |  | $ |  | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2C |  |  |  | $ |  | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2D |  |  |  | $ |  | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 3A |  |  |  | $ |  | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 3B |  |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 3C |  |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 5A |  |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 5B |  |  |  | $ |  | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 5C |  |  |  | $ |  | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES

## Weighted
Weighted | NPV results
NPV results
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | 432277028.0076 | -2962774.1491 | -12680614.7436 | -67951415.4272 | 17400219.4708 | 163456018.5106 | 178378384.1064 | 232464833.4705 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | 115939256.111
Option 1B |  | $ | 451681160.1898 | -2484204.7101 | -12010179.0405 | -66844764.6536 | 74071653.9407 | 147557807.7564 | 168032463.3807 | 207071366.301 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | 128462582.1079
Option 2A |  | $ | 206582705.5553 | -769845.575 | -4066632.3383 | -5802342.2687 | -10377312.2529 | -66353559.8918 | 85168121.5044 | 233382998.2698 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | 96715646.2528
Option 2B |  | $ | 185434735.6862 | -1024975.9944 | -4172008.2173 | -6888294.4643 | -41721405.52 | -60973941.8114 | 91258790.7427 | 233586583.2598 | -1028151.9854 | -981081.509 | -981081.509 | -981081.509 | -981081.509 | -981081.509 | -894785.6354 | -894785.6354 | -894785.6354 | -894785.6354 | -894785.6354 | -667278.3325 | 89619446.5754
Option 2C |  | $ | 187778707.4094 | -769845.575 | -4134646.8553 | -5985340.92 | -11099727.9632 | -89057474.0289 | 63958757.3855 | 240214177.7012 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | 128289442.0814
Option 2D |  | $ | 147827846.0517 | -1263979.0302 | -4762177.534 | -8925982.7656 | -58960854.7904 | -148104930.0886 | 131011341.5094 | 232574116.0468 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | 159181446.3048
Option 3A |  | $ | 469602920.4479 | -1767832.6167 | -6421094.0406 | -27733274.3312 | -16464800.882 | 189253392.0419 | 189907579.3668 | 233343099.5949 | -1271635.6503 | -1224565.1739 | -1224565.1739 | -1224565.1739 | -1224565.1739 | -1224565.1739 | -1138269.3003 | -1138269.3003 | -1138269.3003 | -1138269.3003 | -1138269.3003 | -910761.9974 | 82072908.4681
Option 3B |  | $ | 458142967.0369 | Redacted to preserve confidentiality
Option 3C |  | $ | 451877872.9771 | -1652339.0631 | -6406709.8528 | -27514006.0107 | -11213134.6707 | 170822108.8318 | 158047286.0822 | 240174279.0263 | -1407849.9928 | -1360779.5163 | -1360779.5163 | -1360779.5163 | -1360779.5163 | -1360779.5163 | -1274483.6428 | -1274483.6428 | -1274483.6428 | -1274483.6428 | -1274483.6428 | -1046976.3399 | 114170551.6759
Option 5A |  | $ | 451959912.1726 | Redacted to preserve confidentiality
Option 5B |  | $ | 513435882.5259 | Redacted to preserve confidentiality
Option 5C |  | $ | 496240796.8363 | Redacted to preserve confidentiality
Weighted | Calculation
TNSP capital costs
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | -133049648.8047 | -2962774.1491 | -12680614.7436 | -67951415.4272 | -64355268.205 | -37492923.6316 | -15411185.285 | -7627520.2962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118089157.7878
Option 1B |  | $ | -118423223.7136 | -2484204.7101 | -12010179.0405 | -66844764.6536 | -7683833.7352 | -53195191.4729 | -26601944.2078 | -34061768.5755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130151398.4299
Option 2A |  | $ | -81586251.8528 | -769845.575 | -4066632.3383 | -5802342.2687 | -10295590.4556 | -66271838.0945 | -53646368.6105 | -7627520.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97947383.2282
Option 2B |  | $ | -74604133.9801 | -1024975.9944 | -4172008.2173 | -6888294.4643 | -41639683.7227 | -60892220.0141 | -9436903.1621 | -7627520.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90286724.9079
Option 2C |  | $ | -99516865.1873 | -769845.575 | -4134646.8553 | -5985340.92 | -11018006.1659 | -88975752.2316 | -74855732.7294 | -992283.6764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129657393.3993
Option 2D |  | $ | -134058719.319 | -1263979.0302 | -4762177.534 | -8925982.7656 | -58879132.9931 | -148023208.2913 | -7607205.6927 | -7627520.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161222065.5032
Option 3A |  | $ | -78988013.8635 | -1767832.6167 | -6421094.0406 | -27733274.3312 | -69337630.2627 | -11533035.0135 | -4564313.135 | -7627520.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82983670.4656
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | -95996772.7612 | -1652339.0631 | -6406709.8528 | -27514006.0107 | -64085964.0515 | -29964318.2236 | -36620549.3324 | -992283.6764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115217528.0158
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
NNO capital costs
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
TNSP operating expenditure
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | -19875070.4935 | 0 | 0 | 0 | -775550.2098 | -775550.2098 | -1816331.3197 | -2012274.2325 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768
Option 1B |  | $ | -15097363.4023 | 0 | 0 | 0 | -775550.2098 | -971493.1226 | -971493.1226 | -971493.1226 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322
Option 2A |  | $ | -10197539.8757 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -438369.5728 | -1094109.5344 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754
Option 2B |  | $ | -8332816.4921 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -277664.7101 | -898369.6238 | -1035997.0648 | -1035997.0648 | -1035997.0648 | -1035997.0648 | -1035997.0648 | -1035997.0648 | -1035997.0648 | -1035997.0648 | -1035997.0648 | -1035997.0648 | -1035997.0648 | -1035997.0648 | -1035997.0648
Option 2C |  | $ | -11070924.6871 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -438369.5728 | -898166.6216 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179
Option 2D |  | $ | -16479931.9131 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -634312.4856 | -1902991.7574 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984
Option 3A |  | $ | -12281148.4626 | 0 | 0 | 0 | -945910.3759 | -945910.3759 | -1141853.2887 | -1141853.2887 | -1279480.7297 | -1279480.7297 | -1279480.7297 | -1279480.7297 | -1279480.7297 | -1279480.7297 | -1279480.7297 | -1279480.7297 | -1279480.7297 | -1279480.7297 | -1279480.7297 | -1279480.7297 | -1279480.7297
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | -12997437.0356 | 0 | 0 | 0 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -1415695.0722 | -1415695.0722 | -1415695.0722 | -1415695.0722 | -1415695.0722 | -1415695.0722 | -1415695.0722 | -1415695.0722 | -1415695.0722 | -1415695.0722 | -1415695.0722 | -1415695.0722 | -1415695.0722
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
TSNP network service payments to NNO proponents
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
NNO operating expenditure
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
Avoided fuel consumption from generation dispatch
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
Avoided voluntary load curtailment
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding outside of NW Slopes
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding in NW Slopes
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | 585201747.3057 | 0 | 0 | 0 | 82531037.8856 | 201724492.352 | 195605900.7111 | 242104627.9992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 585201747.3057 | 0 | 0 | 0 | 82531037.8856 | 201724492.352 | 195605900.7111 | 242104627.9992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 298366497.2838 | 0 | 0 | 0 | 0 | 0 | 139252859.6877 | 242104627.9992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 267624837.1067 | 0 | 0 | 0 | 0 | 0 | 100973358.615 | 242104627.9992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 298366497.2838 | 0 | 0 | 0 | 0 | 0 | 139252859.6877 | 242104627.9992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 298366497.2838 | 0 | 0 | 0 | 0 | 0 | 139252859.6877 | 242104627.9992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 560113063.8985 | 0 | 0 | 0 | 53818739.7566 | 201724492.352 | 195605900.7111 | 242104627.9992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | 560113063.8985 | 0 | 0 | 0 | 53818739.7566 | 201724492.352 | 195605900.7111 | 242104627.9992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
Avoided costs for non RIT-T proponent parties
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (wood pole replacement)
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 746849.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 7845.0794 | 7845.0794 | 54915.5559 | 54915.5559 | 54915.5559 | 54915.5559 | 54915.5559 | 141211.4294 | 141211.4294 | 141211.4294 | 141211.4294 | 141211.4294 | 368718.7323 | 368718.7323
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 759018.8754 | 0 | 0 | 0 | 0 | 7845.0794 | 7845.0794 | 7845.0794 | 7845.0794 | 54915.5559 | 54915.5559 | 54915.5559 | 54915.5559 | 54915.5559 | 141211.4294 | 141211.4294 | 141211.4294 | 141211.4294 | 141211.4294 | 368718.7323 | 368718.7323
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | 759018.8754 | 0 | 0 | 0 | 0 | 7845.0794 | 7845.0794 | 7845.0794 | 7845.0794 | 54915.5559 | 54915.5559 | 54915.5559 | 54915.5559 | 54915.5559 | 141211.4294 | 141211.4294 | 141211.4294 | 141211.4294 | 141211.4294 | 368718.7323 | 368718.7323
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (market benefits)
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
NNO receipts received from TNSP
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
Payback analysis
PV gross benefits
Option |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  | $ |  | 0 | 0 | 0 | 72209402.5125 | 169258028.4628 | 157122008.7126 | 186612307.6177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  | $ |  | 0 | 0 | 0 | 72209402.5125 | 169258028.4628 | 157122008.7126 | 186612307.6177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 111754189.6661 | 186612307.6177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 81012529.489 | 186617901.7281 | 5292.375 | 35057.9867 | 33185.3205 | 31421.563 | 29760.0929 | 28194.703 | 68707.4748 | 65132.3511 | 61762.1354 | 58584.4877 | 55587.8335 | 137765.6585 | 130802.9593
Option 2C |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 111754189.6661 | 186612307.6177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 111754189.6661 | 186612307.6177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  | $ |  | 0 | 0 | 0 | 47120719.1054 | 169264283.648 | 157127923.3511 | 186617901.7281 | 5292.375 | 35057.9867 | 33185.3205 | 31421.563 | 29760.0929 | 28194.703 | 68707.4748 | 65132.3511 | 61762.1354 | 58584.4877 | 55587.8335 | 137765.6585 | 130802.9593
Option 3B |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  | $ |  | 0 | 0 | 0 | 47120719.1054 | 169264283.648 | 157127923.3511 | 186617901.7281 | 5292.375 | 35057.9867 | 33185.3205 | 31421.563 | 29760.0929 | 28194.703 | 68707.4748 | 65132.3511 | 61762.1354 | 58584.4877 | 55587.8335 | 137765.6585 | 130802.9593
Option 5A |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  | $ |  | Redacted to preserve confidentiality
Cumulative PV gross benefits
Option |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  | $ |  | 0 | 0 | 0 | 72209402.5125 | 241467430.9753 | 398589439.6879 | 585201747.3057 | 585201747.3057 | 585201747.3057 | 585201747.3057 | 585201747.3057 | 585201747.3057 | 585201747.3057 | 585201747.3057 | 585201747.3057 | 585201747.3057 | 585201747.3057 | 585201747.3057 | 585201747.3057 | 585201747.3057
Option 1B |  |  | $ |  | 0 | 0 | 0 | 72209402.5125 | 241467430.9753 | 398589439.6879 | 585201747.3057 | 585201747.3057 | 585201747.3057 | 585201747.3057 | 585201747.3057 | 585201747.3057 | 585201747.3057 | 585201747.3057 | 585201747.3057 | 585201747.3057 | 585201747.3057 | 585201747.3057 | 585201747.3057 | 585201747.3057
Option 2A |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 111754189.6661 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838
Option 2B |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 81012529.489 | 267630431.2171 | 267635723.5921 | 267670781.5788 | 267703966.8993 | 267735388.4623 | 267765148.5552 | 267793343.2582 | 267862050.733 | 267927183.0841 | 267988945.2195 | 268047529.7072 | 268103117.5406 | 268240883.1992 | 268371686.1585
Option 2C |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 111754189.6661 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838
Option 2D |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 111754189.6661 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838 | 298366497.2838
Option 3A |  |  | $ |  | 0 | 0 | 0 | 47120719.1054 | 216385002.7534 | 373512926.1044 | 560130827.8325 | 560136120.2075 | 560171178.1942 | 560204363.5147 | 560235785.0777 | 560265545.1706 | 560293739.8737 | 560362447.3485 | 560427579.6995 | 560489341.8349 | 560547926.3226 | 560603514.1561 | 560741279.8146 | 560872082.7739
Option 3B |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  | $ |  | 0 | 0 | 0 | 47120719.1054 | 216385002.7534 | 373512926.1044 | 560130827.8325 | 560136120.2075 | 560171178.1942 | 560204363.5147 | 560235785.0777 | 560265545.1706 | 560293739.8737 | 560362447.3485 | 560427579.6995 | 560489341.8349 | 560547926.3226 | 560603514.1561 | 560741279.8146 | 560872082.7739
Option 5A |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  | $ |  | Redacted to preserve confidentiality
Total cost
Option |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  | $ |  | 152924719.2981 | 152924719.2981 | 152924719.2981 | 152924719.2981 | 152924719.2981 | 152924719.2981 | 152924719.2981 | 152924719.2981 | 152924719.2981 | 152924719.2981 | 152924719.2981 | 152924719.2981 | 152924719.2981 | 152924719.2981 | 152924719.2981 | 152924719.2981 | 152924719.2981 | 152924719.2981 | 152924719.2981 | 152924719.2981
Option 1B |  |  | $ |  | 133520587.1159 | 133520587.1159 | 133520587.1159 | 133520587.1159 | 133520587.1159 | 133520587.1159 | 133520587.1159 | 133520587.1159 | 133520587.1159 | 133520587.1159 | 133520587.1159 | 133520587.1159 | 133520587.1159 | 133520587.1159 | 133520587.1159 | 133520587.1159 | 133520587.1159 | 133520587.1159 | 133520587.1159 | 133520587.1159
Option 2A |  |  | $ |  | 91783791.7285 | 91783791.7285 | 91783791.7285 | 91783791.7285 | 91783791.7285 | 91783791.7285 | 91783791.7285 | 91783791.7285 | 91783791.7285 | 91783791.7285 | 91783791.7285 | 91783791.7285 | 91783791.7285 | 91783791.7285 | 91783791.7285 | 91783791.7285 | 91783791.7285 | 91783791.7285 | 91783791.7285 | 91783791.7285
Option 2B |  |  | $ |  | 82936950.4723 | 82936950.4723 | 82936950.4723 | 82936950.4723 | 82936950.4723 | 82936950.4723 | 82936950.4723 | 82936950.4723 | 82936950.4723 | 82936950.4723 | 82936950.4723 | 82936950.4723 | 82936950.4723 | 82936950.4723 | 82936950.4723 | 82936950.4723 | 82936950.4723 | 82936950.4723 | 82936950.4723 | 82936950.4723
Option 2C |  |  | $ |  | 110587789.8745 | 110587789.8745 | 110587789.8745 | 110587789.8745 | 110587789.8745 | 110587789.8745 | 110587789.8745 | 110587789.8745 | 110587789.8745 | 110587789.8745 | 110587789.8745 | 110587789.8745 | 110587789.8745 | 110587789.8745 | 110587789.8745 | 110587789.8745 | 110587789.8745 | 110587789.8745 | 110587789.8745 | 110587789.8745
Option 2D |  |  | $ |  | 150538651.2321 | 150538651.2321 | 150538651.2321 | 150538651.2321 | 150538651.2321 | 150538651.2321 | 150538651.2321 | 150538651.2321 | 150538651.2321 | 150538651.2321 | 150538651.2321 | 150538651.2321 | 150538651.2321 | 150538651.2321 | 150538651.2321 | 150538651.2321 | 150538651.2321 | 150538651.2321 | 150538651.2321 | 150538651.2321
Option 3A |  |  | $ |  | 91269162.326 | 91269162.326 | 91269162.326 | 91269162.326 | 91269162.326 | 91269162.326 | 91269162.326 | 91269162.326 | 91269162.326 | 91269162.326 | 91269162.326 | 91269162.326 | 91269162.326 | 91269162.326 | 91269162.326 | 91269162.326 | 91269162.326 | 91269162.326 | 91269162.326 | 91269162.326
Option 3B |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  | $ |  | 108994209.7968 | 108994209.7968 | 108994209.7968 | 108994209.7968 | 108994209.7968 | 108994209.7968 | 108994209.7968 | 108994209.7968 | 108994209.7968 | 108994209.7968 | 108994209.7968 | 108994209.7968 | 108994209.7968 | 108994209.7968 | 108994209.7968 | 108994209.7968 | 108994209.7968 | 108994209.7968 | 108994209.7968 | 108994209.7968
Option 5A |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  | $ |  | Redacted to preserve confidentiality
Payback
Option |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 1B |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2A |  |  | $ |  | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2B |  |  | $ |  | NO | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2C |  |  | $ |  | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2D |  |  | $ |  | NO | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 3A |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 3B |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 3C |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 5A |  |  | $ |  | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 5B |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 5C |  |  | $ |  | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES