## Cover
North West Slopes amended PACR economic assessment
Legend applied throughout the model template
Table Row Name
Input Cell
Calculation cell
Parameter Cell
Output Cell

## Results
| Scenarios |  |  |  |  | S1 | S2 | S3
| General inputs and sensitivities |  |  |  | Unit | Step Change | Progressive Change | Hydrogen Superpower
| Commercial discount rate |  |  |  | % | 5.5% | 5.5% | 5.5%
| VCR |  |  |  | $/MWh | 46882.8857 | 46882.8857 | 46882.8857
| Cost inputs and sensitivities |  |  |  | Unit | Step Change | Progressive Change | Hydrogen Superpower
| Network capital costs |  |  |  | Factor | 1 | 1 | 1
| NNO capital costs |  |  |  | Factor | 1 | 1 | 1
| Operating and maintenance costs |  |  |  | Factor | 1 | 1 | 1
| Market benefit inputs and sensitivities |  |  |  | Unit | Step Change | Progressive Change | Hydrogen Superpower
| Avoided fuel consumption from generation dispatch |  |  |  | Factor | 1 | 1 | 1
| Avoided voluntary load curtailment |  |  |  | Factor | 1 | 1 | 1
| Avoided involuntary load shedding |  |  |  | Factor | 1 | 1 | 1
| Avoided costs for non RIT-T proponent parties |  |  |  | Factor | 1 | 1 | 1
| Avoided unrelated TNSP expenditure (wood pole replacement) |  |  |  | Factor | 1 | 1 | 1
| Avoided unrelated TNSP expenditure (market benefits) |  |  |  | Factor | 1 | 1 | 1
| Scenario weighting settings |  |  |  | Unit | Step Change | Progressive Change | Hydrogen Superpower
| Scenario weighting |  |  |  | % | 52% | 30% | 18%
Value
| Opex | 1%
NPV results
|  |  | S1 | S2 | S3 |  |  |  |  | Step Change |  | Progressive Change |  | Hydrogen Superpower
| Option | Unit | Step Change | Progressive Change | Hydrogen Superpower | Weighted | Rank | % |  | Rank | % | Rank | % | Rank | %
1A | Option 1A | $NPV | 503.9399 | 74.004 | 503.9399 | 374.9591 | 8 | 81.71% |  | 8 | 81.49% | 2 | 88.86% | 8 | 80.73%
1B | Option 1B | $NPV | 531.9383 | 74.004 | 531.9383 | 394.558 | 7 | 85.98% |  | 7 | 86.02% | 2 | 88.86% | 7 | 85.21%
2A | Option 2A | $NPV | 242.2391 | 18.3253 | 242.2391 | 175.065 | 9 | 38.15% |  | 9 | 39.17% | 9 | 22% | 9 | 38.81%
2B | Option 2B | $NPV | 227.0521 | -1.6148 | 227.0521 | 158.452 | 10 | 34.53% |  | 10 | 36.72% | 11 | -1.939% | 10 | 36.37%
2C | Option 2C | $NPV | 211.9627 | 18.3253 | 211.9627 | 153.8715 | 11 | 33.53% |  | 11 | 34.28% | 9 | 22% | 11 | 33.96%
2D | Option 2D | $NPV | 183.8739 | -38.327 | 183.8739 | 117.2137 | 12 | 25.54% |  | 12 | 29.73% | 12 | -46.02% | 12 | 29.46%
3A | Option 3A | $NPV | 572.908 | 58.3037 | 572.908 | 418.5267 | 3 | 91.2% |  | 3 | 92.65% | 6 | 70.01% | 3 | 91.78%
3B | Option 3B | $NPV | 550.8331 | 69.6883 | 551.6746 | 406.6412 | 4 | 88.61% |  | 5 | 89.08% | 4 | 83.68% | 5 | 88.38%
3C | Option 3C | $NPV | 544.3445 | 58.3037 | 544.3445 | 398.5322 | 5 | 86.84% |  | 6 | 88.03% | 6 | 70.01% | 6 | 87.2%
5A | Option 5A | $NPV | 552.9328 | 33.6128 | 558.302 | 398.1032 | 6 | 86.75% |  | 4 | 89.42% | 8 | 40.36% | 4 | 89.44%
5B | Option 5B | $NPV | 618.3864 | 83.2822 | 624.242 | 458.9091 | 1 | 100% |  | 1 | 100% | 1 | 100% | 1 | 100%
5C | Option 5C | $NPV | 601.9586 | 64.7897 | 605.7273 | 441.4863 | 2 | 96.2% |  | 2 | 97.34% | 5 | 77.8% | 2 | 97.03%
| S1 | Step Change | [12 empty] | S2 | Progressive Change | [11 empty] | S3 | Hydrogen Superpower | [11 empty] | Weighted
| NPV result | Step Change | [12 empty] | NPV result | Progressive Change | [11 empty] | NPV result | Hydrogen Superpower | [11 empty] | NPV result | Weighted
| NPV breakdown | Step Change | [12 empty] | NPV breakdown | Progressive Change | [11 empty] | NPV breakdown | Hydrogen Superpower | [11 empty] | NPV breakdown | Weighted
| Option | Option 1A | Option 1B | Option 2A | Option 2B | Option 2C | Option 2D | Option 3A | Option 3B | Option 3C | Option 5A | Option 5B | Option 5C |  | Option | Option 1A | Option 1B | Option 2A | Option 2B | Option 2C | Option 2D | Option 3A | Option 3B | Option 3C | Option 5A | Option 5B | Option 5C | Option | Option 1A | Option 1B | Option 2A | Option 2B | Option 2C | Option 2D | Option 3A | Option 3B | Option 3C | Option 5A | Option 5B | Option 5C | Option | Option 1A | Option 1B | Option 2A | Option 2B | Option 2C | Option 2D | Option 3A | Option 3B | Option 3C | Option 5A | Option 5B | Option 5C
| TNSP capital costs | -175.4653 | -153.598 | -101.615 | -83.5968 | -130.8078 | -153.831 | -87.7325 | -112.175 | -115.4265 | -61.2863 | -61.2863 | -61.2863 |  | TNSP capital costs | -55.4648 | -55.4648 | -44.5497 | -56.3549 | -44.5497 | -95.2669 | -60.4905 | -60.4905 | -60.4905 | -5.8628 | -5.8628 | -5.8628 | TNSP capital costs | -175.4653 | -153.598 | -101.615 | -83.5968 | -130.8078 | -153.831 | -87.7325 | -112.175 | -115.4265 | -61.2863 | -61.2863 | -61.2863 | TNSP capital costs | -139.4651 | -124.1581 | -84.4954 | -75.4242 | -104.9304 | -136.2618 | -79.5599 | -96.6697 | -98.9457 | -44.6593 | -44.6593 | -44.6593
| NNO capital costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -98.4894 | -121.667 | -123.7322 |  | NNO capital costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -98.4894 | -121.667 | -123.7322 | NNO capital costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -98.4894 | -121.667 | -123.7322 | NNO capital costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -98.4894 | -121.667 | -123.7322
| TNSP operating expenditure | -22.9713 | -16.8402 | -11.6535 | -8.9201 | -12.7371 | -17.8027 | -12.8014 | -14.9715 | -13.6709 | -8.3627 | -8.3627 | -8.3627 |  | TNSP operating expenditure | -7.5704 | -7.5704 | -4.1714 | -5.3521 | -4.1714 | -10.1065 | -9.2333 | -9.2333 | -9.2333 | -0.79771 | -0.79771 | -0.79771 | TNSP operating expenditure | -22.9713 | -16.8402 | -11.6535 | -8.9201 | -12.7371 | -17.8027 | -12.8014 | -14.9715 | -13.6709 | -8.3627 | -8.3627 | -8.3627 | TNSP operating expenditure | -18.3511 | -14.0592 | -9.4089 | -7.8497 | -10.1674 | -15.4939 | -11.731 | -13.25 | -12.3396 | -6.0932 | -6.0932 | -6.0932
| TNSP payments to NNO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -163.9904 | -46.1334 | 0 |  | TNSP payments to NNO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -163.9904 | -46.1334 | 0 | TNSP payments to NNO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -163.9904 | -46.1334 | 0 | TNSP payments to NNO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -163.9904 | -46.1334 | 0
| NNO operating expenditure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -66.8135 | -8.7176 | -11.8516 |  | NNO operating expenditure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -66.8135 | -8.7176 | -11.8516 | NNO operating expenditure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -66.8135 | -8.7176 | -11.8516 | NNO operating expenditure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -66.8135 | -8.7176 | -11.8516
| Avoided fuel consumption from generation dispatch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.77262 | 0 | 2.5482 | 4.1422 | 3.1452 |  | Avoided fuel consumption from generation dispatch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10571 | 0 | 2.9438 | 7.1035 | 5.4278 | Avoided fuel consumption from generation dispatch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2746 | 0 | 2.0157 | 1.6529 | 2.5019 | Avoided fuel consumption from generation dispatch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6629 | 0 | 2.571 | 4.5825 | 3.7142
| Avoided voluntary load curtailment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027 | 0 | 0.015789 | 0.038501 | -0.015799 |  | Avoided voluntary load curtailment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.53931 | 0 | -2.7948 | -2.9655 | -2.9313 | Avoided voluntary load curtailment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.006373 | 0 | -0.77483 | -0.33986 | -0.53571 | Avoided voluntary load curtailment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.1489 | 0 | -0.9697 | -0.93081 | -0.98404
| Avoided involuntary load shedding outside of NW Slopes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0071663 | 0 | 1.0539 | 9.081 | 7.5808 |  | Avoided involuntary load shedding outside of NW Slopes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1537 | 0 | -5.1884 | -4.2581 | -4.3019 | Avoided involuntary load shedding outside of NW Slopes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.16581 | 0 | -0.35299 | 4.6631 | 3.9817 | Avoided involuntary load shedding outside of NW Slopes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61253 | 0 | -1.072 | 4.284 | 3.3681
| Avoided involuntary load shedding in NW Slopes | 702.3765 | 702.3765 | 355.5077 | 318.8109 | 355.5077 | 355.5077 | 672.6715 | 672.6715 | 672.6715 | 739.7074 | 750.3643 | 750.3643 |  | Avoided involuntary load shedding in NW Slopes | 137.0391 | 137.0391 | 67.0464 | 59.334 | 67.0464 | 67.0464 | 127.2572 | 127.2572 | 127.2572 | 137.0391 | 137.0391 | 137.0391 | Avoided involuntary load shedding in NW Slopes | 702.3765 | 702.3765 | 355.5077 | 318.8109 | 355.5077 | 355.5077 | 672.6715 | 672.6715 | 672.6715 | 739.7074 | 750.3643 | 750.3643 | Avoided involuntary load shedding in NW Slopes | 532.7753 | 532.7753 | 268.9693 | 240.9678 | 268.9693 | 268.9693 | 509.0472 | 509.0472 | 509.0472 | 558.9069 | 566.3668 | 566.3668
| Avoided costs for non RIT-T proponent parties | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8122 | 0 | 43.547 | 53.6185 | 45.1147 |  | Avoided costs for non RIT-T proponent parties | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7337 | 0 | 71.5612 | 81.4637 | 70.0284 | Avoided costs for non RIT-T proponent parties | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1476 | 0 | 50.9898 | 65.9822 | 53.0099 | Avoided costs for non RIT-T proponent parties | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.649 | 0 | 53.291 | 64.1975 | 54.01
| Avoided unrelated TNSP expenditure (wood pole replacement) | 0 | 0 | 0 | 0.75808 | 0 | 0 | 0.77033 | 0.77033 | 0.77033 | 0.75243 | 0.75243 | 0.75243 |  | Avoided unrelated TNSP expenditure (wood pole replacement) | 0 | 0 | 0 | 0.75808 | 0 | 0 | 0.77033 | 0.77033 | 0.77033 | 0.75243 | 0.75243 | 0.75243 | Avoided unrelated TNSP expenditure (wood pole replacement) | 0 | 0 | 0 | 0.75808 | 0 | 0 | 0.77033 | 0.77033 | 0.77033 | 0.75243 | 0.75243 | 0.75243 | Avoided unrelated TNSP expenditure (wood pole replacement) | 0 | 0 | 0 | 0.75808 | 0 | 0 | 0.77033 | 0.77033 | 0.77033 | 0.75243 | 0.75243 | 0.75243
| Avoided unrelated TNSP expenditure (market benefits) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.066915 | 0 | 0.26 | 0.42322 | 0.24981 |  | Avoided unrelated TNSP expenditure (market benefits) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.069114 | 0 | 1.2627 | 1.1921 | 1.0194 | Avoided unrelated TNSP expenditure (market benefits) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12932 | 0 | 0.91629 | 1.2006 | 0.88546 | Avoided unrelated TNSP expenditure (market benefits) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.032252 | 0 | 0.67894 | 0.79381 | 0.59511
| NNO receipts received from TNSP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163.9904 | 46.1334 | 0 |  | NNO receipts received from TNSP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163.9904 | 46.1334 | 0 | NNO receipts received from TNSP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163.9904 | 46.1334 | 0 | NNO receipts received from TNSP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163.9904 | 46.1334 | 0
| NPV | 503.9399 | 531.9383 | 242.2391 | 227.0521 | 211.9627 | 183.8739 | 572.908 | 550.8331 | 544.3445 | 552.9328 | 618.3864 | 601.9586 |  | NPV | 74.004 | 74.004 | 18.3253 | -1.6148 | 18.3253 | -38.327 | 58.3037 | 69.6883 | 58.3037 | 33.6128 | 83.2822 | 64.7897 | NPV | 503.9399 | 531.9383 | 242.2391 | 227.0521 | 211.9627 | 183.8739 | 572.908 | 551.6746 | 544.3445 | 558.302 | 624.242 | 605.7273 | NPV | 374.9591 | 394.558 | 175.065 | 158.452 | 153.8715 | 117.2137 | 418.5267 | 406.6412 | 398.5322 | 398.1032 | 458.9091 | 441.4863
| Benefit time series | Step Change | [12 empty] | Benefit time series | Progressive Change | [11 empty] | Benefit time series | Hydrogen Superpower | [11 empty] | Benefit time series | Weighted
Tiled chart
Sensitivities
High discount rate (central scenario)
|  | 1A | 443.8085
|  | 1B | 470.3207
|  | 2A | 206.9658
|  | 2B | 193.6005
|  | 2C | 175.2017
|  | 2D | 146.9101
|  | 3A | 513.3773
|  | 3B | 492.4145
|  | 3C | 483.5266
|  | 5A | 500.7991
|  | 5B | 553.4902
|  | 5C | 539.0737
Low discount rate (central scenario)
|  | 1A | 644.2407
|  | 1B | 677.1857
|  | 2A | 328.2545
|  | 2B | 307.645
|  | 2C | 306.1597
|  | 2D | 279.7519
|  | 3A | 705.6803
|  | 3B | 682.053
|  | 3C | 684.8952
|  | 5A | 668.4449
|  | 5B | 763.1998
|  | 5C | 742.2879

## Chart tables (hidden)
Chart tables
First ranked option |  | Option 5B
Real
Option 5B | Step Change |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Avoided fuel consumption from generation dispatch |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Avoided voluntary load curtailment |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Avoided involuntary load shedding |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Avoided costs for non RIT-T proponent parties |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Avoided unrelated TNSP expenditure (market benefits) |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Option 5B | Progressive Change |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Avoided fuel consumption from generation dispatch |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided voluntary load curtailment |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided involuntary load shedding |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided costs for non RIT-T proponent parties |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (market benefits) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Option 5B | Hydrogen Superpower |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Avoided fuel consumption from generation dispatch |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided voluntary load curtailment |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided involuntary load shedding |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided costs for non RIT-T proponent parties |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (market benefits) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Option 5B | #REF! |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Avoided fuel consumption from generation dispatch |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided voluntary load curtailment |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided involuntary load shedding |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided costs for non RIT-T proponent parties |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (market benefits) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Discounted |  |  | 1 | 0.94787 | 0.89845 | 0.85161 | 0.80722 | 0.76513 | 0.72525 | 0.68744 | 0.6516 | 0.61763 | 0.58543 | 0.55491 | 0.52598 | 0.49856 | 0.47257 | 0.44793 | 0.42458 | 0.40245 | 0.38147 | 0.36158 | 0.34273 | 0.32486 | 0.30793 | 0.29187 | 0.27666 | 0.26223 | 0.24856 | 0.2356 | 0.22332 | 0.21168
Option 5B | Step Change |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Avoided fuel consumption from generation dispatch |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Avoided voluntary load curtailment |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Avoided involuntary load shedding |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Avoided costs for non RIT-T proponent parties |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Avoided unrelated TNSP expenditure (market benefits) |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Option 5B | Progressive Change |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Avoided fuel consumption from generation dispatch |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided voluntary load curtailment |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided involuntary load shedding |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided costs for non RIT-T proponent parties |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (market benefits) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Option 5B | Hydrogen Superpower |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Avoided fuel consumption from generation dispatch |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided voluntary load curtailment |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided involuntary load shedding |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided costs for non RIT-T proponent parties |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (market benefits) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Option 5B | #REF! |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Avoided fuel consumption from generation dispatch |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided voluntary load curtailment |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided involuntary load shedding |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided costs for non RIT-T proponent parties |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (market benefits) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Discounted |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5B | Step Change |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Avoided fuel consumption from generation dispatch |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Avoided voluntary load curtailment |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Avoided involuntary load shedding |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Avoided costs for non RIT-T proponent parties |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Avoided unrelated TNSP expenditure (market benefits) |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Option 5B | Progressive Change |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Avoided fuel consumption from generation dispatch |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided voluntary load curtailment |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided involuntary load shedding |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided costs for non RIT-T proponent parties |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (market benefits) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Option 5B | Hydrogen Superpower |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Avoided fuel consumption from generation dispatch |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided voluntary load curtailment |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided involuntary load shedding |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided costs for non RIT-T proponent parties |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (market benefits) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Option 5B | #REF! |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052
Avoided fuel consumption from generation dispatch |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided voluntary load curtailment |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided involuntary load shedding |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided costs for non RIT-T proponent parties |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Avoided unrelated TNSP expenditure (market benefits) |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## General inputs
General parameters and options inputs
General parameters
Parameter | Unit | Value
First year of analysis | Year | 2023
Discount year | Year | 2023
Analysis period | Years | 20
Option inputs
Options | Stage | Short description
Base |  | No investment
Option 1A | 1 | 3rd Narrabri Tx
Option 1A | 1 | Upgrade 969 line to 160 MVA rating
Option 1A | 1 | 50 MVAr SVC Gunnedah
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating
Option 1A | 1 | Upgrade 968 line to 160 MVA rating
Option 1A | 2 | 60 MVAr SVC at Narrabri
Option 1B | 1 | 3rd Narrabri Tx
Option 1B | 1 | Upgrade 969 line to 160 MVA rating
Option 1B | 1 | 50 MVAr SVC Gunnedah
Option 1B | 1 | Upgrade 9UH line to 100 MVA rating
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri
Option 2A | 1 | 3rd Narrabri Tx
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah
Option 2A | 1 | Upgrade 969 line to 135 MVA rating
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating
Option 2A | 2 | 50 MVAr SVC Narrabri 132
Option 2B | 1 | 3rd Narrabri Tx
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating
Option 2B | 2 | 50 MVAr SVC Narrabri 132
Option 2C | 1 | 3rd Narrabri Tx
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri
Option 2D | 1 | 3rd Narrabri Tx
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV
Option 2D | 1 | Upgrade 969 line to 135 MVA rating
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating
Option 2D | 2 | 50 MVAr SVC Narrabri 132
Option 3A | 1 | 3rd Narrabri Tx
Option 3A | 1 | Rebuild 969 line as double circuit
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating
Option 3A | 2 | 60 MVAr SVC at Narrabri 132
Option 3B | 1 | 3rd Narrabri Tx
Option 3B | 1 | Rebuild 969 line as double circuit
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating
Option 3B | 2 | Install 50 MW / 50 MWh BESS at Narrabri 132
Option 3C | 1 | 3rd Narrabri Tx
Option 3C | 1 | Rebuild 969 line as double circuit
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri
Option 5A | 1 | 3rd Narrabri Tx
Option 5A | 1 | BESS at Gunnedah
Option 5A | 1 | Connection cost
Option 5A | 2 | Rebuild 969 line as double circuit
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating
Option 5B | 1 | 3rd Narrabri Tx
Option 5B | 1 | BESS near Gunnedah
Option 5B | 2 | Rebuild 969 line as double circuit
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating
Option 5C | 1 | 3rd Narrabri Tx
Option 5C | 1 | BESS at Gunnedah
Option 5C | 1 | Connection cost
Option 5C | 2 | Rebuild 969 line as double circuit
Option 5C | 2 | Upgrade 9UH line to 100 MVA rating
Cost and benefit categories |  |  | Scenarios
Cost categories |  |  | Scenario | Name
Capital costs |  |  | S1 | Step Change
Operating and maintenance costs |  |  | S2 | Progressive Change
|  |  | S3 | Hydrogen Superpower
Benefit categories
Avoided fuel consumption from generation dispatch
Avoided voluntary load curtailment
Avoided involuntary load shedding
Avoided costs for non RIT-T proponent parties
Avoided unrelated TNSP expenditure (wood pole replacement)
Avoided unrelated TNSP expenditure (market benefits)
NNO receipts received from TNSP

## CBA inputs
CBA cost inputs
All years in the input sheet are expressed as financial years. ie 2023 refers to FY2022/23 that covers the period from 1 July 2022 to 30 June 2023
Capital costs |  |  | S1 | S2 | S3
Option name | Stage | Capex component | Commission year - step | Commission year - progressive | Commission year - hydrogen | Asset life | 1 if TNSP owns asset | Amount | Build year 1 | Build year 2 | Build year 3 | Build year 4 | Build year 5 | Build year 6 | Build year 7 | Build year 8 | Build year 9 | Build year 10 | Build year 11 | Build year 12 | Build year 13 | Build year 14 | Build year 15 | Build year 16 | Build year 17 | Build year 18 | Build year 19 | Build year 20
Option 1A | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 562958.6578 | 3286846.5899 | 4322374.4822
Option 1A | 1 | Upgrade 969 line to 160 MVA rating | 2026 | 2026 | 2026 | 35 | 1 | 50949682.23 | 466189.595 | 1313773.949 | 49169718.686
Option 1A | 1 | 50 MVAr SVC Gunnedah | 2026 | 2026 | 2026 | 40 | 1 | 18433159.02 | 1270571.3167 | 6682283.4849 | 10480304.2184
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating | 2029 | #N/A | 2029 | 35 | 1 | 27991844.69 | 176326.0359 | 302125.5852 | 916273.6337 | 10037009.3916 | 16560110.0435
Option 1A | 1 | Upgrade 968 line to 160 MVA rating | 2028 | #N/A | 2028 | 35 | 1 | 148683015.7 | 906966.4008 | 1440809.2298 | 2842677.6499 | 97336044.2365 | 46156518.1829
Option 1A | 2 | 60 MVAr SVC at Narrabri | 2030 | #N/A | 2030 | 40 | 1 | 19661063.47 | 1047577.2064 | 6968417.1091 | 11645069.1544
Option 1B | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 562958.6578 | 3286846.5899 | 4322374.4822
Option 1B | 1 | Upgrade 969 line to 160 MVA rating | 2026 | 2026 | 2026 | 35 | 1 | 50949682.23 | 466189.595 | 1313773.949 | 49169718.686
Option 1B | 1 | 50 MVAr SVC Gunnedah | 2026 | 2026 | 2026 | 40 | 1 | 18433159.02 | 1270571.3167 | 6682283.4849 | 10480304.2184
Option 1B | 1 | Upgrade 9UH line to 100 MVA rating | 2027 | #N/A | 2027 | 35 | 1 | 27991844.69 | 176326.0359 | 302125.5852 | 916273.6337 | 10037009.3916 | 16560110.0435
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 102474742.77 | 291443.7217 | 538986.4355 | 1694034.4788 | 17053922.7396 | 30893655.2791 | 52002700.1153
Option 2A | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 562958.6578 | 3286846.5899 | 4322374.4822
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 2029 | 2029 | 2029 | 50 | 1 | 45979704.8847 | 304770.178 | 540678.4002 | 1838846.5297 | 15373872.4983 | 27921537.2786
Option 2A | 1 | Upgrade 969 line to 135 MVA rating | 2028 | #N/A | 2028 | 35 | 1 | 50949682.21 | 290073.5228 | 384387.0441 | 909168.7657 | 11910563.8167 | 37455489.0607
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating | 2029 | #N/A | 2029 | 35 | 1 | 27991844.69 | 176326.0359 | 302125.5852 | 916273.6337 | 10037009.3916 | 16560110.0435
Option 2A | 2 | 50 MVAr SVC Narrabri 132 | 2030 | #N/A | 2030 | 40 | 1 | 19661063 | 1047577 | 6968417 | 11645069
Option 2B | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 562958.6578 | 3286846.5899 | 4322374.4822
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 2029 | 2029 | 2029 | 50 | 1 | 62070491.37 | 320034.0032 | 571518.4188 | 1782611.1821 | 15944119.0011 | 38721538.8356 | 4730669.9292
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating | 2028 | #N/A | 2028 | 35 | 1 | 27991844.69 | 176326.0359 | 302125.5852 | 916273.6337 | 10037009.3916 | 16560110.0435
Option 2B | 2 | 50 MVAr SVC Narrabri 132 | 2030 | #N/A | 2030 | 40 | 1 | 19661063 | 1047577 | 6968417 | 11645069
Option 2C | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 562958.6578 | 3286846.5899 | 4322374.4822
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 2029 | 2029 | 2029 | 50 | 1 | 45979704.8847 | 304770.178 | 540678.4002 | 1838846.5297 | 15373872.4983 | 27921537.2786
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating | 2028 | #N/A | 2028 | 35 | 1 | 50949682.21 | 290073.5228 | 384387.0441 | 909168.7657 | 11910563.8167 | 37455489.0607
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 67112099.47 | 280164.9931 | 581512.839 | 2019198.3822 | 19947050.7231 | 42769235.622 | 1514936.9106
Option 2D | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 562958.6578 | 3286846.5899 | 4322374.4822
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 2029 | 2029 | 2029 | 50 | 1 | 126867927.18 | 367611.5549 | 900058.0332 | 3182788.6187 | 20107254.8947 | 99355949.4593 | 2954264.6191
Option 2D | 1 | Upgrade 969 line to 135 MVA rating | 2028 | #N/A | 2028 | 35 | 1 | 50949682.21 | 290073.5228 | 384387.0441 | 909168.7657 | 11910563.8167 | 37455489.0607
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating | 2028 | #N/A | 2028 | 35 | 1 | 27991844.69 | 176326.0359 | 302125.5852 | 916273.6337 | 10037009.3916 | 16560110.0435
Option 2D | 2 | 50 MVAr SVC Narrabri 132 | 2030 | #N/A | 2030 | 40 | 1 | 19661063 | 1047577 | 6968417 | 11645069
Option 3A | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 562958.6578 | 3286846.5899 | 4322374.4822
Option 3A | 1 | Rebuild 969 line as double circuit | 2026 | 2026 | 2026 | 50 | 1 | 86418857.86 | 1041254.0248 | 2755096.888 | 21687177.713 | 60935329.2341
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating | 2028 | #N/A | 2028 | 35 | 1 | 27991844.69 | 176326.0359 | 302125.5852 | 916273.6337 | 10037009.3916 | 16560110.0435
Option 3A | 2 | 60 MVAr SVC at Narrabri 132 | 2030 | #N/A | 2030 | 40 | 1 | 19661063 | 1047577 | 6968417 | 11645069
Option 3B | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 562958.6578 | 3286846.5899 | 4322374.4822
Option 3B | 1 | Rebuild 969 line as double circuit | 2026 | 2026 | 2026 | 50 | 1 | 86418857.86 | 1041254.0248 | 2755096.888 | 21687177.713 | 60935329.2341
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating | 2028 | #N/A | 2028 | 35 | 1 | 27991844.69 | 176326.0359 | 302125.5852 | 916273.6337 | 10037009.3916 | 16560110.0435
Option 3B | 2 | Install 50 MW / 50 MWh BESS at Narrabri 132 | 2030 | #N/A | 2030 | 20 | 1 |  | Redacted to preserve confidentiality
Option 3C | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 562958.6578 | 3286846.5899 | 4322374.4822
Option 3C | 1 | Rebuild 969 line as double circuit | 2026 | 2026 | 2026 | 50 | 1 | 86418857.86 | 1041254.0248 | 2755096.888 | 21687177.713 | 60935329.2341
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 67112099.47 | 280164.9931 | 581512.839 | 2019198.3822 | 19947050.7231 | 42769235.622 | 1514936.9106
Option 5A | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 562958.6578 | 3286846.5899 | 4322374.4822
Option 5A | 1 | BESS | Redacted to preserve confidentiality |  |  |  | 0 |  | Redacted to preserve confidentiality
Option 5A | 2 | Rebuild 969 line as double circuit | 2030 | #N/A | 2030 | 50 | 1 | 86418857.86 | 1041254.0248 | 2755096.888 | 21687177.713 | 60935329.2341
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating | 2030 | #N/A | 2030 | 35 | 1 | 27991844.69 | 176326.0359 | 302125.5852 | 916273.6337 | 10037009.3916 | 16560110.0435
Option 5B | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 562958.6578 | 3286846.5899 | 4322374.4822
Option 5B | 1 | BESS | Redacted to preserve confidentiality |  |  |  | 0 |  | Redacted to preserve confidentiality
Option 5B | 2 | Rebuild 969 line as double circuit | 2030 | #N/A | 2030 | 50 | 1 | 86418857.86 | 1041254.0248 | 2755096.888 | 21687177.713 | 60935329.2341
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating | 2030 | #N/A | 2030 | 35 | 1 | 27991844.69 | 176326.0359 | 302125.5852 | 916273.6337 | 10037009.3916 | 16560110.0435
Option 5C | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 562958.6578 | 3286846.5899 | 4322374.4822
Option 5C | 1 | BESS | Redacted to preserve confidentiality |  |  |  | 0 |  | Redacted to preserve confidentiality
Option 5C | 2 | Rebuild 969 line as double circuit | 2030 | #N/A | 2030 | 50 | 1 | 86418857.86 | 1041254.0248 | 2755096.888 | 21687177.713 | 60935329.2341
Option 5C | 2 | Upgrade 9UH line to 100 MVA rating | 2030 | #N/A | 2030 | 35 | 1 | 27991844.69 | 176326.0359 | 302125.5852 | 916273.6337 | 10037009.3916 | 16560110.0435
Biodiversity offset costs
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 12600000 | 0 | 0 | 0 | 12600000 | 0 | 0
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 2029 | 2029 | 2029 | 50 | 1 | 8100000 | 0 | 0 | 0 | 8100000 | 0
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 2029 | 2029 | 2029 | 50 | 1 | 8100000 | 0 | 0 | 0 | 8100000 | 0 | 0
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 2029 | 2029 | 2029 | 50 | 1 | 8100000 | 0 | 0 | 0 | 8100000 | 0
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 15800000 | 0 | 0 | 0 | 15800000 | 0 | 0
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 2029 | 2029 | 2029 | 50 | 1 | 8100000 | 0 | 0 | 0 | 8100000 | 0 | 0
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 15800000 | 0 | 0 | 0 | 15800000 | 0 | 0
Property allowances
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 44720000 | 0 | 0 | 0 | 35000000 | 9720000 | 0
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 2029 | 2029 | 2029 | 50 | 1 | 19200000 | 0 | 0 | 0 | 10000000 | 9200000
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 2029 | 2029 | 2029 | 50 | 1 | 19200000 | 0 | 0 | 0 | 10000000 | 9200000 | 0
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 2029 | 2029 | 2029 | 50 | 1 | 19200000 | 0 | 0 | 0 | 10000000 | 9200000
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 23140000 | 0 | 0 | 0 | 10000000 | 13140000 | 0
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 2029 | 2029 | 2029 | 50 | 1 | 24340000 | 0 | 0 | 0 | 15000000 | 9340000 | 0
Option 3A | 1 | Rebuild 969 line as double circuit | 2026 | 2026 | 2026 | 50 | 1 | 333278 | 0 | 0 | 333278 | 0
Option 3B | 1 | Rebuild 969 line as double circuit | 2026 | 2026 | 2026 | 50 | 1 | 333278 | 0 | 0 | 333278 | 0
Option 3C | 1 | Rebuild 969 line as double circuit | 2026 | 2026 | 2026 | 50 | 1 | 333278 | 0 | 0 | 333278 | 0
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 23140000 | 0 | 0 | 0 | 10000000 | 13140000 | 0
Option 5A | 2 | Rebuild 969 line as double circuit | 2030 | #N/A | 2030 | 50 | 1 | 333278 | 0 | 0 | 333278 | 0
Option 5B | 2 | Rebuild 969 line as double circuit | 2030 | #N/A | 2030 | 50 | 1 | 333278 | 0 | 0 | 333278 | 0
Option 5C | 2 | Rebuild 969 line as double circuit | 2030 | #N/A | 2030 | 50 | 1 | 333278 | 0 | 0 | 333278 | 0
Operating and maintenance costs
Option | Stage | Capex component |  | TNSP owned |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | 1 | 3rd Narrabri Tx |  | 1 |  | $ | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973
Option 1A | 1 | Upgrade 969 line to 160 MVA rating |  | 1 |  | $ | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223
Option 1A | 1 | 50 MVAr SVC Gunnedah |  | 1 |  | $ | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating |  | 1 |  | $ | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469
Option 1A | 1 | Upgrade 968 line to 160 MVA rating |  | 1 |  | $ | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157 | 1486830.157
Option 1A | 2 | 60 MVAr SVC at Narrabri |  | 1 |  | $ | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347 | 196610.6347
Option 1B | 1 | 3rd Narrabri Tx |  | 1 |  | $ | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973
Option 1B | 1 | Upgrade 969 line to 160 MVA rating |  | 1 |  | $ | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223 | 509496.8223
Option 1B | 1 | 50 MVAr SVC Gunnedah |  | 1 |  | $ | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902 | 184331.5902
Option 1B | 1 | Upgrade 9UH line to 100 MVA rating |  | 1 |  | $ | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri |  | 1 |  | $ | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277 | 1024747.4277
Option 2A | 1 | 3rd Narrabri Tx |  | 1 |  | $ | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah |  | 1 |  | $ | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488
Option 2A | 1 | Upgrade 969 line to 135 MVA rating |  | 1 |  | $ | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating |  | 1 |  | $ | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469
Option 2A | 2 | 50 MVAr SVC Narrabri 132 |  | 1 |  | $ | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63
Option 2B | 1 | 3rd Narrabri Tx |  | 1 |  | $ | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line |  | 1 |  | $ | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137 | 620704.9137
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating |  | 1 |  | $ | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469
Option 2B | 2 | 50 MVAr SVC Narrabri 132 |  | 1 |  | $ | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63
Option 2C | 1 | 3rd Narrabri Tx |  | 1 |  | $ | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah |  | 1 |  | $ | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488 | 459797.0488
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating |  | 1 |  | $ | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri |  | 1 |  | $ | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947
Option 2D | 1 | 3rd Narrabri Tx |  | 1 |  | $ | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV |  | 1 |  | $ | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718 | 1268679.2718
Option 2D | 1 | Upgrade 969 line to 135 MVA rating |  | 1 |  | $ | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221 | 509496.8221
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating |  | 1 |  | $ | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469
Option 2D | 2 | 50 MVAr SVC Narrabri 132 |  | 1 |  | $ | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63
Option 3A | 1 | 3rd Narrabri Tx |  | 1 |  | $ | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973
Option 3A | 1 | Rebuild 969 line as double circuit |  | 1 |  | $ | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating |  | 1 |  | $ | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469
Option 3A | 2 | 60 MVAr SVC at Narrabri 132 |  | 1 |  | $ | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63 | 196610.63
Option 3B | 1 | 3rd Narrabri Tx |  | 1 |  | $ | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973
Option 3B | 1 | Rebuild 969 line as double circuit |  | 1 |  | $ | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating |  | 1 |  | $ | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469
Option 3B | 2 | Install 50 MW / 50 MWh BESS at Narrabri 132 |  | 1 |  | $ | Redacted to preserve confidentiality
Option 3C | 1 | 3rd Narrabri Tx |  | 1 |  | $ | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973
Option 3C | 1 | Rebuild 969 line as double circuit |  | 1 |  | $ | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri |  | 1 |  | $ | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947 | 671120.9947
Option 5A | 1 | 3rd Narrabri Tx |  | 1 |  | $ | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973
Option 5A | 1 | BESS at Gunnedah |  | 0 |  | $ | Redacted to preserve confidentiality
Option 5A | 2 | Rebuild 969 line as double circuit |  | 1 |  | $ | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating |  | 1 |  | $ | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469
Option 5B | 1 | 3rd Narrabri Tx |  | 1 |  | $ | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973
Option 5B | 1 | BESS near Gunnedah |  | 0 |  | $ | Redacted to preserve confidentiality
Option 5B | 2 | Rebuild 969 line as double circuit |  | 1 |  | $ | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating |  | 1 |  | $ | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469
Option 5C | 1 | 3rd Narrabri Tx |  | 1 |  | $ | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973 | 81721.7973
Option 5C | 1 | BESS at Gunnedah |  | 0 |  | $ | Redacted to preserve confidentiality
Option 5C | 2 | Rebuild 969 line as double circuit |  | 1 |  | $ | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786 | 864188.5786
Option 5C | 2 | Upgrade 9UH line to 100 MVA rating |  | 1 |  | $ | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469 | 279918.4469
Biodiversity offset costs
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Property allowances
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | 1 | Rebuild 969 line as double circuit |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | 1 | Rebuild 969 line as double circuit |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 1 | Rebuild 969 line as double circuit |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | 2 | Rebuild 969 line as double circuit |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5B | 2 | Rebuild 969 line as double circuit |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5C | 2 | Rebuild 969 line as double circuit |  | 1 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TSNP network service payments to NNO proponents (opex)
Option | [5 empty] | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $
Option 3C | [5 empty] | $
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
NNO receipts received from TNSP
Option | [5 empty] | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $
Option 3C | [5 empty] | $
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
CBA benefit inputs
Avoided fuel consumption from generation dispatch
Option name |  | S1 | Step Change |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Option name |  | S2 | Progressive Change |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Option name |  | S3 | Hydrogen Superpower |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Avoided voluntary load curtailment
Option name |  | S1 | Step Change |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Option name |  | S2 | Progressive Change |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Option name |  | S3 | Hydrogen Superpower |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Avoided involuntary load shedding outside of NW Slopes
Option name |  | S1 | Step Change |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Option name |  | S2 | Progressive Change |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Option name |  | S3 | Hydrogen Superpower |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Avoided involuntary load shedding in NW Slopes
Option name |  | S1 | Step Change |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 5236 | 6550 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1A | [5 empty] | MWh | 0 | 0 | 253 | 935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B | [5 empty] | MWh | 0 | 0 | 253 | 935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | [5 empty] | MWh | 0 | 0 | 253 | 1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | [5 empty] | MWh | Redacted to preserve confidentiality
Option 3C | [5 empty] | MWh | 0 | 0 | 253 | 1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | [5 empty] | MWh | Redacted to preserve confidentiality
Option 5B | [5 empty] | MWh | Redacted to preserve confidentiality
Option 5C | [5 empty] | MWh | Redacted to preserve confidentiality
Option name |  | S2 | Progressive Change |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | MWh | 0 | 0 | 0 | 577 | 1036 | 1068 | 1073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1A | [5 empty] | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B | [5 empty] | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | [5 empty] | MWh | 0 | 0 | 0 | 577 | 1036 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | [5 empty] | MWh | 0 | 0 | 0 | 577 | 1036 | 431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | [5 empty] | MWh | 0 | 0 | 0 | 577 | 1036 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | [5 empty] | MWh | 0 | 0 | 0 | 577 | 1036 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | [5 empty] | MWh | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | [5 empty] | MWh | Redacted to preserve confidentiality
Option 3C | [5 empty] | MWh | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | [5 empty] | MWh | Redacted to preserve confidentiality
Option 5B | [5 empty] | MWh | Redacted to preserve confidentiality
Option 5C | [5 empty] | MWh | Redacted to preserve confidentiality
Option name |  | S3 | Hydrogen Superpower |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 5236 | 6550 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1A | [5 empty] | MWh | 0 | 0 | 253 | 935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B | [5 empty] | MWh | 0 | 0 | 253 | 935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | [5 empty] | MWh | 0 | 0 | 253 | 1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | [5 empty] | MWh | Redacted to preserve confidentiality
Option 3C | [5 empty] | MWh | 0 | 0 | 253 | 1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | [5 empty] | MWh | Redacted to preserve confidentiality
Option 5B | [5 empty] | MWh | Redacted to preserve confidentiality
Option 5C | [5 empty] | MWh | Redacted to preserve confidentiality
Avoided costs for non RIT-T proponent parties
Option name |  | S1 | Step Change |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Option name |  | S2 | Progressive Change |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Option name |  | S3 | Hydrogen Superpower |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (wood pole replacement)
Option name |  | S1 | Step Change |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 1A | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 1B | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 2A | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 2B | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 2D | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 3A | [5 empty] | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Option name |  | S2 | Progressive Change |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 1A | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 1B | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 2A | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 2B | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 2D | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 3A | [5 empty] | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Option name |  | S3 | Hydrogen Superpower |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 1A | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 1B | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 2A | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 2B | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 2D | [5 empty] | $ | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 3A | [5 empty] | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (market benefits)
Option name |  | S1 | Step Change |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Option name |  | S2 | Progressive Change |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Option name |  | S3 | Hydrogen Superpower |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | $
Option 1A | [5 empty] | $
Option 1B | [5 empty] | $
Option 2A | [5 empty] | $
Option 2B | [5 empty] | $
Option 2C | [5 empty] | $
Option 2D | [5 empty] | $
Option 3A | [5 empty] | $
Option 3B | [5 empty] | $ | Redacted to preserve confidentiality
Option 3C | [5 empty] | $ | Redacted to preserve confidentiality
Option 5A | [5 empty] | $ | Redacted to preserve confidentiality
Option 5B | [5 empty] | $ | Redacted to preserve confidentiality
Option 5C | [5 empty] | $ | Redacted to preserve confidentiality
Full involuntary load shedding forecast (zeroed out after 2027/28 in NPV assessment - see above, see PACR section 6.1)
Avoided involuntary load shedding in NW Slopes
Option name |  | S1 | Central |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 5236 | 6550 | 12553 | 16394 | 15307 | 15288 | 16185 | 16565 | 15953 | 15560 | 15661 | 15493 | 13403 | 12450 | 13116
Option 1A | [5 empty] | MWh | 0 | 0 | 253 | 935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B | [5 empty] | MWh | 0 | 0 | 253 | 935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | [5 empty] | MWh | 0 | 0 | 253 | 1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | [5 empty] | MWh | Redacted to preserve confidentiality
Option 3C | [5 empty] | MWh | 0 | 0 | 253 | 1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | [5 empty] | MWh | Redacted to preserve confidentiality
Option 5B | [5 empty] | MWh | Redacted to preserve confidentiality
Option 5C | [5 empty] | MWh | Redacted to preserve confidentiality
Option name |  | S2 | Low |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | MWh | 0 | 0 | 0 | 577 | 1036 | 1068 | 1073 | 1077 | 1081 | 1084 | 1086 | 1088 | 1091 | 1094 | 1097 | 1099 | 1102 | 1106 | 1109 | 1110
Option 1A | [5 empty] | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B | [5 empty] | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | [5 empty] | MWh | 0 | 0 | 0 | 577 | 1036 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | [5 empty] | MWh | 0 | 0 | 0 | 577 | 1036 | 431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | [5 empty] | MWh | 0 | 0 | 0 | 577 | 1036 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | [5 empty] | MWh | 0 | 0 | 0 | 577 | 1036 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | [5 empty] | MWh | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | [5 empty] | MWh | Redacted to preserve confidentiality
Option 3C | [5 empty] | MWh | 0 | 0 | 253 | 1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | [5 empty] | MWh | Redacted to preserve confidentiality
Option 5B | [5 empty] | MWh | Redacted to preserve confidentiality
Option 5C | [5 empty] | MWh | Redacted to preserve confidentiality
Option name |  | S3 | High |  |  | Unit | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Base | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 5236 | 6550 | 12553 | 16394 | 15307 | 15288 | 16185 | 16565 | 15953 | 15560 | 15661 | 15493 | 13403 | 12450 | 13116
Option 1A | [5 empty] | MWh | 0 | 0 | 253 | 935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B | [5 empty] | MWh | 0 | 0 | 253 | 935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 2557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | [5 empty] | MWh | 0 | 0 | 253 | 3109 | 5418 | 1534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | [5 empty] | MWh | 0 | 0 | 253 | 1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | [5 empty] | MWh | Redacted to preserve confidentiality
Option 3C | [5 empty] | MWh | 0 | 0 | 253 | 1679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | [5 empty] | MWh | Redacted to preserve confidentiality
Option 5B | [5 empty] | MWh | Redacted to preserve confidentiality
Option 5C | [5 empty] | MWh | Redacted to preserve confidentiality
Note on K60: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Zeroes such that build period matches the above
Note on B432: Liam Hickey: decommissions existing line, builds new in 2029
Note on B435: Liam Hickey: 3A, 3B and 3C rebuild 969 in 2026

## Line 969 costs
Line 969 costs - calculation of avoided unrelated TNSP expenditure (wood pole replacement)
|  |  |  | Annualised cost |  |  | Central
Optimal year of wood pole replacement | Mid point | Quantity | Replacement Cost (based on $125k/pole) | Central (S1) | Low (S2) | High (S3) | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
2026-2028 | 2027 | 1 | 125000 | -7790.0429 | -7790.0429 | -7790.0429 |  |  |  |  | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429
2029-2033 | 2031 | 6 | 750000 | -46740.2575 | -46740.2575 | -46740.2575 | [8 empty] | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575
2034-2038 | 2036 | 11 | 1375000 | -85690.4721 | -85690.4721 | -85690.4721 | Central 2036: -85690.4721; Central 2037: -85690.4721; Central 2038: -85690.4721; Central 2039: -85690.4721; Central 2040: -85690.4721; Central 2041: -85690.4721; Central 2042: -85690.4721
2039-2043 | 2041 | 29 | 3625000 | -225911.2447 | -225911.2447 | -225911.2447 | Central 2041: -225911.2447; Central 2042: -225911.2447
2044-2046 | 2045 | 19 | 2375000 | -148010.8155 | -148010.8155 | -148010.8155
Total |  | 66 | 8250000 | -514142.8327 | -514142.8327 | -514142.8327 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Asset life of wood poles | [6 empty] | Central 2023: Low
40 | [6 empty] | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
[11 empty] | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429
[15 empty] | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575
[20 empty] | -85690.4721 | -85690.4721 | -85690.4721 | -85690.4721 | -85690.4721 | -85690.4721 | -85690.4721
[25 empty] | -225911.2447 | -225911.2447
[7 empty] | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
High
[7 empty] | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
[11 empty] | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429
[15 empty] | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575 | -46740.2575
[20 empty] | -85690.4721 | -85690.4721 | -85690.4721 | -85690.4721 | -85690.4721 | -85690.4721 | -85690.4721
[25 empty] | -225911.2447 | -225911.2447
[7 empty] | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172

## S1
S1 |  | Step Change
S1 |  | NPV results
NPV results
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 503939889.9156 | -3206685.9703 | -12900039.2896 | -67117200.6217 | 2895525.3298 | 195994819.4777 | 219687881.7602 | 292895533.0597 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | 153789901.9645
Option 1B |  |  |  | $ | 531938318.8578 | -2476045.6055 | -11876473.3307 | -65427657.4559 | 89416799.3296 | 171741973.0287 | 203809665.3439 | 254024732.2558 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | 172864229.8967
Option 2A |  |  |  | $ | 242239119.9542 | -853032.1806 | -4152329.8479 | -6074347.2333 | -14747405.7774 | -82095669.7479 | 112319159.7463 | 294106897.9127 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | 115113274.5756
Option 2B |  |  |  | $ | 227052073.845 | -1059318.697 | -4160490.5939 | -7021259.298 | -44162850.1901 | -65610947.6764 | 113538523.4912 | 294463276.9129 | -1171165.745 | -1124425.4875 | -1124425.4875 | -1124425.4875 | -1124425.4875 | -1124425.4875 | -1038735.0153 | -1038735.0153 | -1038735.0153 | -1038735.0153 | -1038735.0153 | -812823.7707 | 97499490.7084
Option 2C |  |  |  | $ | 211962726.5646 | -853032.1806 | -4256168.8051 | -6353734.4871 | -15850330.5259 | -116758134.0794 | 79938451.1678 | 304516948.449 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | 163330911.9266
Option 2D |  |  |  | $ | 183873937.0658 | -1396969.7715 | -4873417.2524 | -9330605.5004 | -65236549.9004 | -163840847.3608 | 162766624.0024 | 293298015.6897 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | 175444945.4141
Option 3A |  |  |  | $ | 572907952.1158 | -1780538.7186 | -6344069.0631 | -27259103.829 | -4875722.5177 | 235465667.092 | 237292333.4998 | 294219793.248 | -1414649.4099 | -1367909.1524 | -1367909.1524 | -1367909.1524 | -1367909.1524 | -1367909.1524 | -1282218.6802 | -1282218.6802 | -1282218.6802 | -1282218.6802 | -1282218.6802 | -1056307.4356 | 90165662.9247
Option 3B |  |  |  | $ | 550833103.1123 | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 544344453.2184 | -1604212.6826 | -6322108.4711 | -26924343.0342 | 3142088.4918 | 207326303.4124 | 188631433.3247 | 304629843.7843 | -1609241.3277 | -1562501.0702 | -1562501.0702 | -1562501.0702 | -1562501.0702 | -1562501.0702 | -1476810.598 | -1476810.598 | -1476810.598 | -1476810.598 | -1476810.598 | -1250899.3534 | 139183067.2668
Option 5A |  |  |  | $ | 552932769.8407 | Redacted to preserve confidentiality
Option 5B |  |  |  | $ | 618386432.423 | Redacted to preserve confidentiality
Option 5C |  |  |  | $ | 601958595.6965 | Redacted to preserve confidentiality
S1 |  | Calculation |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Capital cost calculation
Option | Stage | Components | TNSP | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | Terminal value | Years in analysis period | Annual depreciation
Option 1A | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 1A | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -36413780.2249 | -466189.595 | -1313773.949 | -49169718.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26202693.7183 | 26202693.7183 | 17 | 1455705.2066
Option 1A | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -13188143.5144 | -1270571.3167 | -6682283.4849 | -10480304.2184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10599066.4365 | 10599066.4365 | 17 | 460828.9755
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -15918882.5506 | 0 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16795106.814 | 16795106.814 | 14 | 799766.9911
Option 1A | 1 | Upgrade 968 line to 160 MVA rating | 1 | $ | -94257312.8162 | -906966.4008 | -1440809.2298 | -2842677.6499 | -97336044.2365 | -46156518.1829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84961723.2571 | 84961723.2571 | 15 | 4248086.1629
Option 1A | 2 | 60 MVAr SVC at Narrabri | 1 | $ | -9824340.639 | 0 | 0 | 0 | 0 | -1047577.2064 | -6968417.1091 | -11645069.1544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13271217.8423 | 13271217.8423 | 13 | 491526.5867
Option 1B | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 1B | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -36413780.2249 | -466189.595 | -1313773.949 | -49169718.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26202693.7183 | 26202693.7183 | 17 | 1455705.2066
Option 1B | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -13188143.5144 | -1270571.3167 | -6682283.4849 | -10480304.2184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10599066.4365 | 10599066.4365 | 17 | 460828.9755
Option 1B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -17706780.8168 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15195572.8317 | 15195572.8317 | 16 | 799766.9911
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | -49902903.6746 | 0 | -291443.7217 | -538986.4355 | -1694034.4788 | -17053922.7396 | -30893655.2791 | -52002700.1153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75831309.6498 | 75831309.6498 | 13 | 2049494.8554
Option 2A | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -24144202.2277 | 0 | -304770.178 | -540678.4002 | -1838846.5297 | -15373872.4983 | -27921537.2786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33105387.517 | 33105387.517 | 14 | 919594.0977
Option 2A | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | -31322112.8055 | -290073.5228 | -384387.0441 | -909168.7657 | -11910563.8167 | -37455489.0607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29114104.12 | 29114104.12 | 15 | 1455705.206
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -15918882.5506 | 0 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16795106.814 | 16795106.814 | 14 | 799766.9911
Option 2A | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -9824340.3916 | 0 | 0 | 0 | 0 | -1047577 | -6968417 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13271217.525 | 13271217.525 | 13 | 491526.575
Option 2B | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -34758610.5245 | -320034.0032 | -571518.4188 | -1782611.1821 | -15944119.0011 | -38721538.8356 | -4730669.9292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44690753.7864 | 44690753.7864 | 14 | 1241409.8274
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -17417601.8228 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15995339.8229 | 15995339.8229 | 15 | 799766.9911
Option 2B | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -9824340.3916 | 0 | 0 | 0 | 0 | -1047577 | -6968417 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13271217.525 | 13271217.525 | 13 | 491526.575
Option 2C | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -24144202.2277 | 0 | -304770.178 | -540678.4002 | -1838846.5297 | -15373872.4983 | -27921537.2786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33105387.517 | 33105387.517 | 14 | 919594.0977
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating | 1 | $ | -31322112.8055 | -290073.5228 | -384387.0441 | -909168.7657 | -11910563.8167 | -37455489.0607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29114104.12 | 29114104.12 | 15 | 1455705.206
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -34475020.3507 | 0 | -280164.9931 | -581512.839 | -2019198.3822 | -19947050.7231 | -42769235.622 | -1514936.9106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49662953.6078 | 49662953.6078 | 13 | 1342241.9894
Option 2D | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -70637734.0949 | -367611.5549 | -900058.0332 | -3182788.6187 | -20107254.8947 | -99355949.4593 | -2954264.6191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91344907.5696 | 91344907.5696 | 14 | 2537358.5436
Option 2D | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | -31322112.8055 | -290073.5228 | -384387.0441 | -909168.7657 | -11910563.8167 | -37455489.0607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29114104.12 | 29114104.12 | 15 | 1455705.206
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -17417601.8228 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15995339.8229 | 15995339.8229 | 15 | 799766.9911
Option 2D | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -9824340.3916 | 0 | 0 | 0 | 0 | -1047577 | -6968417 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13271217.525 | 13271217.525 | 13 | 491526.575
Option 3A | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | -54407792.0951 | -1041254.0248 | -2755096.888 | -21687177.713 | -60935329.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57036446.1876 | 57036446.1876 | 17 | 1728377.1572
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -17417601.8228 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15995339.8229 | 15995339.8229 | 15 | 799766.9911
Option 3A | 2 | 60 MVAr SVC at Narrabri 132 | 1 | $ | -9824340.3916 | 0 | 0 | 0 | 0 | -1047577 | -6968417 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13271217.525 | 13271217.525 | 13 | 491526.575
Option 3B | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | -54407792.0951 | -1041254.0248 | -2755096.888 | -21687177.713 | -60935329.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57036446.1876 | 57036446.1876 | 17 | 1728377.1572
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -17417601.8228 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15995339.8229 | 15995339.8229 | 15 | 799766.9911
Option 3B | 2 | Install 50 MW / 50 MWh BESS at Narrabri 132 | 1 | $ |  | Redacted to preserve confidentiality | [19 empty] | Redacted to preserve confidentiality
Option 3C | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | -54407792.0951 | -1041254.0248 | -2755096.888 | -21687177.713 | -60935329.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57036446.1876 | 57036446.1876 | 17 | 1728377.1572
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -34475020.3507 | 0 | -280164.9931 | -581512.839 | -2019198.3822 | -19947050.7231 | -42769235.622 | -1514936.9106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49662953.6078 | 49662953.6078 | 13 | 1342241.9894
Option 5A | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 5A | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality | [19 empty] | Redacted to preserve confidentiality
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | -40774440.4963 | 0 | 0 | 0 | -1041254.0248 | -2755096.888 | -21687177.713 | -60935329.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63949954.8164 | 63949954.8164 | 13 | 1728377.1572
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -14483219.8806 | 0 | 0 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17594873.8051 | 17594873.8051 | 13 | 799766.9911
Option 5B | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 5B | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality | [19 empty] | Redacted to preserve confidentiality
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | -40774440.4963 | 0 | 0 | 0 | -1041254.0248 | -2755096.888 | -21687177.713 | -60935329.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63949954.8164 | 63949954.8164 | 13 | 1728377.1572
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -14483219.8806 | 0 | 0 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17594873.8051 | 17594873.8051 | 13 | 799766.9911
Option 5C | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 5C | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality | [19 empty] | Redacted to preserve confidentiality
Option 5C | 2 | Rebuild 969 line as double circuit | 1 | $ | -40774440.4963 | 0 | 0 | 0 | -1041254.0248 | -2755096.888 | -21687177.713 | -60935329.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63949954.8164 | 63949954.8164 | 13 | 1728377.1572
Option 5C | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -14483219.8806 | 0 | 0 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17594873.8051 | 17594873.8051 | 13 | 799766.9911
Biodiversity offset costs
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | -6799567.8446 | 0 | 0 | 0 | 0 | -12600000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9324000 | 9324000 | 13 | 252000
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -4429726.5643 | 0 | 0 | 0 | 0 | -8100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5832000 | 5832000 | 14 | 162000
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -4789341.6235 | 0 | 0 | 0 | -8100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5832000 | 5832000 | 14 | 162000
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -4429726.5643 | 0 | 0 | 0 | 0 | -8100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5832000 | 5832000 | 14 | 162000
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -8526442.2178 | 0 | 0 | 0 | 0 | -15800000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11692000 | 11692000 | 13 | 316000
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -4789341.6235 | 0 | 0 | 0 | -8100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5832000 | 5832000 | 14 | 162000
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -8526442.2178 | 0 | 0 | 0 | 0 | -15800000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11692000 | 11692000 | 13 | 316000
Property allowances
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | -23724028.5402 | 0 | 0 | 0 | 0 | -35000000 | -9720000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33092800 | 33092800 | 13 | 894400
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -10112934.6139 | 0 | 0 | 0 | 0 | -10000000 | -9200000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13824000 | 13824000 | 14 | 384000
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -10944061.8058 | 0 | 0 | 0 | -10000000 | -9200000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13824000 | 13824000 | 14 | 384000
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -10112934.6139 | 0 | 0 | 0 | 0 | -10000000 | -9200000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13824000 | 13824000 | 14 | 384000
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -11934497.7138 | 0 | 0 | 0 | 0 | -10000000 | -13140000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17123600 | 17123600 | 13 | 462800
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -13977008.6991 | 0 | 0 | 0 | -15000000 | -9340000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17524800 | 17524800 | 14 | 486800
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | -219900.2367 | 0 | 0 | -333278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219963.48 | 219963.48 | 17 | 6665.56
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | -219900.2367 | 0 | 0 | -333278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219963.48 | 219963.48 | 17 | 6665.56
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | -219900.2367 | 0 | 0 | -333278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219963.48 | 219963.48 | 17 | 6665.56
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -11934497.7138 | 0 | 0 | 0 | 0 | -10000000 | -13140000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17123600 | 17123600 | 13 | 462800
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | -165827.7521 | 0 | 0 | 0 | 0 | 0 | -333278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246625.72 | 246625.72 | 13 | 6665.56
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | -165827.7521 | 0 | 0 | 0 | 0 | 0 | -333278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246625.72 | 246625.72 | 13 | 6665.56
Option 5C | 2 | Rebuild 969 line as double circuit | 1 | $ | -165827.7521 | 0 | 0 | 0 | 0 | 0 | -333278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246625.72 | 246625.72 | 13 | 6665.56
TNSP capital costs
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | -175465299.4012 | -3206685.9703 | -12900039.2896 | -67117200.6217 | -98252317.8702 | -57241104.781 | -23528527.1527 | -11645069.1544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156528811.4129
Option 1B |  |  |  | $ | -153598044.2715 | -2476045.6055 | -11876473.3307 | -65427657.4559 | -11731043.8705 | -81214032.7831 | -40613655.2791 | -52002700.1153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174944445.9811
Option 2A |  |  |  | $ | -101615038.8097 | -853032.1806 | -4152329.8479 | -6074347.2333 | -14665683.9801 | -82013947.9506 | -60650064.3221 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116640819.3207
Option 2B |  |  |  | $ | -83596795.8243 | -1059318.697 | -4160490.5939 | -7021259.298 | -44081128.3928 | -65529225.8791 | -11699086.9292 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98312314.479
Option 2C |  |  |  | $ | -130807776.1498 | -853032.1806 | -4256168.8051 | -6353734.4871 | -15768608.7286 | -116676412.2821 | -93030772.9006 | -1514936.9106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165053048.5895
Option 2D |  |  |  | $ | -153830979.0935 | -1396969.7715 | -4873417.2524 | -9330605.5004 | -65154828.1031 | -163759125.5635 | -9922681.6191 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177781372.3822
Option 3A |  |  |  | $ | -87732474.2023 | -1780538.7186 | -6344069.0631 | -27259103.829 | -70972338.6258 | -17607687.0435 | -6968417 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91221970.3602
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | -115426492.2702 | -1604212.6826 | -6322108.4711 | -26924343.0342 | -62954527.6163 | -45747050.7231 | -55909235.622 | -1514936.9106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140433966.6202
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
NNO capital costs
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Operating cost calculation
Option | Stage | Component | TNSP | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 1A | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -4973368.5562 | 0 | 0 | 0 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223
Option 1A | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -1799322.1832 | 0 | 0 | 0 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -2053864.9477 | 0 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 1A | 1 | Upgrade 968 line to 160 MVA rating | 1 | $ | -12047046.402 | 0 | 0 | 0 | 0 | 0 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157
Option 1A | 2 | 60 MVAr SVC at Narrabri | 1 | $ | -1300013.7416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347
Option 1B | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 1B | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -4973368.5562 | 0 | 0 | 0 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223
Option 1B | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -1799322.1832 | 0 | 0 | 0 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902
Option 1B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -2493995.0248 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | -6775756.2541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277
Option 2A | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -3373700.6336 | 0 | 0 | 0 | 0 | 0 | 0 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488
Option 2A | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | -4128199.7333 | 0 | 0 | 0 | 0 | 0 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -2053864.9477 | 0 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 2A | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -1300013.7105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63
Option 2B | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -4554341.0205 | 0 | 0 | 0 | 0 | 0 | 0 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -2268040.1677 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 2B | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -1300013.7105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63
Option 2C | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -3373700.6336 | 0 | 0 | 0 | 0 | 0 | 0 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating | 1 | $ | -4128199.7333 | 0 | 0 | 0 | 0 | 0 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -4437534.7078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947
Option 2D | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -9308768.0182 | 0 | 0 | 0 | 0 | 0 | 0 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718
Option 2D | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | -4128199.7333 | 0 | 0 | 0 | 0 | 0 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -2268040.1677 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 2D | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -1300013.7105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63
Option 3A | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | -8435633.1882 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -2268040.1677 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 3A | 2 | 60 MVAr SVC at Narrabri 132 | 1 | $ | -1300013.7105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63
Option 3B | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | -8435633.1882 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -2268040.1677 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 3B | 2 | Install 50 MW / 50 MWh BESS at Narrabri 132 | 1 | $ | -3470067.4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -524803.8115 | -524803.8115 | -524803.8115 | -524803.8115 | -524803.8115 | -524803.8115 | -524803.8115 | -524803.8115 | -524803.8115 | -524803.8115 | -524803.8115 | -524803.8115 | -524803.8115
Option 3C | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | -8435633.1882 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -4437534.7078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947
Option 5A | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 5A | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | -5714121.3609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -1850855.2605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 5B | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 5B | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | -5714121.3609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -1850855.2605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 5C | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 5C | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 5C | 2 | Rebuild 969 line as double circuit | 1 | $ | -5714121.3609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 5C | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -1850855.2605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Biodiversity offset costs
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Property allowances
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5C | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TNSP operating expenditure
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | -22971329.5735 | 0 | 0 | 0 | -775550.2098 | -775550.2098 | -2262380.3668 | -2542298.8137 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484
Option 1B |  |  |  | $ | -16840155.7611 | 0 | 0 | 0 | -775550.2098 | -1055468.6567 | -1055468.6567 | -1055468.6567 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844
Option 2A |  |  |  | $ | -11653492.7679 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -591218.6194 | -1330934.1151 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451
Option 2B |  |  |  | $ | -8920108.6415 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -361640.2442 | -982345.1579 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879
Option 2C |  |  |  | $ | -12737148.8174 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -591218.6194 | -1051015.6682 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629
Option 2D |  |  |  | $ | -17802735.3724 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -871137.0663 | -2139816.3381 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681
Option 3A |  |  |  | $ | -12801400.8092 | 0 | 0 | 0 | -945910.3759 | -945910.3759 | -1225828.8228 | -1225828.8228 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | -13670881.6387 | 0 | 0 | 0 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
TSNP network service payments to NNO proponents
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
NNO operating expenditure
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided fuel consumption from generation dispatch
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided voluntary load curtailment
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding outside of NW Slopes
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding in NW Slopes
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 702376518.8904 | 0 | 0 | 0 | 101923393.4099 | 254011474.4685 | 245478789.2797 | 307082901.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 702376518.8904 | 0 | 0 | 0 | 101923393.4099 | 254011474.4685 | 245478789.2797 | 307082901.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 355507651.5318 | 0 | 0 | 0 | 0 | 0 | 173560442.6878 | 307082901.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 318810895.8638 | 0 | 0 | 0 | 0 | 0 | 125599250.6647 | 307082901.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 355507651.5318 | 0 | 0 | 0 | 0 | 0 | 173560442.6878 | 307082901.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 355507651.5318 | 0 | 0 | 0 | 0 | 0 | 173560442.6878 | 307082901.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 672671495.9977 | 0 | 0 | 0 | 67042526.4839 | 254011474.4685 | 245478789.2797 | 307082901.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 672671495.9977 | 0 | 0 | 0 | 67042526.4839 | 254011474.4685 | 245478789.2797 | 307082901.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided costs for non RIT-T proponent parties
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 3812220.5031 | 0 | 1893165.9344 | -750155.6229 | 739366.7887 | -595297.7921 | 2535867.2798 | -1987745.4468 | -2401402.3905 | -5402029.9114 | 1446464.5577 | 9013424.9567 | -3844448.9948 | 3036280.5833 | 6114263.1894 | -5483350.1716 | 1116629.2317 | 1545207.5421 | 2257412.1522 | -2290519.8136 | -185724.9205
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (wood pole replacement)
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 758082.447 | 0 | 0 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 770331.1296 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 770331.1296 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (market benefits)
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
NNO receipts received from TNSP
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Payback analysis
[6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
[6 empty] | 1 | 1.055 | 1.113 | 1.1742 | 1.2388 | 1.307 | 1.3788 | 1.4547 | 1.5347 | 1.6191 | 1.7081 | 1.8021 | 1.9012 | 2.0058 | 2.1161 | 2.2325 | 2.3553 | 2.4848 | 2.6215 | 2.7656
PV gross benefits
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ |  | 0 | 0 | 0 | 86799354.5278 | 205042315.1819 | 187824254.8171 | 222710594.3635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ |  | 0 | 0 | 0 | 86799354.5278 | 205042315.1819 | 187824254.8171 | 222710594.3635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 132797057.1683 | 222710594.3635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 96100301.5002 | 222716244.0597 | 5355.1622 | 35531.8822 | 33679.5092 | 31923.7054 | 30259.4364 | 28681.9302 | 69908.5638 | 66264.0416 | 62809.5181 | 59535.0882 | 56431.3632 | 139666.8811 | 132385.6693
Option 2C |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 132797057.1683 | 222710594.3635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 132797057.1683 | 222710594.3635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ |  | 0 | 0 | 0 | 57094331.6351 | 205048603.4349 | 187830215.2466 | 222716244.0597 | 5355.1622 | 35531.8822 | 33679.5092 | 31923.7054 | 30259.4364 | 28681.9302 | 69908.5638 | 66264.0416 | 62809.5181 | 59535.0882 | 56431.3632 | 139666.8811 | 132385.6693
Option 3B |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 3C |  |  |  | $ |  | 0 | 0 | 0 | 57094331.6351 | 205048603.4349 | 187830215.2466 | 222716244.0597 | 5355.1622 | 35531.8822 | 33679.5092 | 31923.7054 | 30259.4364 | 28681.9302 | 69908.5638 | 66264.0416 | 62809.5181 | 59535.0882 | 56431.3632 | 139666.8811 | 132385.6693
Option 5A |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Cumulative PV gross benefits
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ |  | 0 | 0 | 0 | 86799354.5278 | 291841669.7097 | 479665924.5268 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904
Option 1B |  |  |  | $ |  | 0 | 0 | 0 | 86799354.5278 | 291841669.7097 | 479665924.5268 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904
Option 2A |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 132797057.1683 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318
Option 2B |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 96100301.5002 | 318816545.5599 | 318821900.7222 | 318857432.6044 | 318891112.1135 | 318923035.8189 | 318953295.2553 | 318981977.1855 | 319051885.7494 | 319118149.7909 | 319180959.309 | 319240494.3972 | 319296925.7604 | 319436592.6415 | 319568978.3108
Option 2C |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 132797057.1683 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318
Option 2D |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 132797057.1683 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318
Option 3A |  |  |  | $ |  | 0 | 0 | 0 | 57094331.6351 | 262142935.0701 | 449973150.3167 | 672689394.3764 | 672694749.5386 | 672730281.4208 | 672763960.93 | 672795884.6354 | 672826144.0718 | 672854826.002 | 672924734.5658 | 672990998.6074 | 673053808.1254 | 673113343.2137 | 673169774.5769 | 673309441.458 | 673441827.1273
Option 3B |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 3C |  |  |  | $ |  | 0 | 0 | 0 | 57094331.6351 | 262142935.0701 | 449973150.3167 | 672689394.3764 | 672694749.5386 | 672730281.4208 | 672763960.93 | 672795884.6354 | 672826144.0718 | 672854826.002 | 672924734.5658 | 672990998.6074 | 673053808.1254 | 673113343.2137 | 673169774.5769 | 673309441.458 | 673441827.1273
Option 5A |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Total cost
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ |  | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747
Option 1B |  |  |  | $ |  | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326
Option 2A |  |  |  | $ |  | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776
Option 2B |  |  |  | $ |  | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658
Option 2C |  |  |  | $ |  | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673
Option 2D |  |  |  | $ |  | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466
Option 3A |  |  |  | $ |  | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115
Option 3B |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 3C |  |  |  | $ |  | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089
Option 5A |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Payback
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 1B |  |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2A |  |  |  | $ |  | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2B |  |  |  | $ |  | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2C |  |  |  | $ |  | NO | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2D |  |  |  | $ |  | NO | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 3A |  |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 3B |  |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 3C |  |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 5A |  |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 5B |  |  |  | $ |  | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 5C |  |  |  | $ |  | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES

## S2
S2 |  | Progressive Change
S2 |  | NPV results
NPV results
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 74003970.9817 | -2299719.5695 | -11282904.0238 | -63972397.3867 | 26275874.812 | 47795119.3268 | 49295371.6677 | 49529786.096 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | 40725213.2897
Option 1B |  |  |  | $ | 74003970.9817 | -2299719.5695 | -11282904.0238 | -63972397.3867 | 26275874.812 | 47795119.3268 | 49295371.6677 | 49529786.096 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | 40725213.2897
Option 2A |  |  |  | $ | 18325311.9664 | -562958.6578 | -3591616.7679 | -4863052.8824 | -1920568.327 | -33555594.2956 | 2740959.5006 | 49763817.4596 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | 56918872.0156
Option 2B |  |  |  | $ | -1614813.4016 | -882992.661 | -3858365.0087 | -6104985.6643 | -34125840.7984 | -48003260.6329 | 25052006.4345 | 49610699.6377 | -694636.6681 | -647896.4106 | -647896.4106 | -647896.4106 | -647896.4106 | -647896.4106 | -562205.9384 | -562205.9384 | -562205.9384 | -562205.9384 | -562205.9384 | -336294.6938 | 68709462.4374
Option 2C |  |  |  | $ | 18325311.9664 | -562958.6578 | -3591616.7679 | -4863052.8824 | -1920568.327 | -33555594.2956 | 2740959.5006 | 49763817.4596 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | 56918872.0156
Option 2D |  |  |  | $ | -38326976.4297 | -930570.2128 | -4186904.6231 | -7505163.101 | -43288976.692 | -108777671.2566 | 36908232.16 | 48954935.2367 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | 118050309.8452
Option 3A |  |  |  | $ | 58303695.0906 | -1604212.6826 | -6041943.478 | -26342830.1953 | -46316121.5732 | 47632549.2036 | 49132801.5445 | 49367215.9728 | -938120.333 | -891380.0755 | -891380.0755 | -891380.0755 | -891380.0755 | -891380.0755 | -805689.6033 | -805689.6033 | -805689.6033 | -805689.6033 | -805689.6033 | -579778.3587 | 61375634.6537
Option 3B |  |  |  | $ | 69688340.9652 | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 58303695.0906 | -1604212.6826 | -6041943.478 | -26342830.1953 | -46316121.5732 | 47632549.2036 | 49132801.5445 | 49367215.9728 | -938120.333 | -891380.0755 | -891380.0755 | -891380.0755 | -891380.0755 | -891380.0755 | -805689.6033 | -805689.6033 | -805689.6033 | -805689.6033 | -805689.6033 | -579778.3587 | 61375634.6537
Option 5A |  |  |  | $ | 33612762.2897 | Redacted to preserve confidentiality
Option 5B |  |  |  | $ | 83282152.5255 | Redacted to preserve confidentiality
Option 5C |  |  |  | $ | 64789668.6293 | Redacted to preserve confidentiality
S2 |  | Calculation |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Capital cost calculation
Option | Stage | Components | TNSP | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | Terminal value | Years in analysis period | Annual depreciation
Option 1A | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 1A | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -36413780.2249 | -466189.595 | -1313773.949 | -49169718.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26202693.7183 | 26202693.7183 | 17 | 1455705.2066
Option 1A | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -13188143.5144 | -1270571.3167 | -6682283.4849 | -10480304.2184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10599066.4365 | 10599066.4365 | 17 | 460828.9755
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 799766.9911
Option 1A | 1 | Upgrade 968 line to 160 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 4248086.1629
Option 1A | 2 | 60 MVAr SVC at Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 491526.5867
Option 1B | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 1B | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -36413780.2249 | -466189.595 | -1313773.949 | -49169718.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26202693.7183 | 26202693.7183 | 17 | 1455705.2066
Option 1B | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -13188143.5144 | -1270571.3167 | -6682283.4849 | -10480304.2184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10599066.4365 | 10599066.4365 | 17 | 460828.9755
Option 1B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 799766.9911
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 2049494.8554
Option 2A | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -24144202.2277 | 0 | -304770.178 | -540678.4002 | -1838846.5297 | -15373872.4983 | -27921537.2786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33105387.517 | 33105387.517 | 14 | 919594.0977
Option 2A | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 1455705.206
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 799766.9911
Option 2A | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 491526.575
Option 2B | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -34758610.5245 | -320034.0032 | -571518.4188 | -1782611.1821 | -15944119.0011 | -38721538.8356 | -4730669.9292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44690753.7864 | 44690753.7864 | 14 | 1241409.8274
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 799766.9911
Option 2B | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 491526.575
Option 2C | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -24144202.2277 | 0 | -304770.178 | -540678.4002 | -1838846.5297 | -15373872.4983 | -27921537.2786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33105387.517 | 33105387.517 | 14 | 919594.0977
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 1455705.206
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 1342241.9894
Option 2D | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -70637734.0949 | -367611.5549 | -900058.0332 | -3182788.6187 | -20107254.8947 | -99355949.4593 | -2954264.6191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91344907.5696 | 91344907.5696 | 14 | 2537358.5436
Option 2D | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 1455705.206
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 799766.9911
Option 2D | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 491526.575
Option 3A | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | -54407792.0951 | -1041254.0248 | -2755096.888 | -21687177.713 | -60935329.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57036446.1876 | 57036446.1876 | 17 | 1728377.1572
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 799766.9911
Option 3A | 2 | 60 MVAr SVC at Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 491526.575
Option 3B | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | -54407792.0951 | -1041254.0248 | -2755096.888 | -21687177.713 | -60935329.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57036446.1876 | 57036446.1876 | 17 | 1728377.1572
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 799766.9911
Option 3B | 2 | Install 50 MW / 50 MWh BESS at Narrabri 132 | 1 | $ |  | Redacted to preserve confidentiality | [19 empty] | Redacted to preserve confidentiality
Option 3C | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | -54407792.0951 | -1041254.0248 | -2755096.888 | -21687177.713 | -60935329.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57036446.1876 | 57036446.1876 | 17 | 1728377.1572
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 1342241.9894
Option 5A | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 5A | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality | [19 empty] | Redacted to preserve confidentiality
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 1728377.1572
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 799766.9911
Option 5B | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 5B | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality | [19 empty] | Redacted to preserve confidentiality
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 1728377.1572
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 799766.9911
Option 5C | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 5C | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality | [19 empty] | Redacted to preserve confidentiality
Option 5C | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 1728377.1572
Option 5C | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 799766.9911
Biodiversity offset costs
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 252000
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -4429726.5643 | 0 | 0 | 0 | 0 | -8100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5832000 | 5832000 | 14 | 162000
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -4789341.6235 | 0 | 0 | 0 | -8100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5832000 | 5832000 | 14 | 162000
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -4429726.5643 | 0 | 0 | 0 | 0 | -8100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5832000 | 5832000 | 14 | 162000
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 316000
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -4789341.6235 | 0 | 0 | 0 | -8100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5832000 | 5832000 | 14 | 162000
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 316000
Property allowances
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 894400
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -10112934.6139 | 0 | 0 | 0 | 0 | -10000000 | -9200000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13824000 | 13824000 | 14 | 384000
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -10944061.8058 | 0 | 0 | 0 | -10000000 | -9200000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13824000 | 13824000 | 14 | 384000
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -10112934.6139 | 0 | 0 | 0 | 0 | -10000000 | -9200000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13824000 | 13824000 | 14 | 384000
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 462800
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -13977008.6991 | 0 | 0 | 0 | -15000000 | -9340000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17524800 | 17524800 | 14 | 486800
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | -219900.2367 | 0 | 0 | -333278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219963.48 | 219963.48 | 17 | 6665.56
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | -219900.2367 | 0 | 0 | -333278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219963.48 | 219963.48 | 17 | 6665.56
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | -219900.2367 | 0 | 0 | -333278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219963.48 | 219963.48 | 17 | 6665.56
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 462800
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 6665.56
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 6665.56
Option 5C | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 6665.56
TNSP capital costs
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | -55464763.3954 | -2299719.5695 | -11282904.0238 | -63972397.3867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41500763.4995
Option 1B |  |  |  | $ | -55464763.3954 | -2299719.5695 | -11282904.0238 | -63972397.3867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41500763.4995
Option 2A |  |  |  | $ | -44549703.062 | -562958.6578 | -3591616.7679 | -4863052.8824 | -1838846.5297 | -33473872.4983 | -37121537.2786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57460390.8617
Option 2B |  |  |  | $ | -56354853.6098 | -882992.661 | -3858365.0087 | -6104985.6643 | -34044119.0011 | -47921538.8356 | -4730669.9292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69045757.1312
Option 2C |  |  |  | $ | -44549703.062 | -562958.6578 | -3591616.7679 | -4863052.8824 | -1838846.5297 | -33473872.4983 | -37121537.2786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57460390.8617
Option 2D |  |  |  | $ | -95266924.0736 | -930570.2128 | -4186904.6231 | -7505163.101 | -43207254.8947 | -108695949.4593 | -2954264.6191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119400710.9143
Option 3A |  |  |  | $ | -60490531.9878 | -1604212.6826 | -6041943.478 | -26342830.1953 | -60935329.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61955413.0124
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | -60490531.9878 | -1604212.6826 | -6041943.478 | -26342830.1953 | -60935329.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61955413.0124
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
NNO capital costs
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Operating cost calculation
Option | Stage | Component | TNSP | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 1A | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -4973368.5562 | 0 | 0 | 0 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223
Option 1A | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -1799322.1832 | 0 | 0 | 0 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1A | 1 | Upgrade 968 line to 160 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1A | 2 | 60 MVAr SVC at Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 1B | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -4973368.5562 | 0 | 0 | 0 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223
Option 1B | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -1799322.1832 | 0 | 0 | 0 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902
Option 1B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -3373700.6336 | 0 | 0 | 0 | 0 | 0 | 0 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488
Option 2A | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -4554341.0205 | 0 | 0 | 0 | 0 | 0 | 0 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -3373700.6336 | 0 | 0 | 0 | 0 | 0 | 0 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -9308768.0182 | 0 | 0 | 0 | 0 | 0 | 0 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718
Option 2D | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | -8435633.1882 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | 2 | 60 MVAr SVC at Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | -8435633.1882 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | 2 | Install 50 MW / 50 MWh BESS at Narrabri 132 | 1 | $ |  | Redacted to preserve confidentiality
Option 3C | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | -8435633.1882 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 5A | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5B | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 5B | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5C | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 5C | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 5C | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5C | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Biodiversity offset costs
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Property allowances
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5C | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TNSP operating expenditure
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | -7570404.4822 | 0 | 0 | 0 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098
Option 1B |  |  |  | $ | -7570404.4822 | 0 | 0 | 0 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098 | -775550.2098
Option 2A |  |  |  | $ | -4171414.3764 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461
Option 2B |  |  |  | $ | -5352054.7632 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -702426.711 | -702426.711 | -702426.711 | -702426.711 | -702426.711 | -702426.711 | -702426.711 | -702426.711 | -702426.711 | -702426.711 | -702426.711 | -702426.711 | -702426.711 | -702426.711
Option 2C |  |  |  | $ | -4171414.3764 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461 | -541518.8461
Option 2D |  |  |  | $ | -10106481.761 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691 | -1350401.0691
Option 3A |  |  |  | $ | -9233346.931 | 0 | 0 | 0 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | -9233346.931 | 0 | 0 | 0 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
TSNP network service payments to NNO proponents
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
NNO operating expenditure
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided fuel consumption from generation dispatch
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided voluntary load curtailment
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding outside of NW Slopes
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding in NW Slopes
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 137039138.8592 | 0 | 0 | 0 | 27051425.0218 | 48570669.5366 | 50070921.8775 | 50305336.3058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 137039138.8592 | 0 | 0 | 0 | 27051425.0218 | 48570669.5366 | 50070921.8775 | 50305336.3058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 67046429.4048 | 0 | 0 | 0 | 0 | 0 | 39944218.5764 | 50305336.3058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 59334012.5245 | 0 | 0 | 0 | 0 | 0 | 29864398.161 | 50305336.3058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 67046429.4048 | 0 | 0 | 0 | 0 | 0 | 39944218.5764 | 50305336.3058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 67046429.4048 | 0 | 0 | 0 | 0 | 0 | 39944218.5764 | 50305336.3058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 127257242.8798 | 0 | 0 | 0 | 15565118.0368 | 48570669.5366 | 50070921.8775 | 50305336.3058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 127257242.8798 | 0 | 0 | 0 | 15565118.0368 | 48570669.5366 | 50070921.8775 | 50305336.3058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided costs for non RIT-T proponent parties
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (wood pole replacement)
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 758082.447 | 0 | 0 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 770331.1296 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 770331.1296 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (market benefits)
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
NNO receipts received from TNSP
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Payback analysis
[6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
[6 empty] | 1 | 1.055 | 1.113 | 1.1742 | 1.2388 | 1.307 | 1.3788 | 1.4547 | 1.5347 | 1.6191 | 1.7081 | 1.8021 | 1.9012 | 2.0058 | 2.1161 | 2.2325 | 2.3553 | 2.4848 | 2.6215 | 2.7656
PV gross benefits
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ |  | 0 | 0 | 0 | 23037363.1842 | 39207057.6834 | 38310982.457 | 36483735.5347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ |  | 0 | 0 | 0 | 23037363.1842 | 39207057.6834 | 38310982.457 | 36483735.5347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 30562693.8702 | 36483735.5347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 22850276.9898 | 36489385.2308 | 5355.1622 | 35531.8822 | 33679.5092 | 31923.7054 | 30259.4364 | 28681.9302 | 69908.5638 | 66264.0416 | 62809.5181 | 59535.0882 | 56431.3632 | 139666.8811 | 132385.6693
Option 2C |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 30562693.8702 | 36483735.5347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 30562693.8702 | 36483735.5347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ |  | 0 | 0 | 0 | 13255467.2048 | 39213345.9364 | 38316942.8864 | 36489385.2308 | 5355.1622 | 35531.8822 | 33679.5092 | 31923.7054 | 30259.4364 | 28681.9302 | 69908.5638 | 66264.0416 | 62809.5181 | 59535.0882 | 56431.3632 | 139666.8811 | 132385.6693
Option 3B |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 3C |  |  |  | $ |  | 0 | 0 | 0 | 13255467.2048 | 39213345.9364 | 38316942.8864 | 36489385.2308 | 5355.1622 | 35531.8822 | 33679.5092 | 31923.7054 | 30259.4364 | 28681.9302 | 69908.5638 | 66264.0416 | 62809.5181 | 59535.0882 | 56431.3632 | 139666.8811 | 132385.6693
Option 5A |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Cumulative PV gross benefits
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ |  | 0 | 0 | 0 | 23037363.1842 | 62244420.8676 | 100555403.3246 | 137039138.8592 | 137039138.8592 | 137039138.8592 | 137039138.8592 | 137039138.8592 | 137039138.8592 | 137039138.8592 | 137039138.8592 | 137039138.8592 | 137039138.8592 | 137039138.8592 | 137039138.8592 | 137039138.8592 | 137039138.8592
Option 1B |  |  |  | $ |  | 0 | 0 | 0 | 23037363.1842 | 62244420.8676 | 100555403.3246 | 137039138.8592 | 137039138.8592 | 137039138.8592 | 137039138.8592 | 137039138.8592 | 137039138.8592 | 137039138.8592 | 137039138.8592 | 137039138.8592 | 137039138.8592 | 137039138.8592 | 137039138.8592 | 137039138.8592 | 137039138.8592
Option 2A |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 30562693.8702 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048
Option 2B |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 22850276.9898 | 59339662.2206 | 59345017.3829 | 59380549.2651 | 59414228.7742 | 59446152.4796 | 59476411.916 | 59505093.8462 | 59575002.4101 | 59641266.4516 | 59704075.9697 | 59763611.0579 | 59820042.4211 | 59959709.3022 | 60092094.9715
Option 2C |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 30562693.8702 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048
Option 2D |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 30562693.8702 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048 | 67046429.4048
Option 3A |  |  |  | $ |  | 0 | 0 | 0 | 13255467.2048 | 52468813.1412 | 90785756.0277 | 127275141.2585 | 127280496.4207 | 127316028.3029 | 127349707.8121 | 127381631.5175 | 127411890.9539 | 127440572.8841 | 127510481.4479 | 127576745.4895 | 127639555.0075 | 127699090.0958 | 127755521.459 | 127895188.3401 | 128027574.0094
Option 3B |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 3C |  |  |  | $ |  | 0 | 0 | 0 | 13255467.2048 | 52468813.1412 | 90785756.0277 | 127275141.2585 | 127280496.4207 | 127316028.3029 | 127349707.8121 | 127381631.5175 | 127411890.9539 | 127440572.8841 | 127510481.4479 | 127576745.4895 | 127639555.0075 | 127699090.0958 | 127755521.459 | 127895188.3401 | 128027574.0094
Option 5A |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Total cost
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ |  | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775
Option 1B |  |  |  | $ |  | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775 | 63035167.8775
Option 2A |  |  |  | $ |  | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384
Option 2B |  |  |  | $ |  | 61706908.3731 | 61706908.3731 | 61706908.3731 | 61706908.3731 | 61706908.3731 | 61706908.3731 | 61706908.3731 | 61706908.3731 | 61706908.3731 | 61706908.3731 | 61706908.3731 | 61706908.3731 | 61706908.3731 | 61706908.3731 | 61706908.3731 | 61706908.3731 | 61706908.3731 | 61706908.3731 | 61706908.3731 | 61706908.3731
Option 2C |  |  |  | $ |  | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384 | 48721117.4384
Option 2D |  |  |  | $ |  | 105373405.8346 | 105373405.8346 | 105373405.8346 | 105373405.8346 | 105373405.8346 | 105373405.8346 | 105373405.8346 | 105373405.8346 | 105373405.8346 | 105373405.8346 | 105373405.8346 | 105373405.8346 | 105373405.8346 | 105373405.8346 | 105373405.8346 | 105373405.8346 | 105373405.8346 | 105373405.8346 | 105373405.8346 | 105373405.8346
Option 3A |  |  |  | $ |  | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188
Option 3B |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 3C |  |  |  | $ |  | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188 | 69723878.9188
Option 5A |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Payback
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ |  | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 1B |  |  |  | $ |  | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2A |  |  |  | $ |  | NO | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2B |  |  |  | $ | bar: 0 to 19
Option 2C |  |  |  | $ |  | NO | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2D |  |  |  | $ | bar: 0 to 19
Option 3A |  |  |  | $ |  | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 3B |  |  |  | $ |  | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 3C |  |  |  | $ |  | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 5A |  |  |  | $ |  | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES
Option 5B |  |  |  | $ |  | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 5C |  |  |  | $ |  | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES

## S3
S3 |  | Hydrogen Superpower
S3 |  | NPV results
NPV results
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 503939889.9156 | -3206685.9703 | -12900039.2896 | -67117200.6217 | 2895525.3298 | 195994819.4777 | 219687881.7602 | 292895533.0597 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | 153789901.9645
Option 1B |  |  |  | $ | 531938318.8578 | -2476045.6055 | -11876473.3307 | -65427657.4559 | 89416799.3296 | 171741973.0287 | 203809665.3439 | 254024732.2558 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | 172864229.8967
Option 2A |  |  |  | $ | 242239119.9542 | -853032.1806 | -4152329.8479 | -6074347.2333 | -14747405.7774 | -82095669.7479 | 112319159.7463 | 294106897.9127 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | 115113274.5756
Option 2B |  |  |  | $ | 227052073.845 | -1059318.697 | -4160490.5939 | -7021259.298 | -44162850.1901 | -65610947.6764 | 113538523.4912 | 294463276.9129 | -1171165.745 | -1124425.4875 | -1124425.4875 | -1124425.4875 | -1124425.4875 | -1124425.4875 | -1038735.0153 | -1038735.0153 | -1038735.0153 | -1038735.0153 | -1038735.0153 | -812823.7707 | 97499490.7084
Option 2C |  |  |  | $ | 211962726.5646 | -853032.1806 | -4256168.8051 | -6353734.4871 | -15850330.5259 | -116758134.0794 | 79938451.1678 | 304516948.449 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | 163330911.9266
Option 2D |  |  |  | $ | 183873937.0658 | -1396969.7715 | -4873417.2524 | -9330605.5004 | -65236549.9004 | -163840847.3608 | 162766624.0024 | 293298015.6897 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | 175444945.4141
Option 3A |  |  |  | $ | 572907952.1158 | -1780538.7186 | -6344069.0631 | -27259103.829 | -4875722.5177 | 235465667.092 | 237292333.4998 | 294219793.248 | -1414649.4099 | -1367909.1524 | -1367909.1524 | -1367909.1524 | -1367909.1524 | -1367909.1524 | -1282218.6802 | -1282218.6802 | -1282218.6802 | -1282218.6802 | -1282218.6802 | -1056307.4356 | 90165662.9247
Option 3B |  |  |  | $ | 551674648.4895 | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 544344453.2184 | -1604212.6826 | -6322108.4711 | -26924343.0342 | 3142088.4918 | 207326303.4124 | 188631433.3247 | 304629843.7843 | -1609241.3277 | -1562501.0702 | -1562501.0702 | -1562501.0702 | -1562501.0702 | -1562501.0702 | -1476810.598 | -1476810.598 | -1476810.598 | -1476810.598 | -1476810.598 | -1250899.3534 | 139183067.2668
Option 5A |  |  |  | $ | 558301966.7425 | Redacted to preserve confidentiality
Option 5B |  |  |  | $ | 624241972.2798 | Redacted to preserve confidentiality
Option 5C |  |  |  | $ | 605727250.9782 | Redacted to preserve confidentiality
S3 |  | Calculation |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Capital cost calculation
Option | Stage | Components | TNSP | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | Terminal value | Years in analysis period | Annual depreciation
Option 1A | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 1A | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -36413780.2249 | -466189.595 | -1313773.949 | -49169718.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26202693.7183 | 26202693.7183 | 17 | 1455705.2066
Option 1A | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -13188143.5144 | -1270571.3167 | -6682283.4849 | -10480304.2184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10599066.4365 | 10599066.4365 | 17 | 460828.9755
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -15918882.5506 | 0 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16795106.814 | 16795106.814 | 14 | 799766.9911
Option 1A | 1 | Upgrade 968 line to 160 MVA rating | 1 | $ | -94257312.8162 | -906966.4008 | -1440809.2298 | -2842677.6499 | -97336044.2365 | -46156518.1829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84961723.2571 | 84961723.2571 | 15 | 4248086.1629
Option 1A | 2 | 60 MVAr SVC at Narrabri | 1 | $ | -9824340.639 | 0 | 0 | 0 | 0 | -1047577.2064 | -6968417.1091 | -11645069.1544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13271217.8423 | 13271217.8423 | 13 | 491526.5867
Option 1B | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 1B | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -36413780.2249 | -466189.595 | -1313773.949 | -49169718.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26202693.7183 | 26202693.7183 | 17 | 1455705.2066
Option 1B | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -13188143.5144 | -1270571.3167 | -6682283.4849 | -10480304.2184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10599066.4365 | 10599066.4365 | 17 | 460828.9755
Option 1B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -17706780.8168 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15195572.8317 | 15195572.8317 | 16 | 799766.9911
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | -49902903.6746 | 0 | -291443.7217 | -538986.4355 | -1694034.4788 | -17053922.7396 | -30893655.2791 | -52002700.1153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75831309.6498 | 75831309.6498 | 13 | 2049494.8554
Option 2A | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -24144202.2277 | 0 | -304770.178 | -540678.4002 | -1838846.5297 | -15373872.4983 | -27921537.2786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33105387.517 | 33105387.517 | 14 | 919594.0977
Option 2A | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | -31322112.8055 | -290073.5228 | -384387.0441 | -909168.7657 | -11910563.8167 | -37455489.0607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29114104.12 | 29114104.12 | 15 | 1455705.206
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -15918882.5506 | 0 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16795106.814 | 16795106.814 | 14 | 799766.9911
Option 2A | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -9824340.3916 | 0 | 0 | 0 | 0 | -1047577 | -6968417 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13271217.525 | 13271217.525 | 13 | 491526.575
Option 2B | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -34758610.5245 | -320034.0032 | -571518.4188 | -1782611.1821 | -15944119.0011 | -38721538.8356 | -4730669.9292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44690753.7864 | 44690753.7864 | 14 | 1241409.8274
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -17417601.8228 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15995339.8229 | 15995339.8229 | 15 | 799766.9911
Option 2B | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -9824340.3916 | 0 | 0 | 0 | 0 | -1047577 | -6968417 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13271217.525 | 13271217.525 | 13 | 491526.575
Option 2C | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -24144202.2277 | 0 | -304770.178 | -540678.4002 | -1838846.5297 | -15373872.4983 | -27921537.2786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33105387.517 | 33105387.517 | 14 | 919594.0977
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating | 1 | $ | -31322112.8055 | -290073.5228 | -384387.0441 | -909168.7657 | -11910563.8167 | -37455489.0607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29114104.12 | 29114104.12 | 15 | 1455705.206
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -34475020.3507 | 0 | -280164.9931 | -581512.839 | -2019198.3822 | -19947050.7231 | -42769235.622 | -1514936.9106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49662953.6078 | 49662953.6078 | 13 | 1342241.9894
Option 2D | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -70637734.0949 | -367611.5549 | -900058.0332 | -3182788.6187 | -20107254.8947 | -99355949.4593 | -2954264.6191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91344907.5696 | 91344907.5696 | 14 | 2537358.5436
Option 2D | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | -31322112.8055 | -290073.5228 | -384387.0441 | -909168.7657 | -11910563.8167 | -37455489.0607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29114104.12 | 29114104.12 | 15 | 1455705.206
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -17417601.8228 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15995339.8229 | 15995339.8229 | 15 | 799766.9911
Option 2D | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -9824340.3916 | 0 | 0 | 0 | 0 | -1047577 | -6968417 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13271217.525 | 13271217.525 | 13 | 491526.575
Option 3A | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | -54407792.0951 | -1041254.0248 | -2755096.888 | -21687177.713 | -60935329.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57036446.1876 | 57036446.1876 | 17 | 1728377.1572
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -17417601.8228 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15995339.8229 | 15995339.8229 | 15 | 799766.9911
Option 3A | 2 | 60 MVAr SVC at Narrabri 132 | 1 | $ | -9824340.3916 | 0 | 0 | 0 | 0 | -1047577 | -6968417 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13271217.525 | 13271217.525 | 13 | 491526.575
Option 3B | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | -54407792.0951 | -1041254.0248 | -2755096.888 | -21687177.713 | -60935329.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57036446.1876 | 57036446.1876 | 17 | 1728377.1572
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -17417601.8228 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15995339.8229 | 15995339.8229 | 15 | 799766.9911
Option 3B | 2 | Install 50 MW / 50 MWh BESS at Narrabri 132 | 1 | $ |  | Redacted to preserve confidentiality | [19 empty] | Redacted to preserve confidentiality
Option 3C | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | -54407792.0951 | -1041254.0248 | -2755096.888 | -21687177.713 | -60935329.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57036446.1876 | 57036446.1876 | 17 | 1728377.1572
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -34475020.3507 | 0 | -280164.9931 | -581512.839 | -2019198.3822 | -19947050.7231 | -42769235.622 | -1514936.9106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49662953.6078 | 49662953.6078 | 13 | 1342241.9894
Option 5A | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 5A | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality | [19 empty] | Redacted to preserve confidentiality
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | -40774440.4963 | 0 | 0 | 0 | -1041254.0248 | -2755096.888 | -21687177.713 | -60935329.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63949954.8164 | 63949954.8164 | 13 | 1728377.1572
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -14483219.8806 | 0 | 0 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17594873.8051 | 17594873.8051 | 13 | 799766.9911
Option 5B | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 5B | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality | [19 empty] | Redacted to preserve confidentiality
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | -40774440.4963 | 0 | 0 | 0 | -1041254.0248 | -2755096.888 | -21687177.713 | -60935329.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63949954.8164 | 63949954.8164 | 13 | 1728377.1572
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -14483219.8806 | 0 | 0 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17594873.8051 | 17594873.8051 | 13 | 799766.9911
Option 5C | 1 | 3rd Narrabri Tx | 1 | $ | -5862839.6561 | -562958.6578 | -3286846.5899 | -4322374.4822 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4699003.3448 | 4699003.3448 | 17 | 204304.4932
Option 5C | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality | [19 empty] | Redacted to preserve confidentiality
Option 5C | 2 | Rebuild 969 line as double circuit | 1 | $ | -40774440.4963 | 0 | 0 | 0 | -1041254.0248 | -2755096.888 | -21687177.713 | -60935329.2341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63949954.8164 | 63949954.8164 | 13 | 1728377.1572
Option 5C | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -14483219.8806 | 0 | 0 | -176326.0359 | -302125.5852 | -916273.6337 | -10037009.3916 | -16560110.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17594873.8051 | 17594873.8051 | 13 | 799766.9911
Biodiversity offset costs
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | -6799567.8446 | 0 | 0 | 0 | 0 | -12600000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9324000 | 9324000 | 13 | 252000
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -4429726.5643 | 0 | 0 | 0 | 0 | -8100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5832000 | 5832000 | 14 | 162000
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -4789341.6235 | 0 | 0 | 0 | -8100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5832000 | 5832000 | 14 | 162000
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -4429726.5643 | 0 | 0 | 0 | 0 | -8100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5832000 | 5832000 | 14 | 162000
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -8526442.2178 | 0 | 0 | 0 | 0 | -15800000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11692000 | 11692000 | 13 | 316000
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -4789341.6235 | 0 | 0 | 0 | -8100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5832000 | 5832000 | 14 | 162000
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -8526442.2178 | 0 | 0 | 0 | 0 | -15800000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11692000 | 11692000 | 13 | 316000
Property allowances
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | -23724028.5402 | 0 | 0 | 0 | 0 | -35000000 | -9720000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33092800 | 33092800 | 13 | 894400
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -10112934.6139 | 0 | 0 | 0 | 0 | -10000000 | -9200000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13824000 | 13824000 | 14 | 384000
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -10944061.8058 | 0 | 0 | 0 | -10000000 | -9200000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13824000 | 13824000 | 14 | 384000
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -10112934.6139 | 0 | 0 | 0 | 0 | -10000000 | -9200000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13824000 | 13824000 | 14 | 384000
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -11934497.7138 | 0 | 0 | 0 | 0 | -10000000 | -13140000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17123600 | 17123600 | 13 | 462800
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -13977008.6991 | 0 | 0 | 0 | -15000000 | -9340000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17524800 | 17524800 | 14 | 486800
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | -219900.2367 | 0 | 0 | -333278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219963.48 | 219963.48 | 17 | 6665.56
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | -219900.2367 | 0 | 0 | -333278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219963.48 | 219963.48 | 17 | 6665.56
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | -219900.2367 | 0 | 0 | -333278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 219963.48 | 219963.48 | 17 | 6665.56
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -11934497.7138 | 0 | 0 | 0 | 0 | -10000000 | -13140000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17123600 | 17123600 | 13 | 462800
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | -165827.7521 | 0 | 0 | 0 | 0 | 0 | -333278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246625.72 | 246625.72 | 13 | 6665.56
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | -165827.7521 | 0 | 0 | 0 | 0 | 0 | -333278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246625.72 | 246625.72 | 13 | 6665.56
Option 5C | 2 | Rebuild 969 line as double circuit | 1 | $ | -165827.7521 | 0 | 0 | 0 | 0 | 0 | -333278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246625.72 | 246625.72 | 13 | 6665.56
TNSP capital costs
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | -175465299.4012 | -3206685.9703 | -12900039.2896 | -67117200.6217 | -98252317.8702 | -57241104.781 | -23528527.1527 | -11645069.1544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156528811.4129
Option 1B |  |  |  | $ | -153598044.2715 | -2476045.6055 | -11876473.3307 | -65427657.4559 | -11731043.8705 | -81214032.7831 | -40613655.2791 | -52002700.1153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174944445.9811
Option 2A |  |  |  | $ | -101615038.8097 | -853032.1806 | -4152329.8479 | -6074347.2333 | -14665683.9801 | -82013947.9506 | -60650064.3221 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116640819.3207
Option 2B |  |  |  | $ | -83596795.8243 | -1059318.697 | -4160490.5939 | -7021259.298 | -44081128.3928 | -65529225.8791 | -11699086.9292 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98312314.479
Option 2C |  |  |  | $ | -130807776.1498 | -853032.1806 | -4256168.8051 | -6353734.4871 | -15768608.7286 | -116676412.2821 | -93030772.9006 | -1514936.9106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165053048.5895
Option 2D |  |  |  | $ | -153830979.0935 | -1396969.7715 | -4873417.2524 | -9330605.5004 | -65154828.1031 | -163759125.5635 | -9922681.6191 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177781372.3822
Option 3A |  |  |  | $ | -87732474.2023 | -1780538.7186 | -6344069.0631 | -27259103.829 | -70972338.6258 | -17607687.0435 | -6968417 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91221970.3602
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | -115426492.2702 | -1604212.6826 | -6322108.4711 | -26924343.0342 | -62954527.6163 | -45747050.7231 | -55909235.622 | -1514936.9106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140433966.6202
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
NNO capital costs
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Operating cost calculation
Option | Stage | Component | TNSP | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 1A | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -4973368.5562 | 0 | 0 | 0 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223
Option 1A | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -1799322.1832 | 0 | 0 | 0 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -2053864.9477 | 0 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 1A | 1 | Upgrade 968 line to 160 MVA rating | 1 | $ | -12047046.402 | 0 | 0 | 0 | 0 | 0 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157 | -1486830.157
Option 1A | 2 | 60 MVAr SVC at Narrabri | 1 | $ | -1300013.7416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347 | -196610.6347
Option 1B | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 1B | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -4973368.5562 | 0 | 0 | 0 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223 | -509496.8223
Option 1B | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -1799322.1832 | 0 | 0 | 0 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902 | -184331.5902
Option 1B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -2493995.0248 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | -6775756.2541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277 | -1024747.4277
Option 2A | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -3373700.6336 | 0 | 0 | 0 | 0 | 0 | 0 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488
Option 2A | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | -4128199.7333 | 0 | 0 | 0 | 0 | 0 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -2053864.9477 | 0 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 2A | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -1300013.7105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63
Option 2B | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -4554341.0205 | 0 | 0 | 0 | 0 | 0 | 0 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137 | -620704.9137
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -2268040.1677 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 2B | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -1300013.7105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63
Option 2C | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -3373700.6336 | 0 | 0 | 0 | 0 | 0 | 0 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488 | -459797.0488
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating | 1 | $ | -4128199.7333 | 0 | 0 | 0 | 0 | 0 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -4437534.7078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947
Option 2D | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -9308768.0182 | 0 | 0 | 0 | 0 | 0 | 0 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718 | -1268679.2718
Option 2D | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | -4128199.7333 | 0 | 0 | 0 | 0 | 0 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221 | -509496.8221
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -2268040.1677 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 2D | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -1300013.7105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63
Option 3A | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | -8435633.1882 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -2268040.1677 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 3A | 2 | 60 MVAr SVC at Narrabri 132 | 1 | $ | -1300013.7105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63 | -196610.63
Option 3B | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | -8435633.1882 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -2268040.1677 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 3B | 2 | Install 50 MW / 50 MWh BESS at Narrabri 132 | 1 | $ |  | Redacted to preserve confidentiality
Option 3C | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | -8435633.1882 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -4437534.7078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947 | -671120.9947
Option 5A | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 5A | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | -5714121.3609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -1850855.2605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 5B | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 5B | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | -5714121.3609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -1850855.2605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Option 5C | 1 | 3rd Narrabri Tx | 1 | $ | -797713.7428 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973 | -81721.7973
Option 5C | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 5C | 2 | Rebuild 969 line as double circuit | 1 | $ | -5714121.3609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786 | -864188.5786
Option 5C | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -1850855.2605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469 | -279918.4469
Biodiversity offset costs
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Property allowances
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5C | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TNSP operating expenditure
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | -22971329.5735 | 0 | 0 | 0 | -775550.2098 | -775550.2098 | -2262380.3668 | -2542298.8137 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484 | -2738909.4484
Option 1B |  |  |  | $ | -16840155.7611 | 0 | 0 | 0 | -775550.2098 | -1055468.6567 | -1055468.6567 | -1055468.6567 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844 | -2080216.0844
Option 2A |  |  |  | $ | -11653492.7679 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -591218.6194 | -1330934.1151 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451 | -1527544.7451
Option 2B |  |  |  | $ | -8920108.6415 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -361640.2442 | -982345.1579 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879 | -1178955.7879
Option 2C |  |  |  | $ | -12737148.8174 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -591218.6194 | -1051015.6682 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629 | -1722136.6629
Option 2D |  |  |  | $ | -17802735.3724 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -871137.0663 | -2139816.3381 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681 | -2336426.9681
Option 3A |  |  |  | $ | -12801400.8092 | 0 | 0 | 0 | -945910.3759 | -945910.3759 | -1225828.8228 | -1225828.8228 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528 | -1422439.4528
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | -13670881.6387 | 0 | 0 | 0 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706 | -1617031.3706
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
TSNP network service payments to NNO proponents
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
NNO operating expenditure
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided fuel consumption from generation dispatch
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided voluntary load curtailment
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding outside of NW Slopes
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding in NW Slopes
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 702376518.8904 | 0 | 0 | 0 | 101923393.4099 | 254011474.4685 | 245478789.2797 | 307082901.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 702376518.8904 | 0 | 0 | 0 | 101923393.4099 | 254011474.4685 | 245478789.2797 | 307082901.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 355507651.5318 | 0 | 0 | 0 | 0 | 0 | 173560442.6878 | 307082901.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 318810895.8638 | 0 | 0 | 0 | 0 | 0 | 125599250.6647 | 307082901.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 355507651.5318 | 0 | 0 | 0 | 0 | 0 | 173560442.6878 | 307082901.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 355507651.5318 | 0 | 0 | 0 | 0 | 0 | 173560442.6878 | 307082901.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 672671495.9977 | 0 | 0 | 0 | 67042526.4839 | 254011474.4685 | 245478789.2797 | 307082901.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 672671495.9977 | 0 | 0 | 0 | 67042526.4839 | 254011474.4685 | 245478789.2797 | 307082901.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided costs for non RIT-T proponent parties
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 4147577.2794 | 0 | 590456.1755 | 347314.6546 | 328621.0586 | -277268.9702 | 3712921.9201 | -3260389.4993 | 1089261.3727 | 3919887.3123 | -1233860.6647 | 1266730.5724 | 959375.3517 | -4139385.6945 | 183982.1705 | 2156625.4184 | -470851.4666 | 854642.2052 | -547904.3231 | -145878.9089 | 329651.1322
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (wood pole replacement)
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 758082.447 | 0 | 0 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 770331.1296 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 770331.1296 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (market benefits)
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
NNO receipts received from TNSP
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | Redacted to preserve confidentiality
Payback analysis
[6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
[6 empty] | 1 | 1.055 | 1.113 | 1.1742 | 1.2388 | 1.307 | 1.3788 | 1.4547 | 1.5347 | 1.6191 | 1.7081 | 1.8021 | 1.9012 | 2.0058 | 2.1161 | 2.2325 | 2.3553 | 2.4848 | 2.6215 | 2.7656
PV gross benefits
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ |  | 0 | 0 | 0 | 86799354.5278 | 205042315.1819 | 187824254.8171 | 222710594.3635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ |  | 0 | 0 | 0 | 86799354.5278 | 205042315.1819 | 187824254.8171 | 222710594.3635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 132797057.1683 | 222710594.3635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 96100301.5002 | 222716244.0597 | 5355.1622 | 35531.8822 | 33679.5092 | 31923.7054 | 30259.4364 | 28681.9302 | 69908.5638 | 66264.0416 | 62809.5181 | 59535.0882 | 56431.3632 | 139666.8811 | 132385.6693
Option 2C |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 132797057.1683 | 222710594.3635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 132797057.1683 | 222710594.3635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ |  | 0 | 0 | 0 | 57094331.6351 | 205048603.4349 | 187830215.2466 | 222716244.0597 | 5355.1622 | 35531.8822 | 33679.5092 | 31923.7054 | 30259.4364 | 28681.9302 | 69908.5638 | 66264.0416 | 62809.5181 | 59535.0882 | 56431.3632 | 139666.8811 | 132385.6693
Option 3B |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 3C |  |  |  | $ |  | 0 | 0 | 0 | 57094331.6351 | 205048603.4349 | 187830215.2466 | 222716244.0597 | 5355.1622 | 35531.8822 | 33679.5092 | 31923.7054 | 30259.4364 | 28681.9302 | 69908.5638 | 66264.0416 | 62809.5181 | 59535.0882 | 56431.3632 | 139666.8811 | 132385.6693
Option 5A |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Cumulative PV gross benefits
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ |  | 0 | 0 | 0 | 86799354.5278 | 291841669.7097 | 479665924.5268 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904
Option 1B |  |  |  | $ |  | 0 | 0 | 0 | 86799354.5278 | 291841669.7097 | 479665924.5268 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904 | 702376518.8904
Option 2A |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 132797057.1683 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318
Option 2B |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 96100301.5002 | 318816545.5599 | 318821900.7222 | 318857432.6044 | 318891112.1135 | 318923035.8189 | 318953295.2553 | 318981977.1855 | 319051885.7494 | 319118149.7909 | 319180959.309 | 319240494.3972 | 319296925.7604 | 319436592.6415 | 319568978.3108
Option 2C |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 132797057.1683 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318
Option 2D |  |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 132797057.1683 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318 | 355507651.5318
Option 3A |  |  |  | $ |  | 0 | 0 | 0 | 57094331.6351 | 262142935.0701 | 449973150.3167 | 672689394.3764 | 672694749.5386 | 672730281.4208 | 672763960.93 | 672795884.6354 | 672826144.0718 | 672854826.002 | 672924734.5658 | 672990998.6074 | 673053808.1254 | 673113343.2137 | 673169774.5769 | 673309441.458 | 673441827.1273
Option 3B |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 3C |  |  |  | $ |  | 0 | 0 | 0 | 57094331.6351 | 262142935.0701 | 449973150.3167 | 672689394.3764 | 672694749.5386 | 672730281.4208 | 672763960.93 | 672795884.6354 | 672826144.0718 | 672854826.002 | 672924734.5658 | 672990998.6074 | 673053808.1254 | 673113343.2137 | 673169774.5769 | 673309441.458 | 673441827.1273
Option 5A |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Total cost
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ |  | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747 | 198436628.9747
Option 1B |  |  |  | $ |  | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326 | 170438200.0326
Option 2A |  |  |  | $ |  | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776 | 113268531.5776
Option 2B |  |  |  | $ |  | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658 | 92516904.4658
Option 2C |  |  |  | $ |  | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673 | 143544924.9673
Option 2D |  |  |  | $ |  | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466 | 171633714.466
Option 3A |  |  |  | $ |  | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115 | 100533875.0115
Option 3B |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 3C |  |  |  | $ |  | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089 | 129097373.9089
Option 5A |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Option 5C |  |  |  | $ |  | 0: Redacted to preserve confidentiality
Payback
Option |  |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 1B |  |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2A |  |  |  | $ |  | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2B |  |  |  | $ |  | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2C |  |  |  | $ |  | NO | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2D |  |  |  | $ |  | NO | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 3A |  |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 3B |  |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 3C |  |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 5A |  |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 5B |  |  |  | $ |  | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 5C |  |  |  | $ |  | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES

## Weighted
Weighted | NPV results
NPV results
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | 374959114.2354 | -2934596.0501 | -12414898.7099 | -66173759.6512 | 9909630.1745 | 151534909.4324 | 168570128.7325 | 219885808.9706 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | 119870495.3621
Option 1B |  | $ | 394558014.495 | -2423147.7947 | -11698402.5386 | -64991079.4351 | 70474521.9743 | 134557916.9181 | 157455377.241 | 192676248.4079 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | 133222524.9146
Option 2A |  | $ | 175064977.5578 | -766010.1238 | -3984115.9239 | -5710958.928 | -10899354.5423 | -67533647.1122 | 79445699.6726 | 220803973.7768 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | 97654953.8076
Option 2B |  | $ | 158452007.671 | -1006420.8862 | -4069852.9183 | -6746377.2079 | -41151747.3726 | -60328641.5633 | 86992568.3742 | 221007503.7303 | -1028207.0219 | -981466.7644 | -981466.7644 | -981466.7644 | -981466.7644 | -981466.7644 | -895776.2923 | -895776.2923 | -895776.2923 | -895776.2923 | -895776.2923 | -669865.0476 | 88862482.2271
Option 2C |  | $ | 153871502.1851 | -766010.1238 | -4056803.1939 | -5906530.0057 | -11671401.8662 | -91797372.1442 | 56779203.6676 | 228091009.1522 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | 131407299.9533
Option 2D |  | $ | 117213663.0172 | -1257049.9039 | -4667463.4636 | -8782972.7806 | -58652277.9379 | -147321894.5295 | 125009106.4497 | 219995091.5538 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | 158226554.7434
Option 3A |  | $ | 418526675.0082 | -1727640.9078 | -6253431.3876 | -26984221.7389 | -17307842.2344 | 179115731.7255 | 180844473.9132 | 220764020.0654 | -1271690.6868 | -1224950.4293 | -1224950.4293 | -1224950.4293 | -1224950.4293 | -1224950.4293 | -1139259.9572 | -1139259.9572 | -1139259.9572 | -1139259.9572 | -1139259.9572 | -913348.7125 | 81528654.4434
Option 3B |  | $ | 406641152.6361 | Redacted to preserve confidentiality
Option 3C |  | $ | 398532225.78 | -1604212.6826 | -6238058.9732 | -26749889.1825 | -11695374.5277 | 159418177.1498 | 146781843.7906 | 228051055.4408 | -1407905.0293 | -1361164.7717 | -1361164.7717 | -1361164.7717 | -1361164.7717 | -1361164.7717 | -1275474.2996 | -1275474.2996 | -1275474.2996 | -1275474.2996 | -1275474.2996 | -1049563.0549 | 115840837.4829
Option 5A |  | $ | 398103223.0178 | Redacted to preserve confidentiality
Option 5B |  | $ | 458909145.628 | Redacted to preserve confidentiality
Option 5C |  | $ | 441486275.527 | Redacted to preserve confidentiality
Weighted | Calculation
TNSP capital costs
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | -139465138.5995 | -2934596.0501 | -12414898.7099 | -66173759.6512 | -68776622.5092 | -40068773.3467 | -16469969.0069 | -8151548.4081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122020397.0389
Option 1B |  | $ | -124158060.0087 | -2423147.7947 | -11698402.5386 | -64991079.4351 | -8211730.7093 | -56849822.9482 | -28429558.6953 | -36401890.0807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134911341.2366
Option 2A |  | $ | -84495438.0854 | -766010.1238 | -3984115.9239 | -5710958.928 | -10817632.745 | -67451925.3149 | -53591506.2091 | -8151548.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98886690.783
Option 2B |  | $ | -75424213.16 | -1006420.8862 | -4069852.9183 | -6746377.2079 | -41070025.5753 | -60246919.766 | -9608561.8292 | -8151548.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89532347.2747
Option 2C |  | $ | -104930354.2235 | -766010.1238 | -4056803.1939 | -5906530.0057 | -11589680.0689 | -91715650.3469 | -76258002.214 | -1060455.8374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132775251.2712
Option 2D |  | $ | -136261762.5876 | -1257049.9039 | -4667463.4636 | -8782972.7806 | -58570556.1406 | -147240172.7322 | -7832156.5191 | -8151548.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160267173.9418
Option 3A |  | $ | -79559891.538 | -1727640.9078 | -6253431.3876 | -26984221.7389 | -67961235.8083 | -12325380.9305 | -4877891.9 | -8151548.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82442003.1559
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | -98945704.1855 | -1604212.6826 | -6238058.9732 | -26749889.1825 | -62348768.1016 | -32022935.5062 | -39136464.9354 | -1060455.8374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116890400.5378
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
NNO capital costs
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
TNSP operating expenditure
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | -18351052.0461 | 0 | 0 | 0 | -775550.2098 | -775550.2098 | -1816331.3197 | -2012274.2325 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768 | -2149901.6768
Option 1B |  | $ | -14059230.3774 | 0 | 0 | 0 | -775550.2098 | -971493.1226 | -971493.1226 | -971493.1226 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322 | -1688816.322
Option 2A |  | $ | -9408869.2505 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -438369.5728 | -1094109.5344 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754 | -1231736.9754
Option 2B |  | $ | -7849692.478 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -277664.7101 | -898369.6238 | -1035997.0648 | -1035997.0648 | -1035997.0648 | -1035997.0648 | -1035997.0648 | -1035997.0648 | -1035997.0648 | -1035997.0648 | -1035997.0648 | -1035997.0648 | -1035997.0648 | -1035997.0648 | -1035997.0648
Option 2C |  | $ | -10167428.4851 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -438369.5728 | -898166.6216 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179 | -1367951.3179
Option 2D |  | $ | -15493859.289 | 0 | 0 | 0 | -81721.7973 | -81721.7973 | -634312.4856 | -1902991.7574 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984 | -2040619.1984
Option 3A |  | $ | -11730984.6457 | 0 | 0 | 0 | -945910.3759 | -945910.3759 | -1141853.2887 | -1141853.2887 | -1279480.7297 | -1279480.7297 | -1279480.7297 | -1279480.7297 | -1279480.7297 | -1279480.7297 | -1279480.7297 | -1279480.7297 | -1279480.7297 | -1279480.7297 | -1279480.7297 | -1279480.7297 | -1279480.7297
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | -12339621.2264 | 0 | 0 | 0 | -945910.3759 | -945910.3759 | -945910.3759 | -945910.3759 | -1415695.0722 | -1415695.0722 | -1415695.0722 | -1415695.0722 | -1415695.0722 | -1415695.0722 | -1415695.0722 | -1415695.0722 | -1415695.0722 | -1415695.0722 | -1415695.0722 | -1415695.0722 | -1415695.0722
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
TSNP network service payments to NNO proponents
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
NNO operating expenditure
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
Avoided fuel consumption from generation dispatch
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
Avoided voluntary load curtailment
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding outside of NW Slopes
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding in NW Slopes
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | 532775304.881 | 0 | 0 | 0 | 79461802.8934 | 192379232.989 | 186856429.059 | 230049631.6112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 532775304.881 | 0 | 0 | 0 | 79461802.8934 | 192379232.989 | 186856429.059 | 230049631.6112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 268969284.8937 | 0 | 0 | 0 | 0 | 0 | 133475575.4544 | 230049631.6112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 240967830.862 | 0 | 0 | 0 | 0 | 0 | 96878794.9136 | 230049631.6112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 268969284.8937 | 0 | 0 | 0 | 0 | 0 | 133475575.4544 | 230049631.6112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 268969284.8937 | 0 | 0 | 0 | 0 | 0 | 133475575.4544 | 230049631.6112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 509047220.0623 | 0 | 0 | 0 | 51599303.9498 | 192379232.989 | 186856429.059 | 230049631.6112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | 509047220.0623 | 0 | 0 | 0 | 51599303.9498 | 192379232.989 | 186856429.059 | 230049631.6112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
Avoided costs for non RIT-T proponent parties
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (wood pole replacement)
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 758082.447 | 0 | 0 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 770331.1296 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | 770331.1296 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172 | 366132.0172
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (market benefits)
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
NNO receipts received from TNSP
Option |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ |  | Redacted to preserve confidentiality
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Option 5C |  | $ |  | Redacted to preserve confidentiality
Payback analysis
PV gross benefits
Option |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  | $ |  | 0 | 0 | 0 | 67670757.1247 | 155291737.9323 | 142970273.1091 | 166842536.7149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  | $ |  | 0 | 0 | 0 | 67670757.1247 | 155291737.9323 | 142970273.1091 | 166842536.7149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 102126748.1788 | 166842536.7149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 74125294.1471 | 166848186.411 | 5355.1622 | 35531.8822 | 33679.5092 | 31923.7054 | 30259.4364 | 28681.9302 | 69908.5638 | 66264.0416 | 62809.5181 | 59535.0882 | 56431.3632 | 139666.8811 | 132385.6693
Option 2C |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 102126748.1788 | 166842536.7149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 102126748.1788 | 166842536.7149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  | $ |  | 0 | 0 | 0 | 43942672.306 | 155298026.1854 | 142976233.5386 | 166848186.411 | 5355.1622 | 35531.8822 | 33679.5092 | 31923.7054 | 30259.4364 | 28681.9302 | 69908.5638 | 66264.0416 | 62809.5181 | 59535.0882 | 56431.3632 | 139666.8811 | 132385.6693
Option 3B |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  | $ |  | 0 | 0 | 0 | 43942672.306 | 155298026.1854 | 142976233.5386 | 166848186.411 | 5355.1622 | 35531.8822 | 33679.5092 | 31923.7054 | 30259.4364 | 28681.9302 | 69908.5638 | 66264.0416 | 62809.5181 | 59535.0882 | 56431.3632 | 139666.8811 | 132385.6693
Option 5A |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  | $ |  | Redacted to preserve confidentiality
Cumulative PV gross benefits
Option |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  | $ |  | 0 | 0 | 0 | 67670757.1247 | 222962495.0571 | 365932768.1662 | 532775304.881 | 532775304.881 | 532775304.881 | 532775304.881 | 532775304.881 | 532775304.881 | 532775304.881 | 532775304.881 | 532775304.881 | 532775304.881 | 532775304.881 | 532775304.881 | 532775304.881 | 532775304.881
Option 1B |  |  | $ |  | 0 | 0 | 0 | 67670757.1247 | 222962495.0571 | 365932768.1662 | 532775304.881 | 532775304.881 | 532775304.881 | 532775304.881 | 532775304.881 | 532775304.881 | 532775304.881 | 532775304.881 | 532775304.881 | 532775304.881 | 532775304.881 | 532775304.881 | 532775304.881 | 532775304.881
Option 2A |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 102126748.1788 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937
Option 2B |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 74125294.1471 | 240973480.5581 | 240978835.7204 | 241014367.6026 | 241048047.1117 | 241079970.8171 | 241110230.2535 | 241138912.1837 | 241208820.7476 | 241275084.7891 | 241337894.3072 | 241397429.3954 | 241453860.7586 | 241593527.6397 | 241725913.309
Option 2C |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 102126748.1788 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937
Option 2D |  |  | $ |  | 0 | 0 | 0 | 0 | 0 | 102126748.1788 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937 | 268969284.8937
Option 3A |  |  | $ |  | 0 | 0 | 0 | 43942672.306 | 199240698.4914 | 342216932.03 | 509065118.441 | 509070473.6033 | 509106005.4855 | 509139684.9946 | 509171608.7 | 509201868.1364 | 509230550.0666 | 509300458.6305 | 509366722.672 | 509429532.1901 | 509489067.2783 | 509545498.6415 | 509685165.5226 | 509817551.1919
Option 3B |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  | $ |  | 0 | 0 | 0 | 43942672.306 | 199240698.4914 | 342216932.03 | 509065118.441 | 509070473.6033 | 509106005.4855 | 509139684.9946 | 509171608.7 | 509201868.1364 | 509230550.0666 | 509300458.6305 | 509366722.672 | 509429532.1901 | 509489067.2783 | 509545498.6415 | 509685165.5226 | 509817551.1919
Option 5A |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  | $ |  | Redacted to preserve confidentiality
Total cost
Option |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  | $ |  | 157816190.6456 | 157816190.6456 | 157816190.6456 | 157816190.6456 | 157816190.6456 | 157816190.6456 | 157816190.6456 | 157816190.6456 | 157816190.6456 | 157816190.6456 | 157816190.6456 | 157816190.6456 | 157816190.6456 | 157816190.6456 | 157816190.6456 | 157816190.6456 | 157816190.6456 | 157816190.6456 | 157816190.6456 | 157816190.6456
Option 1B |  |  | $ |  | 138217290.3861 | 138217290.3861 | 138217290.3861 | 138217290.3861 | 138217290.3861 | 138217290.3861 | 138217290.3861 | 138217290.3861 | 138217290.3861 | 138217290.3861 | 138217290.3861 | 138217290.3861 | 138217290.3861 | 138217290.3861 | 138217290.3861 | 138217290.3861 | 138217290.3861 | 138217290.3861 | 138217290.3861 | 138217290.3861
Option 2A |  |  | $ |  | 93904307.3359 | 93904307.3359 | 93904307.3359 | 93904307.3359 | 93904307.3359 | 93904307.3359 | 93904307.3359 | 93904307.3359 | 93904307.3359 | 93904307.3359 | 93904307.3359 | 93904307.3359 | 93904307.3359 | 93904307.3359 | 93904307.3359 | 93904307.3359 | 93904307.3359 | 93904307.3359 | 93904307.3359 | 93904307.3359
Option 2B |  |  | $ |  | 83273905.638 | 83273905.638 | 83273905.638 | 83273905.638 | 83273905.638 | 83273905.638 | 83273905.638 | 83273905.638 | 83273905.638 | 83273905.638 | 83273905.638 | 83273905.638 | 83273905.638 | 83273905.638 | 83273905.638 | 83273905.638 | 83273905.638 | 83273905.638 | 83273905.638 | 83273905.638
Option 2C |  |  | $ |  | 115097782.7086 | 115097782.7086 | 115097782.7086 | 115097782.7086 | 115097782.7086 | 115097782.7086 | 115097782.7086 | 115097782.7086 | 115097782.7086 | 115097782.7086 | 115097782.7086 | 115097782.7086 | 115097782.7086 | 115097782.7086 | 115097782.7086 | 115097782.7086 | 115097782.7086 | 115097782.7086 | 115097782.7086 | 115097782.7086
Option 2D |  |  | $ |  | 151755621.8766 | 151755621.8766 | 151755621.8766 | 151755621.8766 | 151755621.8766 | 151755621.8766 | 151755621.8766 | 151755621.8766 | 151755621.8766 | 151755621.8766 | 151755621.8766 | 151755621.8766 | 151755621.8766 | 151755621.8766 | 151755621.8766 | 151755621.8766 | 151755621.8766 | 151755621.8766 | 151755621.8766 | 151755621.8766
Option 3A |  |  | $ |  | 91290876.1837 | 91290876.1837 | 91290876.1837 | 91290876.1837 | 91290876.1837 | 91290876.1837 | 91290876.1837 | 91290876.1837 | 91290876.1837 | 91290876.1837 | 91290876.1837 | 91290876.1837 | 91290876.1837 | 91290876.1837 | 91290876.1837 | 91290876.1837 | 91290876.1837 | 91290876.1837 | 91290876.1837 | 91290876.1837
Option 3B |  |  | $ |  | Redacted to preserve confidentiality
Option 3C |  |  | $ |  | 111285325.4119 | 111285325.4119 | 111285325.4119 | 111285325.4119 | 111285325.4119 | 111285325.4119 | 111285325.4119 | 111285325.4119 | 111285325.4119 | 111285325.4119 | 111285325.4119 | 111285325.4119 | 111285325.4119 | 111285325.4119 | 111285325.4119 | 111285325.4119 | 111285325.4119 | 111285325.4119 | 111285325.4119 | 111285325.4119
Option 5A |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  | $ |  | Redacted to preserve confidentiality
Option 5C |  |  | $ |  | Redacted to preserve confidentiality
Payback
Option |  |  | Unit | PV | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042
Option 1A |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 1B |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2A |  |  | $ |  | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2B |  |  | $ |  | NO | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2C |  |  | $ |  | NO | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 2D |  |  | $ |  | NO | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 3A |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 3B |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 3C |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 5A |  |  | $ |  | NO | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 5B |  |  | $ |  | NO | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES
Option 5C |  |  | $ |  | NO | NO | NO | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES