## Sunraysia SF
Generator name | Capacity (MW) | (1) Ancillary service requirements | (2) Level and pattern of network congestion | (3) Impact on timing of expenditure on the network | (4) Impact on interconnector power transfer capability
Sunraysia Solar Farm | 200 | There were no new ancillary service contracts in South-western NSW in the 12 months prior to, or following, the commissioning of the Sunraysia SF. | The connection of Sunraysia SF has increased the generation capacity in South Western NSW. When Sunraysia is generating, it has the potential to reduce the power transfer from VNI into Wagga (i.e. reduced utilisation of lines 63) and increase the utilisation of South Western NSW 132kV network lines (i.e. the utilisation of 132kV line X5 from Balranald to Darlington Point). A new constraint equation to limit power flow on line X5 from Balranald to Darlington Point (X5) to avoid voltage collapse at Balranald for contingency trip of any major 220kV line in NW Victoria was created after the connection of Sunraysia SF and the constraint equation was binding for approximately 104 hours in the 12 months following the connection of Sunraysia SF. There are many factors that impact the operation of Darlington Point Voltage constraint equation: - the relative operation of the existing generating units in NSW - NEM dispatch price in NSW and VIC - network outages (planned and unplanned) significantly impact the power transfer limits. All of the above have a far greater impact on the utilisation of VNI and the South Western NSW network compared to a connection of any single SF in South Western NSW. The constraints in the NEM dispatch system can also not specifically by attributed to any single generator. Therefore, it cannot be said that the connection of Sunraysia SF has specifically had a material impact on network congestion in the main 330, 220 kV and 132 kV system network, however it is a contributing factor. Localised historical transmission line flows were investigated surrounding Sunraysia SF in the south western 132kV network, showing congestion may occur due to Sunraysia SF. This is managed by runback and transfer trip schemes in operation and lines were well utilised but did not exceed contingency ratings.This is managed by runback and transfer trip schemes in operation and lines were well utilised but did not exceed contingency ratings. The system strenght schemes are for outages of lines X3, 63, OX1, X5 and either TX. | No project timings have been affected by the inclusion of the Sunraysia SF. Timing of upgrades to the VNI to NSW interconnector identified in Section 2.1.2 of TransGrid's 2021 TAPR is not specifically affected by the Sunraysia SF. | Sunraysia SF has positive contribution factor in N^^N_NIL_1, N^^N_NIL_2 and N^^N_NIL_3, which menas it may reduce the transfer capability of VNI. The Sunraysia SF has no direct impact on the southerly or northerly power transfer capability between QLD and NSW .
Note on D1: Dragana Hele: Compare it with constraint spreadsheet