## Overview of the model
Bathurst, Orange and Parkes PADR economic assessment
Legend applied throughout the model template
Table Row Name
Input Cell
Calculation cell
Parameter Cell
Output Cell

## Results
Scenarios |  |  |  |  | S1 | S2 | S4
General inputs and sensitivities |  |  |  | Unit | Central | High | Low
Commercial discount rate |  |  |  | % | 5.5% | 2.23% | 7.5%
VCR |  |  |  | $/MWh | 53484 | 69529.2 | 37438.8
Cost inputs and sensitivities |  |  |  | Unit | Central | High | Low
Network capital costs |  |  |  | Factor | 1 | 0.75 | 1.25
NNO capital costs |  |  |  | Factor | 1 | 1 | 1
Operating and maintenance costs |  |  |  | Factor | 1 | 0.75 | 1.25
Market benefit inputs and sensitivities |  |  |  | Unit | Central | High | Low
Avoided fuel consumption from generation dispatch |  |  |  | Factor | 1 | 1.3 | 0.7
Avoided voluntary load curtailment |  |  |  | Factor | 1 | 1.3 | 0.7
Avoided involuntary load shedding outside of CW NSW |  |  |  | Factor | 1 | 1.3 | 0.7
Avoided costs for non RIT-T proponent parties |  |  |  | Factor | 1 | 1.3 | 0.7
Avoided unrelated TNSP expenditure |  |  |  | Factor | 1 | 1.3 | 0.7
Competition benefits |  |  |  | Factor | 1 | 1.3 | 0.7
Scenario weighting settings |  |  |  | Unit | Central | High | Low
Scenario weighting |  |  |  | % | 50% | 25% | 25%
NPV results
Option | Unit | Central | High | Low | Weighted | Rank | % from 1st
Option 1A/1B | $NPV | -186.9378 | -139.6044 | -124.5846 | -159.5162 | 10 | -4.07%
Option 1C | $NPV | 1377.8532 | 3099.3004 | -102.9599 | 1438.0117 | 9 | 36.69%
Option 3 | $NPV | 1383.4753 | 3399.5305 | -98.594 | 1516.9718 | 5 | 38.7%
Option 4 | $NPV | 1370.1218 | 3370.4108 | -98.594 | 1503.0151 | 6 | 38.34%
Option 5 | $NPV | 1355.4859 | 3389.7824 | -143.0597 | 1489.4236 | 7 | 38%
Option 6 | $NPV | 1342.1323 | 3360.6628 | -143.0597 | 1475.4669 | 8 | 37.64%
Option 7A | $NPV | 3528.2409 | 8442.5331 | -174.1785 | 3831.2091 | 3 | 97.74%
Option 7B | $NPV | 3545.1724 | 8556.387 | -204.6078 | 3860.531 | 2 | 98.49%
Option 7C | $NPV | 3518.7392 | 8470.6119 | -227.5173 | 3820.1433 | 4 | 97.46%
Option 7D | $NPV | 3625.4606 | 8468.3899 | -40.332 | 3919.7448 | 1 | 100%
S1 | Central | [9 empty] | S2 | High | [9 empty] | S3 | Low | [9 empty] | Weighted
NPV result | Central | [9 empty] | NPV result | High | [9 empty] | NPV result | Low | [9 empty] | NPV result | Weighted
NPV breakdown | Central | [9 empty] | NPV breakdown | High | [9 empty] | NPV breakdown | Low | [9 empty] | NPV breakdown | Weighted
Option | Option 1A/1B | Option 1C | Option 3 | Option 4 | Option 5 | Option 6 | Option 7A | Option 7B | Option 7C | Option 7D | Option | Option 1A/1B | Option 1C | Option 3 | Option 4 | Option 5 | Option 6 | Option 7A | Option 7B | Option 7C | Option 7D | Option | Option 1A/1B | Option 1C | Option 3 | Option 4 | Option 5 | Option 6 | Option 7A | Option 7B | Option 7C | Option 7D | Option | Option 1A/1B | Option 1C | Option 3 | Option 4 | Option 5 | Option 6 | Option 7A | Option 7B | Option 7C | Option 7D
TNSP capital costs | -150.8618 | -112.5346 | -108.5345 | -121.6691 |  |  | Redacted to preserve confidentiality |  |  |  | TNSP capital costs | -100.2627 | -96.0903 | -88.0328 | -112.3293 |  |  | Redacted to preserve confidentiality |  |  |  | TNSP capital costs | -106.3891 | -89.0175 | -83.0511 | -83.0511 |  |  | Redacted to preserve confidentiality |  |  |  | TNSP capital costs | -127.0939 | -102.5443 | -97.0382 | -109.6797 |  |  | Redacted to preserve confidentiality
NNO capital costs | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | NNO capital costs | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | NNO capital costs | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | NNO capital costs | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality
TNSP operating expenditure | -36.076 | -25.3834 | -28.5085 | -28.7274 |  |  | Redacted to preserve confidentiality |  |  |  | TNSP operating expenditure | -39.3417 | -37.3104 | -37.8045 | -42.6276 |  |  | Redacted to preserve confidentiality |  |  |  | TNSP operating expenditure | -18.1955 | -16.007 | -17.6075 | -17.6075 |  |  | Redacted to preserve confidentiality |  |  |  | TNSP operating expenditure | -32.4223 | -26.0211 | -28.1072 | -29.4225 |  |  | Redacted to preserve confidentiality
TNSP payments to NNO proponents | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | TNSP payments to NNO proponents | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | TNSP payments to NNO proponents | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | TNSP payments to NNO proponents | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality
NNO operating expenditure | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | NNO operating expenditure | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | NNO operating expenditure | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | NNO operating expenditure | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality
Avoided fuel consumption from generation dispatch | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | Avoided fuel consumption from generation dispatch | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | Avoided fuel consumption from generation dispatch | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | Avoided fuel consumption from generation dispatch | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality
Avoided voluntary load curtailment | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | Avoided voluntary load curtailment | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | Avoided voluntary load curtailment | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | Avoided voluntary load curtailment | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality
Avoided involuntary load shedding - outside of CW NSW | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | Avoided involuntary load shedding - outside of CW NSW | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | Avoided involuntary load shedding - outside of CW NSW | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | Avoided involuntary load shedding - outside of CW NSW | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality
Avoided involuntary load shedding in CW NSW | 0 | 1515.7713 | 1520.5183 | 1520.5183 |  |  | Redacted to preserve confidentiality |  |  |  | Avoided involuntary load shedding in CW NSW | 0 | 3232.7011 | 3525.3678 | 3525.3678 |  |  | Redacted to preserve confidentiality |  |  |  | Avoided involuntary load shedding in CW NSW | 0 | 2.0646 | 2.0646 | 2.0646 |  |  | Redacted to preserve confidentiality |  |  |  | Avoided involuntary load shedding in CW NSW | 0 | 1566.5771 | 1642.1172 | 1642.1172 |  |  | Redacted to preserve confidentiality
Avoided costs for non RIT-T proponent parties | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | Avoided costs for non RIT-T proponent parties | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | Avoided costs for non RIT-T proponent parties | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | Avoided costs for non RIT-T proponent parties | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | Avoided unrelated TNSP expenditure | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | Avoided unrelated TNSP expenditure | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | Avoided unrelated TNSP expenditure | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality
NNO receipts received from TNSP | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | NNO receipts received from TNSP | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | NNO receipts received from TNSP | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality |  |  |  | NNO receipts received from TNSP | 0 | 0 | 0 | 0 |  |  | Redacted to preserve confidentiality
NPV | -186.9378 | 1377.8532 | 1383.4753 | 1370.1218 | 1355.4859 | 1342.1323 | 3528.2409 | 3545.1724 | 3518.7392 | 3625.4606 | NPV | -139.6044 | 3099.3004 | 3399.5305 | 3370.4108 | 3389.7824 | 3360.6628 | 8442.5331 | 8556.387 | 8470.6119 | 8468.3899 | NPV | -124.5846 | -102.9599 | -98.594 | -98.594 | -143.0597 | -143.0597 | -174.1785 | -204.6078 | -227.5173 | -40.332 | NPV | -159.5162 | 1438.0117 | 1516.9718 | 1503.0151 | 1489.4236 | 1475.4669 | 3831.2091 | 3860.531 | 3820.1433 | 3919.7448
Sensitivities 7.5.2 - 7.5.6
Option | Unit | Central | High | Sensitivity 7.5.2 | Low | Weighted | Rank | %
Option 1A/1B | $NPV | -186.9378 | -139.6044 | -124.5846 | -124.5846 | -159.5162 | 10 | -4.07%
Option 1C | $NPV | 1377.8532 | 3099.3004 | -66.0239 | -102.9599 | 1438.0117 | 9 | 36.69%
Option 3 | $NPV | 1383.4753 | 3399.5305 | -98.594 | -98.594 | 1516.9718 | 5 | 38.7%
Option 4 | $NPV | 1370.1218 | 3370.4108 | -98.594 | -98.594 | 1503.0151 | 6 | 38.34%
Option 5 | $NPV | 1355.4859 | 3389.7824 | -143.0597 | -143.0597 | 1489.4236 | 7 | 38%
Option 6 | $NPV | 1342.1323 | 3360.6628 | -143.0597 | -143.0597 | 1475.4669 | 8 | 37.64%
Option 7A | $NPV | 3528.2409 | 8442.5331 | -174.1785 | -174.1785 | 3831.2091 | 3 | 97.74%
Option 7B | $NPV | 3545.1724 | 8556.387 | -204.6078 | -204.6078 | 3860.531 | 2 | 98.49%
Option 7C | $NPV | 3518.7392 | 8470.6119 | -227.5173 | -227.5173 | 3820.1433 | 4 | 97.46%
Option 7D | $NPV | 3625.4606 | 8468.3899 | -40.332 | -40.332 | 3919.7448 | 1 | 100%
Low demand forecast in central scenario
| Central | Sensitivity
Option 1A/1B | -186.9378 | -186.9378
Option 1C | 1377.8532 | -134.6782
Option 3 | 1383.4753 | -133.8032
Option 4 | 1370.1218 | -147.1567
Option 5 | 1355.4859 | -161.7926
Option 6 | 1342.1323 | -175.1461
Option 7A | 3528.2409 | -178.427
Option 7B | 3545.1724 | -161.4955
Option 7C | 3518.7392 | -187.5089
Option 7D | 3625.4606 | -81.2073
25% lower battery reinvestment costs
| Core | Sensitivity
Option 1A/1B | -159.5162 | -159.5162
Option 1C | 1438.0117 | 1438.0117
Option 3 | 1516.9718 | 1516.9718
Option 4 | 1503.0151 | 1503.0151
Option 5 | 1489.4236 | 1489.4236
Option 6 | 1475.4669 | 1475.4669
Option 7A | 3831.2091 | 3838.2065
Option 7B | 3860.531 | 3860.531
Option 7C | 3820.1433 | 3842.0319
Option 7D | 3919.7448 | 3920.8342
High discount rate
| Option 1A/1B | -180.2729
| Option 1C | 1246.9632
| Option 3 | 1254.5205
| Option 4 | 1242.1132
| Option 5 | 1229.6822
| Option 6 | 1217.275
| Option 7A | 3237.5059
| Option 7B | 3233.5593
| Option 7C | 3232.5375
| Option 7D | 3344.0447
Low discount rate
| Option 1A/1B | -186.1392
| Option 1C | 1637.0898
| Option 3 | 1637.2587
| Option 4 | 1623.7734
| Option 5 | 1601.1463
| Option 6 | 1587.661
| Option 7A | 4083.1763
| Option 7B | 4153.1212
| Option 7C | 4062.7208
| Option 7D | 4156.6998
High capex
| Option 1A/1B | -224.6533
| Option 1C | 1349.7196
| Option 3 | 1356.3417
| Option 4 | 1339.7045
| Option 5 | 1316.6239
| Option 6 | 1299.9867
| Option 7A | 3517.6803
| Option 7B | 3534.6118
| Option 7C | 3508.1785
| Option 7D | 3614.8999
Low capex
| Option 1A/1B | -149.2224
| Option 1C | 1405.9869
| Option 3 | 1410.6089
| Option 4 | 1400.5391
| Option 5 | 1394.3479
| Option 6 | 1384.278
| Option 7A | 3538.8016
| Option 7B | 3555.7331
| Option 7C | 3529.2999
| Option 7D | 3636.0212

## Chart tables (hidden)
Chart tables
First ranked option |  | Option 7D |  | LH to complete
Real
Option 7D | #REF! |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Option 7D | #REF! |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Option 7D | #REF! |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Option 7D | #REF! |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Discounted |  |  | 1 | 0.94787 | 0.89845 | 0.85161 | 0.80722 | 0.76513 | 0.72525 | 0.68744 | 0.6516 | 0.61763 | 0.58543 | 0.55491 | 0.52598 | 0.49856 | 0.47257 | 0.44793 | 0.42458 | 0.40245 | 0.38147 | 0.36158 | 0.34273 | 0.32486 | 0.30793 | 0.29187 | 0.27666 | 0.26223 | 0.24856 | 0.2356 | 0.22332 | 0.21168
Option 7D | #REF! |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Option 7D | #REF! |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Option 7D | #REF! |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Option 7D | #REF! |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Discounted |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7D | #REF! |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
#REF! |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#REF! |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#REF! |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#REF! |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#REF! |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#REF! |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Option 7D | #REF! |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Option 7D | #REF! |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Option 7D | #REF! |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Option 1C
Options 3, 4, 5, 6
|  | Options 7A, 7B, 7D | 2023: 0; 2024: 4862534.104; 2025: 514914259.0095; 2026: 2109800130.8296; 2027: 1920681529.6026
Option 7C

## General inputs
General parameter and option inputs
General parameters
Parameter | Unit | Value
First year of analysis | Year | 2022
Discount year | Year | 2022
Analysis period | Years | 20
Option inputs
Options | Short description
Base | No investment
Option 1A/1B | Stage 1: Install a 330/132 kV substation at Orange (2 transformers, 132kv line to Orange North) Stage 2: Install a 132 kV line between Wellington and Parkes
Option 1C | Stage 1: Install syncon at Parkes 132 kV (40 MVA) Stage 2: Install a 330/132 kV substation at Orange (2 transformers, 132kv line to Orange North) Stage 3: Install syncon at Parkes 132 kV (30 MVA) Stage 4: Install 2 syncons at Parkes 132 kV (2 * 30MVA)
Option 3 | Stage 1: Install SVC at Panorama 132 kV (25 MVA) and 3 syncons at Parkes 132 kV (3 * 30 MVA) Stage 2: Install a 132 kV line between Wellington and Parkes
Option 4 | Stage 1: Install SVC at Panorama 132 kV (25 MVA) and 3 syncons at Parkes 132 kV (3 * 30 MVA) Stage 2: Install a 330/132 kV substation at Orange (2 transformers, 132kv line to Orange North) Stage 3: Install syncon at Parkes 132 kV (40 MVA)
Option 5 | Stage 1: Install 2 30 MVAr syncons at Parkes, a 15MW (30 MWh) battery at Parkes and a 20 MW (40 MWh) battery at Panorama Stage 2: Install a 132 kV line between Wellington and Parkes
Option 6 | Stage 1: Install 2 30 MVAr syncons at Parkes, a 15MW (30 MWh) battery at Parkes and a 20 MW (40 MWh) battery at Panorama Stage 2: Install a 330/132 kV substation at Orange (2 transformers, 132kv line to Orange North) Stage 3: Install a syncon at Parkes 132 kV (40 MVA)
Option 7A | Stage 1: Solar PV and BESS at Parkes; BESS at Panorama Stage 2: Install a 132 kV line between Wellington and Parkes
Option 7B | Stage 1: Solar PV and BESS at Parkes; BESS at Panorama Stage 2: Install a 132 kV line between Wellington and Parkes
Option 7C | Stage 1: BESS at Parkes; BESS at Panorama Stage 2: Install a 132 kV line between Wellington and Parkes
Option 7D | Stage 1: BESS at Parkes; BESS at Panorama; 2*42.5 MVA syncons Stage 2: Install a 132 kV line between Wellington and Parkes

## CBA inputs
CBA cost inputs
All years in the input sheet are expressed as financial years. ie 2022 refers to FY2021/22 that covers the period from 1 July 2021 to 30 June 2022.
All commissioning dates post 2041 are stated as N/A for consistency.
Capital costs |  | S1 | S2 | S3 | S4
Option name | Capex component | Commission year - central | Commission year - high | Commission year - low (sensitivity 7.5.2) | Commission year - low | Asset life | 1 if TNSP owns asset | Amount | Build year 1 | Build year 2 | Build year 3 | Build year 4 | Build year 5 | Build year 6
Option 1A/1B | Stage 1: line | 2028 | 2028 | 2028 | 2028 | 40 | 1 | 32145916.8154 | 369584.1317 | 911433.596 | 2531172.9888 | 13116120.4567 | 15217605.6421
Option 1A/1B | Stage 1: substation (inc. the 2 TFs) | 2028 | 2028 | 2028 | 2028 | 40 | 1 | 90938043.1846 | 720424.5162 | 1910871.303 | 5679005.4949 | 31953027.13 | 50674714.7405
Option 1A/1B | Stage 2: line | 2028 | 2028 | #N/A | #N/A | 40 | 1 | 122753453 | 500490 | 968373 | 3205108 | 11802832 | 96622262 | 9654388
Option 1C | Stage 1: syncon | 2027 | 2027 | 2027 | 2027 | 40 | 1 | 30200162 | 1453876 | 8092064 | 19995479 | 658743
Option 1C | Stage 2: line | 2028 | 2028 | 2036 | 2032 | 40 | 1 | 32145916.8154 | 369584.1317 | 911433.596 | 2531172.9888 | 13116120.4567 | 15217605.6421
Option 1C | Stage 2: substation (inc. the 2 TFs) | 2028 | 2028 | 2036 | 2032 | 40 | 1 | 90938043.1846 | 720424.5162 | 1910871.303 | 5679005.4949 | 31953027.13 | 50674714.7405
Option 1C | Stage 3: syncon | 2032 | 2028 | #N/A | #N/A | 40 | 1 | 26068664 | 1236083 | 6996825 | 17274814 | 560942
Option 1C | Stage 4: 2 x syncons | #N/A | 2028 | #N/A | #N/A | 40 | 1 | 51256387 | 2456948 | 13740648 | 33945068 | 1113723
Option 3 | Stage 1: SVC at Panorama | 2027 | 2027 | 2027 | 2027 | 20 | 1 | 26477857.75 | 383983 | 2436167 | 9265109.75 | 14392598
Option 3 | Stage 1: syncons at Parkes | 2027 | 2027 | 2027 | 2027 | 40 | 1 | 80076544 | 3872150 | 21445629 | 53005115 | 1753650
Option 3 | Stage 2: line | 2032 | 2028 | #N/A | #N/A | 40 | 1 | 120732902 | 425105 | 869813 | 2920272 | 10749172 | 96140301 | 9628239
Option 4 | Stage 1: SVC at Panorama | 2027 | 2027 | 2027 | 2027 | 20 | 1 | 26477857.75 | 383983 | 2436167 | 9265109.75 | 14392598
Option 4 | Stage 1: syncons at Parkes | 2027 | 2027 | 2027 | 2027 | 40 | 1 | 80076544 | 3872150 | 21445629 | 53005115 | 1753650
Option 4 | Stage 2: line | 2032 | 2028 | #N/A | #N/A | 40 | 1 | 32145916.8154 | 369584.1317 | 911433.596 | 2531172.9888 | 13116120.4567 | 15217605.6421
Option 4 | Stage 2: substation (inc. the 2 TFs) | 2032 | 2028 | #N/A | #N/A | 40 | 1 | 90938043.1846 | 720424.5162 | 1910871.303 | 5679005.4949 | 31953027.13 | 50674714.7405
Option 4 | Stage 3: syncon | #N/A | 2028 | #N/A | #N/A | 40 | 1 | 27787669 | 1308499 | 7463880 | 18421057 | 594233
Option 5 | Stage 1: syncons | 2027 | 2027 | 2027 | 2027 | 40 | 1 |  | Redacted to preserve confidentiality
Option 5 | Stage 1: Panorama - 20MW/40MWh BESS | 2027 | 2027 | 2027 | 2027 | 15 | 1 |  | Redacted to preserve confidentiality
Option 5 | Stage 1: Parkes - 15MW/30MWh BESS | 2027 | 2027 | 2027 | 2027 | 15 | 1 |  | Redacted to preserve confidentiality
Option 5 | Stage 2: line | 2032 | 2028 | #N/A | #N/A | 40 | 1 |  | Redacted to preserve confidentiality
Option 6 | Stage 1: syncons | 2027 | 2027 | 2027 | 2027 | 40 | 1 |  | Redacted to preserve confidentiality
Option 6 | Stage 1: Panorama - 20MW/40MWh BESS | 2027 | 2027 | 2027 | 2027 | 15 | 1 |  | Redacted to preserve confidentiality
Option 6 | Stage 1: Parkes - 15MW/30MWh BESS | 2027 | 2027 | 2027 | 2027 | 15 | 1 |  | Redacted to preserve confidentiality
Option 6 | Stage 2: line | 2032 | 2028 | #N/A | #N/A | 40 | 1 |  | Redacted to preserve confidentiality
Option 6 | Stage 2: substation (inc. the 2 TFs) | 2032 | 2028 | #N/A | #N/A | 40 | 1 |  | Redacted to preserve confidentiality
Option 6 | Stage 3: syncon | #N/A | 2028 | #N/A | #N/A | 40 | 1 |  | Redacted to preserve confidentiality
Option 7A | Stage 1: Parkes BESS and PV | Redacted to preserve confidentiality |  |  |  |  | 0 |  | Redacted to preserve confidentiality
Option 7A | Stage 1: Panorama BESS | Redacted to preserve confidentiality |  |  |  |  | 0 |  | Redacted to preserve confidentiality
Option 7A | Stage 2: line (same as Option 3 stage 2) | 2032 | 2028 | #N/A | #N/A | 40 | 1 | 120732902 | 425105 | 869813 | 2920272 | 10749172 | 96140301 | 9628239
Option 7B | Stage 1: Parkes BESS and PV | Redacted to preserve confidentiality |  |  |  |  | 0 |  | Redacted to preserve confidentiality
Option 7B | Stage 1: Panorama BESS | Redacted to preserve confidentiality |  |  |  |  | 0 |  | Redacted to preserve confidentiality
Option 7B | Stage 2: line (same as Option 3 stage 2) | 2032 | 2028 | #N/A | #N/A | 40 | 1 | 120732902 | 425105 | 869813 | 2920272 | 10749172 | 96140301 | 9628239
Option 7C | Stage 1: Parkes BESS | Redacted to preserve confidentiality |  |  |  |  | 0 |  | Redacted to preserve confidentiality
Option 7C | Stage 1: Panorama BESS | Redacted to preserve confidentiality |  |  |  |  | 0 |  | Redacted to preserve confidentiality
Option 7C | Stage 2: line (same as Option 3 stage 2) | 2032 | 2028 | #N/A | #N/A | 40 | 1 | 120732902 | 425105 | 869813 | 2920272 | 10749172 | 96140301 | 9628239
Option 7D | Stage 1: Parkes BESS | Redacted to preserve confidentiality |  |  |  |  | 0 |  | Redacted to preserve confidentiality
Option 7D | Stage 1: Panorama BESS | Redacted to preserve confidentiality |  |  |  |  | 0 |  | Redacted to preserve confidentiality
Option 7D | Syncons | Redacted to preserve confidentiality |  |  |  |  | 0 |  | Redacted to preserve confidentiality
Option 7D | Stage 2: line (same as Option 3 stage 2) | 2032 | 2028 | #N/A | #N/A | 40 | 1 | 120732902 | 425105 | 869813 | 2920272 | 10749172 | 96140301 | 9628239
Biodiversity offset costs | Bio costs component
Option 1A/1B | Stage 1: line | 2028 | 2028 | 2028 | 2028 | 40 | 1 | 4180000 | 0 | 0 | 0 | 4180000 | 0
Option 1A/1B | Stage 1: substation (inc. the 2 TFs) | 2028 | 2028 | 2028 | 2028 | 40 | 1 | 9090000 | 0 | 0 | 0 | 9090000 | 0
Option 1C | Stage 2: line | 2028 | 2028 | 2036 | 2032 | 40 | 1 | 4180000 | 0 | 0 | 0 | 4180000 | 0
Option 1C | Stage 2: substation (inc. the 2 TFs) | 2028 | 2028 | 2036 | 2032 | 40 | 1 | 9090000 | 0 | 0 | 0 | 9090000 | 0
Option 4 | Stage 2: line | 2032 | 2028 | #N/A | #N/A | 40 | 1 | 4180000 | 0 | 0 | 0 | 4180000 | 0
Option 4 | Stage 2: substation (inc. the 2 TFs) | 2032 | 2028 | #N/A | #N/A | 40 | 1 | 9090000 | 0 | 0 | 0 | 9090000 | 0
Option 6 | Stage 2: line | 2032 | 2028 | #N/A | #N/A | 40 | 1 | 4180000 | 0 | 0 | 0 | 4180000 | 0
Option 6 | Stage 2: substation (inc. the 2 TFs) | 2032 | 2028 | #N/A | #N/A | 40 | 1 | 9090000 | 0 | 0 | 0 | 9090000 | 0
Property allowances | Property allowances component
Option 1A/1B | Stage 1: line | 2028 | 2028 | 2028 | 2028 | 40 | 1 | 23480000 | 0 | 0 | 0 | 23480000 | 0
Option 1A/1B | Stage 1: substation (inc. the 2 TFs) | 2028 | 2028 | 2028 | 2028 | 40 | 1 | 4422000 | 0 | 0 | 0 | 4422000 | 0
Option 1C | Stage 2: line | 2028 | 2028 | 2036 | 2032 | 40 | 1 | 23480000 | 0 | 0 | 0 | 23480000 | 0
Option 1C | Stage 2: substation (inc. the 2 TFs) | 2028 | 2028 | 2036 | 2032 | 40 | 1 | 4422000 | 0 | 0 | 0 | 4422000 | 0
Option 4 | Stage 2: line | 2032 | 2028 | #N/A | #N/A | 40 | 1 | 23480000 | 0 | 0 | 0 | 23480000 | 0
Option 4 | Stage 2: substation (inc. the 2 TFs) | 2032 | 2028 | #N/A | #N/A | 40 | 1 | 4422000 | 0 | 0 | 0 | 4422000 | 0
Option 6 | Stage 2: line | 2032 | 2028 | #N/A | #N/A | 40 | 1 | 23480000 | 0 | 0 | 0 | 23480000 | 0
Option 6 | Stage 2: substation (inc. the 2 TFs) | 2032 | 2028 | #N/A | #N/A | 40 | 1 | 4422000 | 0 | 0 | 0 | 4422000 | 0
Operating and maintenance costs
Option | Capex component | TNSP owned | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  | $
Option 1A/1B | Stage 1: line | 1 | $ | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363
Option 1A/1B | Stage 1: substation (inc. the 2 TFs) | 1 | $ | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637
Option 1A/1B | Stage 2: line | 1 | $ | 2455069.06 | 2455069.06 | 2455069.06 | 2455069.06 | 2455069.06 | 2455069.06 | 2455069.06 | 2455069.06 | 2455069.06 | 2455069.06 | 2455069.06 | 2455069.06 | 2455069.06 | 2455069.06 | 2455069.06 | 2455069.06 | 2455069.06 | 2455069.06 | 2455069.06 | 2455069.06
Option 1C | Stage 1: syncon | 1 | $ | 604003.24 | 604003.24 | 604003.24 | 604003.24 | 604003.24 | 604003.24 | 604003.24 | 604003.24 | 604003.24 | 604003.24 | 604003.24 | 604003.24 | 604003.24 | 604003.24 | 604003.24 | 604003.24 | 604003.24 | 604003.24 | 604003.24 | 604003.24
Option 1C | Stage 2: line | 1 | $ | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363
Option 1C | Stage 2: substation (inc. the 2 TFs) | 1 | $ | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637
Option 1C | Stage 3: syncon | 1 | $ | 521373.28 | 521373.28 | 521373.28 | 521373.28 | 521373.28 | 521373.28 | 521373.28 | 521373.28 | 521373.28 | 521373.28 | 521373.28 | 521373.28 | 521373.28 | 521373.28 | 521373.28 | 521373.28 | 521373.28 | 521373.28 | 521373.28 | 521373.28
Option 1C | Stage 4: 2 x syncons | 1 | $ | 1025127.74 | 1025127.74 | 1025127.74 | 1025127.74 | 1025127.74 | 1025127.74 | 1025127.74 | 1025127.74 | 1025127.74 | 1025127.74 | 1025127.74 | 1025127.74 | 1025127.74 | 1025127.74 | 1025127.74 | 1025127.74 | 1025127.74 | 1025127.74 | 1025127.74 | 1025127.74
Option 3 | Stage 1: SVC at Panorama | 1 | $ | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155
Option 3 | Stage 1: syncons at Parkes | 1 | $ | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88
Option 3 | Stage 2: line | 1 | $ | 2414658.04 | 2414658.04 | 2414658.04 | 2414658.04 | 2414658.04 | 2414658.04 | 2414658.04 | 2414658.04 | 2414658.04 | 2414658.04 | 2414658.04 | 2414658.04 | 2414658.04 | 2414658.04 | 2414658.04 | 2414658.04 | 2414658.04 | 2414658.04 | 2414658.04 | 2414658.04
Option 4 | Stage 1: SVC at Panorama | 1 | $ | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155 | 529557.155
Option 4 | Stage 1: syncons at Parkes | 1 | $ | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88 | 1601530.88
Option 4 | Stage 2: line | 1 | $ | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363 | 642918.3363
Option 4 | Stage 2: substation (inc. the 2 TFs) | 1 | $ | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637 | 1818760.8637
Option 4 | Stage 3: syncon | 1 | $ | 555753.38 | 555753.38 | 555753.38 | 555753.38 | 555753.38 | 555753.38 | 555753.38 | 555753.38 | 555753.38 | 555753.38 | 555753.38 | 555753.38 | 555753.38 | 555753.38 | 555753.38 | 555753.38 | 555753.38 | 555753.38 | 555753.38 | 555753.38
Option 5 | Stage 1: syncons | 1 | $ | Redacted to preserve confidentiality
Option 5 | Stage 1: Panorama - 20MW/40MWh BESS | 1 | $ | Redacted to preserve confidentiality
Option 5 | Stage 1: Parkes - 15MW/30MWh BESS | 1 | $ | Redacted to preserve confidentiality
Option 5 | Stage 2: line | 1 | $ | Redacted to preserve confidentiality
Option 6 | Stage 1: syncons | 1 | $ | Redacted to preserve confidentiality
Option 6 | Stage 1: Panorama - 20MW/40MWh BESS | 1 | $ | Redacted to preserve confidentiality
Option 6 | Stage 1: Parkes - 15MW/30MWh BESS | 1 | $ | Redacted to preserve confidentiality
Option 6 | Stage 2: line | 1 | $ | Redacted to preserve confidentiality
Option 6 | Stage 2: substation (inc. the 2 TFs) | 1 | $ | Redacted to preserve confidentiality
Option 6 | Stage 3: syncon | 1 | $ | Redacted to preserve confidentiality
Option 7A | Stage 1: Parkes BESS and PV | 0 | $ | Redacted to preserve confidentiality
Option 7A | Stage 1: Panorama BESS | 0 | $ | Redacted to preserve confidentiality
Option 7A | Stage 2: line | 1 | $ | Redacted to preserve confidentiality
Option 7B | Stage 1: Parkes BESS and PV | 0 | $ | Redacted to preserve confidentiality
Option 7B | Stage 1: Panorama BESS | 0 | $ | Redacted to preserve confidentiality
Option 7B | Stage 2: line | 1 | $ | Redacted to preserve confidentiality
Option 7C | Stage 1: Parkes BESS | 0 | $ | Redacted to preserve confidentiality
Option 7C | Stage 1: Panorama BESS | 0 | $ | Redacted to preserve confidentiality
Option 7C | Stage 2: line | 1 | $ | Redacted to preserve confidentiality
Option 7D | Stage 1: Parkes BESS | 0 | $ | Redacted to preserve confidentiality
Option 7D | Stage 1: Panorama BESS | 0 | $ | Redacted to preserve confidentiality
Option 7D | Syncons | 0 | $ | Redacted to preserve confidentiality
Option 7D | Stage 2: line | 1 | $ | Redacted to preserve confidentiality
TSNP network service payments to NNO proponents
Option |  |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  | $
Option 1A/1B |  |  | $
Option 1C |  |  | $
Option 3 |  |  | $
Option 4 |  |  | $
Option 5 |  |  | $
Option 6 |  |  | $
Option 7A |  |  | $ | Redacted to preserve confidentiality
Option 7B |  |  | $ | Redacted to preserve confidentiality
Option 7C |  |  | $ | Redacted to preserve confidentiality
Option 7D |  |  | $ | Redacted to preserve confidentiality
NNO proponent receipts from TSNP
Option |  |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  | $
Option 1A/1B |  |  | $
Option 1C |  |  | $
Option 3 |  |  | $
Option 4 |  |  | $
Option 5 |  |  | $
Option 6 |  |  | $
Option 7A |  |  | $ | Redacted to preserve confidentiality
Option 7B |  |  | $ | Redacted to preserve confidentiality
Option 7C |  |  | $ | Redacted to preserve confidentiality
Option 7D |  |  | $ | Redacted to preserve confidentiality
CBA benefit inputs
Avoided fuel consumption from generation dispatch
Option name |  |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  | $
Option 1A/1B |  |  | $
Option 1C |  |  | $
Option 3 |  |  | $
Option 4 |  |  | $
Option 5 |  |  | $ | Redacted to preserve confidentiality
Option 6 |  |  | $ | Redacted to preserve confidentiality
Option 7A |  |  | $ | Redacted to preserve confidentiality
Option 7B |  |  | $ | Redacted to preserve confidentiality
Option 7C |  |  | $ | Redacted to preserve confidentiality
Option 7D |  |  | $ | Redacted to preserve confidentiality
Avoided voluntary load curtailment
Option name |  |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  | $
Option 1A/1B |  |  | $
Option 1C |  |  | $
Option 3 |  |  | $
Option 4 |  |  | $
Option 5 |  |  | $ | Redacted to preserve confidentiality
Option 6 |  |  | $ | Redacted to preserve confidentiality
Option 7A |  |  | $ | Redacted to preserve confidentiality
Option 7B |  |  | $ | Redacted to preserve confidentiality
Option 7C |  |  | $ | Redacted to preserve confidentiality
Option 7D |  |  | $ | Redacted to preserve confidentiality
Avoided involuntary load shedding - outside of CW NSW
Option name |  |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  | $
Option 1A/1B |  |  | $
Option 1C |  |  | $
Option 3 |  |  | $
Option 4 |  |  | $
Option 5 |  |  | $ | Redacted to preserve confidentiality
Option 6 |  |  | $ | Redacted to preserve confidentiality
Option 7A |  |  | $ | Redacted to preserve confidentiality
Option 7B |  |  | $ | Redacted to preserve confidentiality
Option 7C |  |  | $ | Redacted to preserve confidentiality
Option 7D |  |  | $ | Redacted to preserve confidentiality
Avoided involuntary load shedding in CW NSW - estimated by Transgrid
Option name |  | Central | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  | MWh | 0 | 0 | 8.7361 | 9314.5445 | 40909.3467 | 37156.0952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1A/1B |  |  | MWh | 0 | 0 | 8.7361 | 9314.5445 | 40909.3467 | 37156.0952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | MWh | 0 | 0 | 8.7361 | 9314.5445 | 40909.3467 | 116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | MWh | 0 | 0 | 8.7361 | 9314.5445 | 40909.3467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | MWh | 0 | 0 | 8.7361 | 9314.5445 | 40909.3467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | MWh | Redacted to preserve confidentiality
Option 6 |  |  | MWh | Redacted to preserve confidentiality
Option 7A |  |  | MWh | Redacted to preserve confidentiality
Option 7B |  |  | MWh | Redacted to preserve confidentiality
Option 7C |  |  | MWh | Redacted to preserve confidentiality
Option 7D |  |  | MWh | Redacted to preserve confidentiality
Option name |  | High | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  | MWh | 0 | 12.4367 | 274.716 | 16184.002 | 62089.9572 | 56637.6725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1A/1B |  |  | MWh | 0 | 12.4367 | 274.716 | 16184.002 | 62089.9572 | 56637.6725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | MWh | 0 | 12.4367 | 274.716 | 16184.002 | 62089.9572 | 4723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | MWh | 0 | 12.4367 | 274.716 | 16184.002 | 62089.9572 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | MWh | 0 | 12.4367 | 274.716 | 16184.002 | 62089.9572 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | MWh | Redacted to preserve confidentiality
Option 6 |  |  | MWh | Redacted to preserve confidentiality
Option 7A |  |  | MWh | Redacted to preserve confidentiality
Option 7B |  |  | MWh | Redacted to preserve confidentiality
Option 7C |  |  | MWh | Redacted to preserve confidentiality
Option 7D |  |  | MWh | Redacted to preserve confidentiality
Option name |  | Low | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  | MWh | 0 | 0 | 0 | 0 | 34.1203 | 79.1693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1A/1B |  |  | MWh | 0 | 0 | 0 | 0 | 34.1203 | 79.1693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | MWh | 0 | 0 | 0 | 0 | 34.1203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | MWh | 0 | 0 | 0 | 0 | 34.1203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | MWh | 0 | 0 | 0 | 0 | 34.1203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | MWh | Redacted to preserve confidentiality
Option 6 |  |  | MWh | Redacted to preserve confidentiality
Option 7A |  |  | MWh | Redacted to preserve confidentiality
Option 7B |  |  | MWh | Redacted to preserve confidentiality
Option 7C |  |  | MWh | Redacted to preserve confidentiality
Option 7D |  |  | MWh | Redacted to preserve confidentiality
Avoided costs for non RIT-T proponent parties
Option name |  |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  | $
Option 1A/1B |  |  | $
Option 1C |  |  | $
Option 3 |  |  | $
Option 4 |  |  | $
Option 5 |  |  | $ | Redacted to preserve confidentiality
Option 6 |  |  | $ | Redacted to preserve confidentiality
Option 7A |  |  | $ | Redacted to preserve confidentiality
Option 7B |  |  | $ | Redacted to preserve confidentiality
Option 7C |  |  | $ | Redacted to preserve confidentiality
Option 7D |  |  | $ | Redacted to preserve confidentiality
Option name |  |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 1A/1B |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 1C |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 3 |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 4 |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 5 |  |  | $ |  | 646310733.1939 | 2233731892.7715 | 3642378135.6984 | 5248694033.4415 | 5198508424.0997 | 7582256393.8497 | 7822469003.6884 | 5184428599.4783 | 1794407344.59 | 1268421452.383 | 4441137426.686 | 6466973175.2445 | 4057419028.7535 | 13553339978.2 | 6911708223.0189 | 12489440876.0351 | 3206083274.6963 | 1465117118.895 | 2561552162.5281
Option 6 |  |  | $ |  | 646310733.1939 | 2233731892.7715 | 3642378135.6984 | 5248694033.4415 | 5198508424.0997 | 7582256393.8497 | 7822469003.6884 | 5184428599.4783 | 1794407344.59 | 1268421452.383 | 4441137426.686 | 6466973175.2445 | 4057419028.7535 | 13553339978.2 | 6911708223.0189 | 12489440876.0351 | 3206083274.6963 | 1465117118.895 | 2561552162.5281
Option 7A |  |  | $ |  | 646315174.6837 | 2227838534.1271 | 3653253287.1001 | 5211525971.4781 | 5239425490.1961 | 7542142363.2048 | 7931017559.4333 | 5190651997.4935 | 1805290446.0303 | 1184595138.1697 | 4382862400.3482 | 6424666574.0218 | 4026058695.0939 | 13559586146.9312 | 6917042624.996 | 12486439408.677 | 3211735376.1999 | 1463004612.8431 | 2554084915.0284
Option 7B |  |  | $ |  | 646324972.6196 | 2226085555.9836 | 3655314848.6101 | 5199890430.984 | 5259377272.2133 | 7520347413.7799 | 7962759404.0722 | 5191901758.2027 | 1812010246.0013 | 1172601449.7974 | 4321584163.3856 | 6267082250.1503 | 4113524052.6887 | 13584385632.5232 | 6897529691.1933 | 12488525864.2326 | 3213710158.9292 | 1475996553.5131 | 2543657690.8315
Option 7C |  |  | $ |  | 646317282.2776 | 2233746496.7215 | 3649681628.3133 | 5154049810.6877 | 5233970375.0809 | 7557223142.1279 | 7789728654.8783 | 5136583035.2172 | 1814408351.62 | 1348115599.5454 | 4152143944.4081 | 6443949352.4859 | 4055529935.7322 | 13611420875.1733 | 6904145128.784 | 12488349743.5459 | 3216633279.291 | 1464493004.4719 | 2563466085.5817
Option 7D |  |  | $ |  | 646308150.9936 | 2230075269.164 | 3651179967.6171 | 5227713431.0389 | 5208245596.6576 | 7578412590.1121 | 7846607514.6232 | 5192479003.8453 | 1794824571.1968 | 1245169294.612 | 4441583303.6045 | 6468457446.8785 | 4054941834.0415 | 13553723255.4272 | 6911413126.1245 | 12490128504.9818 | 3206378452.4157 | 1465079912.5599 | 2561633506.5041
Option name |  |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 1A/1B |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 1C |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 3 |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 4 |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 5 |  |  | $ |  | 646310733.1939 | 2233731892.7715 | 3642378135.6984 | 5248694033.4415 | 5198508424.0997 | 7582256393.8497 | 7822469003.6884 | 5184428599.4783 | 1794407344.59 | 1268421452.383 | 4441137426.686 | 6466973175.2445 | 4057419028.7535 | 13553339978.2 | 6911708223.0189 | 12489440876.0351 | 3206083274.6963 | 1465117118.895 | 2561552162.5281
Option 6 |  |  | $ |  | 646310733.1939 | 2233731892.7715 | 3642378135.6984 | 5248694033.4415 | 5198508424.0997 | 7582256393.8497 | 7822469003.6884 | 5184428599.4783 | 1794407344.59 | 1268421452.383 | 4441137426.686 | 6466973175.2445 | 4057419028.7535 | 13553339978.2 | 6911708223.0189 | 12489440876.0351 | 3206083274.6963 | 1465117118.895 | 2561552162.5281
Option 7A |  |  | $ |  | 646315174.6837 | 2227838534.1271 | 3653253287.1001 | 5211525971.4781 | 5239425490.1961 | 7542142363.2048 | 7931017559.4333 | 5190651997.4935 | 1805290446.0303 | 1184595138.1697 | 4382862400.3482 | 6424666574.0218 | 4026058695.0939 | 13559586146.9312 | 6917042624.996 | 12486439408.677 | 3211735376.1999 | 1463004612.8431 | 2554084915.0284
Option 7B |  |  | $ |  | 646324972.6196 | 2226085555.9836 | 3655314848.6101 | 5199890430.984 | 5259377272.2133 | 7520347413.7799 | 7962759404.0722 | 5191901758.2027 | 1812010246.0013 | 1172601449.7974 | 4321584163.3856 | 6267082250.1503 | 4113524052.6887 | 13584385632.5232 | 6897529691.1933 | 12488525864.2326 | 3213710158.9292 | 1475996553.5131 | 2543657690.8315
Option 7C |  |  | $ |  | 646317282.2776 | 2233746496.7215 | 3649681628.3133 | 5154049810.6877 | 5233970375.0809 | 7557223142.1279 | 7789728654.8783 | 5136583035.2172 | 1814408351.62 | 1348115599.5454 | 4152143944.4081 | 6443949352.4859 | 4055529935.7322 | 13611420875.1733 | 6904145128.784 | 12488349743.5459 | 3216633279.291 | 1464493004.4719 | 2563466085.5817
Option 7D |  |  | $ |  | 646308150.9936 | 2230075269.164 | 3651179967.6171 | 5227713431.0389 | 5208245596.6576 | 7578412590.1121 | 7846607514.6232 | 5192479003.8453 | 1794824571.1968 | 1245169294.612 | 4441583303.6045 | 6468457446.8785 | 4054941834.0415 | 13553723255.4272 | 6911413126.1245 | 12490128504.9818 | 3206378452.4157 | 1465079912.5599 | 2561633506.5041
Option name |  |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 1A/1B |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 1C |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 3 |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 4 |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 5 |  |  | $ |  | 646310733.1939 | 2233731892.7715 | 3642378135.6984 | 5248694033.4415 | 5198508424.0997 | 7582256393.8497 | 7822469003.6884 | 5184428599.4783 | 1794407344.59 | 1268421452.383 | 4441137426.686 | 6466973175.2445 | 4057419028.7535 | 13553339978.2 | 6911708223.0189 | 12489440876.0351 | 3206083274.6963 | 1465117118.895 | 2561552162.5281
Option 6 |  |  | $ |  | 646310733.1939 | 2233731892.7715 | 3642378135.6984 | 5248694033.4415 | 5198508424.0997 | 7582256393.8497 | 7822469003.6884 | 5184428599.4783 | 1794407344.59 | 1268421452.383 | 4441137426.686 | 6466973175.2445 | 4057419028.7535 | 13553339978.2 | 6911708223.0189 | 12489440876.0351 | 3206083274.6963 | 1465117118.895 | 2561552162.5281
Option 7A |  |  | $ |  | 646315174.6837 | 2227838534.1271 | 3653253287.1001 | 5211525971.4781 | 5239425490.1961 | 7542142363.2048 | 7931017559.4333 | 5190651997.4935 | 1805290446.0303 | 1184595138.1697 | 4382862400.3482 | 6424666574.0218 | 4026058695.0939 | 13559586146.9312 | 6917042624.996 | 12486439408.677 | 3211735376.1999 | 1463004612.8431 | 2554084915.0284
Option 7B |  |  | $ |  | 646324972.6196 | 2226085555.9836 | 3655314848.6101 | 5199890430.984 | 5259377272.2133 | 7520347413.7799 | 7962759404.0722 | 5191901758.2027 | 1812010246.0013 | 1172601449.7974 | 4321584163.3856 | 6267082250.1503 | 4113524052.6887 | 13584385632.5232 | 6897529691.1933 | 12488525864.2326 | 3213710158.9292 | 1475996553.5131 | 2543657690.8315
Option 7C |  |  | $ |  | 646317282.2776 | 2233746496.7215 | 3649681628.3133 | 5154049810.6877 | 5233970375.0809 | 7557223142.1279 | 7789728654.8783 | 5136583035.2172 | 1814408351.62 | 1348115599.5454 | 4152143944.4081 | 6443949352.4859 | 4055529935.7322 | 13611420875.1733 | 6904145128.784 | 12488349743.5459 | 3216633279.291 | 1464493004.4719 | 2563466085.5817
Option 7D |  |  | $ |  | 646308150.9936 | 2230075269.164 | 3651179967.6171 | 5227713431.0389 | 5208245596.6576 | 7578412590.1121 | 7846607514.6232 | 5192479003.8453 | 1794824571.1968 | 1245169294.612 | 4441583303.6045 | 6468457446.8785 | 4054941834.0415 | 13553723255.4272 | 6911413126.1245 | 12490128504.9818 | 3206378452.4157 | 1465079912.5599 | 2561633506.5041
Avoided unrelated TNSP expenditure
Option name |  |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  | $
Option 1A/1B |  |  | $
Option 1C |  |  | $
Option 3 |  |  | $
Option 4 |  |  | $
Option 5 |  |  | $ | Redacted to preserve confidentiality
Option 6 |  |  | $ | Redacted to preserve confidentiality
Option 7A |  |  | $ | Redacted to preserve confidentiality
Option 7B |  |  | $ | Redacted to preserve confidentiality
Option 7C |  |  | $ | Redacted to preserve confidentiality
Option 7D |  |  | $ | Redacted to preserve confidentiality
Full unserved energy inputs under core assumptions (ie, not zeroed out after 2026/27, as outlined in section 6.1 of the PADR)
Option name |  | Central | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  | MWh | 0 | 0 | 8.7361 | 9314.5445 | 40909.3467 | 37156.0952 | 59354.7145 | 50758.249 | 55581.6952 | 60517.1627 | 65826.4554 | 68771.5264 | 71767.3258 | 73672.6425 | 69211.7247 | 62839.16 | 66724.5128 | 71689.6031 | 76879.5236 | 82177.7666
Option 1A/1B |  |  | MWh | 0 | 0 | 8.7361 | 9314.5445 | 40909.3467 | 37156.0952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | MWh | 0 | 0 | 8.7361 | 9314.5445 | 40909.3467 | 116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | MWh | 0 | 0 | 8.7361 | 9314.5445 | 40909.3467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | MWh | 0 | 0 | 8.7361 | 9314.5445 | 40909.3467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | MWh | Redacted to preserve confidentiality
Option 6 |  |  | MWh | Redacted to preserve confidentiality
Option 7A |  |  | MWh | Redacted to preserve confidentiality
Option 7B |  |  | MWh | Redacted to preserve confidentiality
Option 7C |  |  | MWh | Redacted to preserve confidentiality
Option 7D |  |  | MWh | Redacted to preserve confidentiality
Option name |  | High | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  | MWh | 0 | 12.4367 | 274.716 | 16184.002 | 62089.9572 | 56637.6725 | 92666.5476 | 87367.2651 | 103787.9749 | 122730.0398 | 145532.9587 | 156420.5419 | 160268.9704 | 154643.154 | 145516.2588 | 134575.9439 | 135484.5757 | 140851.1972 | 146345.8314 | 154692.4537
Option 1A/1B |  |  | MWh | 0 | 12.4367 | 274.716 | 16184.002 | 62089.9572 | 56637.6725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | MWh | 0 | 12.4367 | 274.716 | 16184.002 | 62089.9572 | 4723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | MWh | 0 | 12.4367 | 274.716 | 16184.002 | 62089.9572 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | MWh | 0 | 12.4367 | 274.716 | 16184.002 | 62089.9572 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | MWh | Redacted to preserve confidentiality
Option 6 |  |  | MWh | Redacted to preserve confidentiality
Option 7A |  |  | MWh | Redacted to preserve confidentiality
Option 7B |  |  | MWh | Redacted to preserve confidentiality
Option 7C |  |  | MWh | Redacted to preserve confidentiality
Option 7D |  |  | MWh | Redacted to preserve confidentiality
Option name |  | Low | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  | MWh | 0 | 0 | 0 | 0 | 34.1203 | 79.1693 | 79.6155 | 80.7145 | 115.9393 | 117.8456 | 166.4317 | 175.4858 | 242.2356 | 243.7262 | 328.711 | 347.5182 | 453.5363 | 583.6226 | 902.9605 | 1352.3171
Option 1A/1B |  |  | MWh | 0 | 0 | 0 | 0 | 34.1203 | 79.1693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | MWh | 0 | 0 | 0 | 0 | 34.1203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | MWh | 0 | 0 | 0 | 0 | 34.1203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | MWh | 0 | 0 | 0 | 0 | 34.1203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | MWh | Redacted to preserve confidentiality
Option 6 |  |  | MWh | Redacted to preserve confidentiality
Option 7A |  |  | MWh | Redacted to preserve confidentiality
Option 7B |  |  | MWh | Redacted to preserve confidentiality
Option 7C |  |  | MWh | Redacted to preserve confidentiality
Option 7D |  |  | MWh | Redacted to preserve confidentiality

## Central
Central
NPV results
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | -186937843.819 | 0 | -500490 | -2058381.6479 | -6027412.899 | -20013010.4837 | -182863409.5867 | -80463456.6426 | -4916748.26 | -4916748.26 | -4916748.26 | -4916748.26 | -4916748.26 | -4916748.26 | -4916748.26 | -4916748.26 | -4916748.26 | -4916748.26 | -4916748.26 | -4916748.26 | 181639370.19
Option 1C |  |  | $ | 1377853243.992 | 0 | 0 | -2543884.6479 | -10914368.899 | -28205657.4837 | 1893548556.0784 | -68958002.8226 | -4301765.44 | -10062507.44 | -20340496.44 | -4147997.72 | -3587055.72 | -3587055.72 | -3587055.72 | -3587055.72 | -3587055.72 | -3587055.72 | -3587055.72 | -3587055.72 | 141605917.53
Option 3 |  |  | $ | 1383475295.1889 | 0 | 0 | -4256133 | -23881796 | -62270224.75 | 1968554152.8701 | -3000901.035 | -5051360.035 | -12880260.035 | -98271389.035 | -14173985.075 | -4545746.075 | -4545746.075 | -4545746.075 | -4545746.075 | -4545746.075 | -4545746.075 | -4545746.075 | -4545746.075 | 142671234.8625
Option 4 |  |  | $ | 1370121770.8279 | 0 | 0 | -4256133 | -23881796 | -62270224.75 | 1968979257.8701 | -3221096.6829 | -4953392.934 | -10341266.5187 | -88372235.6217 | -70485087.6176 | -4592767.235 | -4592767.235 | -4592767.235 | -4592767.235 | -4592767.235 | -4592767.235 | -4592767.235 | -4592767.235 | 175266507.2025
Option 5 |  |  | $ | 1355485872.6775 | Redacted to preserve confidentiality
Option 6 |  |  | $ | 1342132348.3166 | Redacted to preserve confidentiality
Option 7A |  |  | $ | 3528240924.5478 | Redacted to preserve confidentiality
Option 7B |  |  | $ | 3545172443.393 | Redacted to preserve confidentiality
Option 7C |  |  | $ | 3518739199.2363 | Redacted to preserve confidentiality
Option 7D |  |  | $ | 3625460592.3657 | Redacted to preserve confidentiality
Capital cost calculation
Option | Components | TNSP | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B | Stage 1: line | 1 | $ | -16668409.035 | 0 | 0 | -369584.1317 | -911433.596 | -2531172.9888 | -13116120.4567 | -15217605.6421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20894845.93
Option 1A/1B | Stage 1: substation (inc. the 2 TFs) | 1 | $ | -46685924.3571 | 0 | 0 | -720424.5162 | -1910871.303 | -5679005.4949 | -31953027.13 | -50674714.7405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59109728.07
Option 1A/1B | Stage 2: line | 1 | $ | -65681908.71 | 0 | -500490 | -968373 | -3205108 | -11802832 | -96622262 | -9654388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79789744.45
Option 1C | Stage 1: syncon | 1 | $ | -18017421.7192 | 0 | 0 | -1453876 | -8092064 | -19995479 | -658743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18875101.25
Option 1C | Stage 2: line | 1 | $ | -16668409.035 | 0 | 0 | -369584.1317 | -911433.596 | -2531172.9888 | -13116120.4567 | -15217605.6421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20894845.93
Option 1C | Stage 2: substation (inc. the 2 TFs) | 1 | $ | -46685924.3571 | 0 | 0 | -720424.5162 | -1910871.303 | -5679005.4949 | -31953027.13 | -50674714.7405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59109728.07
Option 1C | Stage 3: syncon | 1 | $ | -9337263.2345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1236083 | -6996825 | -17274814 | -560942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19551498
Option 1C | Stage 4: 2 x syncons | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Stage 1: SVC at Panorama | 1 | $ | -18517426.7443 | 0 | 0 | -383983 | -2436167 | -9265109.75 | -14392598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6619464.4375
Option 3 | Stage 1: syncons at Parkes | 1 | $ | -47774476.6255 | 0 | 0 | -3872150 | -21445629 | -53005115 | -1753650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50047840
Option 3 | Stage 2: line | 1 | $ | -42242603.5387 | 0 | 0 | 0 | 0 | 0 | -425105 | -869813 | -2920272 | -10749172 | -96140301 | -9628239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90549676.5
Option 4 | Stage 1: SVC at Panorama | 1 | $ | -18517426.7443 | 0 | 0 | -383983 | -2436167 | -9265109.75 | -14392598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6619464.4375
Option 4 | Stage 1: syncons at Parkes | 1 | $ | -47774476.6255 | 0 | 0 | -3872150 | -21445629 | -53005115 | -1753650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50047840
Option 4 | Stage 2: line | 1 | $ | -10836185.5924 | 0 | 0 | 0 | 0 | 0 | 0 | -369584.1317 | -911433.596 | -2531172.9888 | -13116120.4567 | -15217605.6421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24109437.6115
Option 4 | Stage 2: substation (inc. the 2 TFs) | 1 | $ | -30277204.9926 | 0 | 0 | 0 | 0 | 0 | 0 | -720424.5162 | -1910871.303 | -5679005.4949 | -31953027.13 | -50674714.7405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68203532.3885
Option 4 | Stage 3: syncon | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Stage 1: syncons | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Stage 1: Panorama - 20MW/40MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Stage 1: Parkes - 15MW/30MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Reinvestment: Panorama - 20MW/40MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Reinvestment: Parkes - 15MW/30MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 1: syncons | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 1: Panorama - 20MW/40MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 1: Parkes - 15MW/30MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Reinvestment: Panorama - 20MW/40MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Reinvestment: Parkes - 15MW/30MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 2: substation (inc. the 2 TFs) | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 3: syncon | 1 | $ |  | Redacted to preserve confidentiality
Option 7A | Stage 1: Parkes BESS and PV | 0 | $ |  | Redacted to preserve confidentiality
Option 7A | Stage 1: Panorama BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7A | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 7B | Stage 1: Parkes BESS and PV | 0 | $ |  | Redacted to preserve confidentiality
Option 7B | Stage 1: Panorama BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7B | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 7C | Stage 1: Parkes BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7C | Stage 1: Panorama BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7C | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 7D | Stage 1: Parkes BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7D | Stage 1: Panorama BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7D | Syncons | 0 | $ |  | Redacted to preserve confidentiality
Option 7D | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Biodiversity offset costs | Bio costs component
Option 1A/1B | Stage 1: line | 1 | $ | -2215851.3031 | 0 | 0 | 0 | 0 | 0 | -4180000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2717000
Option 1A/1B | Stage 1: substation (inc. the 2 TFs) | 1 | $ | -4818681.4222 | 0 | 0 | 0 | 0 | 0 | -9090000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5908500
Option 1C | Stage 2: line | 1 | $ | -2215851.3031 | 0 | 0 | 0 | 0 | 0 | -4180000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2717000
Option 1C | Stage 2: substation (inc. the 2 TFs) | 1 | $ | -4818681.4222 | 0 | 0 | 0 | 0 | 0 | -9090000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5908500
Option 4 | Stage 2: line | 1 | $ | -1448139.9707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4180000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3135000
Option 4 | Stage 2: substation (inc. the 2 TFs) | 1 | $ | -3149184.7688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9090000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6817500
Option 6 | Stage 2: line | 1 | $ | -1448139.9707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4180000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3135000
Option 6 | Stage 2: substation (inc. the 2 TFs) | 1 | $ | -3149184.7688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9090000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6817500
Property allowances | Property allowances component
Option 1A/1B | Stage 1: line | 1 | $ | -12446935.0708 | 0 | 0 | 0 | 0 | 0 | -23480000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15262000
Option 1A/1B | Stage 1: substation (inc. the 2 TFs) | 1 | $ | -2344137.4311 | 0 | 0 | 0 | 0 | 0 | -4422000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2874300
Option 1C | Stage 2: line | 1 | $ | -12446935.0708 | 0 | 0 | 0 | 0 | 0 | -23480000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15262000
Option 1C | Stage 2: substation (inc. the 2 TFs) | 1 | $ | -2344137.4311 | 0 | 0 | 0 | 0 | 0 | -4422000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2874300
Option 4 | Stage 2: line | 1 | $ | -8134527.8736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -23480000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17610000
Option 4 | Stage 2: substation (inc. the 2 TFs) | 1 | $ | -1531979.6532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4422000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3316500
Option 6 | Stage 2: line | 1 | $ | -8134527.8736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -23480000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17610000
Option 6 | Stage 2: substation (inc. the 2 TFs) | 1 | $ | -1531979.6532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4422000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3316500
TNSP capital costs
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | -150861847.3292 | 0 | -500490 | -2058381.6479 | -6027412.899 | -20013010.4837 | -182863409.5867 | -75546708.3826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186556118.45
Option 1C |  |  | $ | -112534623.573 | 0 | 0 | -2543884.6479 | -10914368.899 | -28205657.4837 | -86899890.5867 | -65892320.3826 | -1236083 | -6996825 | -17274814 | -560942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145192973.25
Option 3 |  |  | $ | -108534506.9085 | 0 | 0 | -4256133 | -23881796 | -62270224.75 | -16571353 | -869813 | -2920272 | -10749172 | -96140301 | -9628239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147216980.9375
Option 4 |  |  | $ | -121669126.2212 | 0 | 0 | -4256133 | -23881796 | -62270224.75 | -16146248 | -1090008.6479 | -2822304.899 | -8210178.4837 | -86241147.5867 | -65892320.3826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179859274.4375
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
NNO capital costs
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
Operating cost calculation
Option | Components | TNSP | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B | Stage 1: line | 1 | $ | -4717329.0999 | 0 | 0 | 0 | 0 | 0 | 0 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363
Option 1A/1B | Stage 1: substation (inc. the 2 TFs) | 1 | $ | -13344919.6633 | 0 | 0 | 0 | 0 | 0 | 0 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637
Option 1A/1B | Stage 2: line | 1 | $ | -18013747.7266 | 0 | 0 | 0 | 0 | 0 | 0 | -2455069.06 | -2455069.06 | -2455069.06 | -2455069.06 | -2455069.06 | -2455069.06 | -2455069.06 | -2455069.06 | -2455069.06 | -2455069.06 | -2455069.06 | -2455069.06 | -2455069.06 | -2455069.06
Option 1C | Stage 1: syncon | 1 | $ | -4893938.3056 | 0 | 0 | 0 | 0 | 0 | -604003.24 | -604003.24 | -604003.24 | -604003.24 | -604003.24 | -604003.24 | -604003.24 | -604003.24 | -604003.24 | -604003.24 | -604003.24 | -604003.24 | -604003.24 | -604003.24 | -604003.24
Option 1C | Stage 2: line | 1 | $ | -4717329.0999 | 0 | 0 | 0 | 0 | 0 | 0 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363
Option 1C | Stage 2: substation (inc. the 2 TFs) | 1 | $ | -13344919.6633 | 0 | 0 | 0 | 0 | 0 | 0 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637
Option 1C | Stage 3: syncon | 1 | $ | -2427231.5494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -521373.28 | -521373.28 | -521373.28 | -521373.28 | -521373.28 | -521373.28 | -521373.28 | -521373.28 | -521373.28 | -521373.28
Option 1C | Stage 4: 2 x syncons | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Stage 1: SVC at Panorama | 1 | $ | -4290738.6488 | 0 | 0 | 0 | 0 | 0 | -529557.155 | -529557.155 | -529557.155 | -529557.155 | -529557.155 | -529557.155 | -529557.155 | -529557.155 | -529557.155 | -529557.155 | -529557.155 | -529557.155 | -529557.155 | -529557.155 | -529557.155
Option 3 | Stage 1: syncons at Parkes | 1 | $ | -12976409.4001 | 0 | 0 | 0 | 0 | 0 | -1601530.88 | -1601530.88 | -1601530.88 | -1601530.88 | -1601530.88 | -1601530.88 | -1601530.88 | -1601530.88 | -1601530.88 | -1601530.88 | -1601530.88 | -1601530.88 | -1601530.88 | -1601530.88 | -1601530.88
Option 3 | Stage 2: line | 1 | $ | -11241339.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2414658.04 | -2414658.04 | -2414658.04 | -2414658.04 | -2414658.04 | -2414658.04 | -2414658.04 | -2414658.04 | -2414658.04 | -2414658.04
Option 4 | Stage 1: SVC at Panorama | 1 | $ | -4290738.6488 | 0 | 0 | 0 | 0 | 0 | -529557.155 | -529557.155 | -529557.155 | -529557.155 | -529557.155 | -529557.155 | -529557.155 | -529557.155 | -529557.155 | -529557.155 | -529557.155 | -529557.155 | -529557.155 | -529557.155 | -529557.155
Option 4 | Stage 1: syncons at Parkes | 1 | $ | -12976409.4001 | 0 | 0 | 0 | 0 | 0 | -1601530.88 | -1601530.88 | -1601530.88 | -1601530.88 | -1601530.88 | -1601530.88 | -1601530.88 | -1601530.88 | -1601530.88 | -1601530.88 | -1601530.88 | -1601530.88 | -1601530.88 | -1601530.88 | -1601530.88
Option 4 | Stage 2: line | 1 | $ | -2993079.4873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363 | -642918.3363
Option 4 | Stage 2: substation (inc. the 2 TFs) | 1 | $ | -8467165.3085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637 | -1818760.8637
Option 4 | Stage 3: syncon | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Stage 1: syncons | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Stage 1: Panorama - 20MW/40MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Stage 1: Parkes - 15MW/30MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Reinvestment: Panorama - 20MW/40MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Reinvestment: Parkes - 15MW/30MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 1: syncons | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 1: Panorama - 20MW/40MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 1: Parkes - 15MW/30MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Reinvestment: Panorama - 20MW/40MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Reinvestment: Parkes - 15MW/30MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 2: substation (inc. the 2 TFs) | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 3: syncon | 1 | $ |  | Redacted to preserve confidentiality
Option 7A | Stage 1: Parkes BESS and PV | 0 | $ |  | Redacted to preserve confidentiality
Option 7A | Stage 1: Panorama BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7A | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 7B | Stage 1: Parkes BESS and PV | 0 | $ |  | Redacted to preserve confidentiality
Option 7B | Stage 1: Panorama BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7B | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 7C | Stage 1: Parkes BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7C | Stage 1: Panorama BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7C | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 7D | Stage 1: Parkes BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7D | Stage 1: Panorama BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7D | Syncons | 0 | $ |  | Redacted to preserve confidentiality
Option 7D | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
TNSP operating expenditure
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | -36075996.4898 | 0 | 0 | 0 | 0 | 0 | 0 | -4916748.26 | -4916748.26 | -4916748.26 | -4916748.26 | -4916748.26 | -4916748.26 | -4916748.26 | -4916748.26 | -4916748.26 | -4916748.26 | -4916748.26 | -4916748.26 | -4916748.26 | -4916748.26
Option 1C |  |  | $ | -25383418.6182 | 0 | 0 | 0 | 0 | 0 | -604003.24 | -3065682.44 | -3065682.44 | -3065682.44 | -3065682.44 | -3587055.72 | -3587055.72 | -3587055.72 | -3587055.72 | -3587055.72 | -3587055.72 | -3587055.72 | -3587055.72 | -3587055.72 | -3587055.72
Option 3 |  |  | $ | -28508487.7963 | 0 | 0 | 0 | 0 | 0 | -2131088.035 | -2131088.035 | -2131088.035 | -2131088.035 | -2131088.035 | -4545746.075 | -4545746.075 | -4545746.075 | -4545746.075 | -4545746.075 | -4545746.075 | -4545746.075 | -4545746.075 | -4545746.075 | -4545746.075
Option 4 |  |  | $ | -28727392.8446 | 0 | 0 | 0 | 0 | 0 | -2131088.035 | -2131088.035 | -2131088.035 | -2131088.035 | -2131088.035 | -4592767.235 | -4592767.235 | -4592767.235 | -4592767.235 | -4592767.235 | -4592767.235 | -4592767.235 | -4592767.235 | -4592767.235 | -4592767.235
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
TNSP NNO operating expenditure
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
NNO operating expenditure
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
Avoided fuel consumption from generation dispatch
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
Avoided voluntary load curtailment
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding - outside of CW NSW
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding in CW NSW
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 1515771286.1832 | 0 | 0 | 0 | 0 | 0 | 1981052449.9051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 1520518289.8937 | 0 | 0 | 0 | 0 | 0 | 1987256593.9051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 1520518289.8937 | 0 | 0 | 0 | 0 | 0 | 1987256593.9051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
Avoided costs for non RIT-T proponent parties
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
Competition benefits
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7A |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7D |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NNO receipts received from TNSP
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality

## High
High
NPV results
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | -139604367.0144 | 0 | -375367.5 | -1543786.2359 | -4520559.6742 | -15009757.8628 | -137147557.19 | -60347592.482 | -3687561.195 | -3687561.195 | -3687561.195 | -3687561.195 | -3687561.195 | -3687561.195 | -3687561.195 | -3687561.195 | -3687561.195 | -3687561.195 | -3687561.195 | -3687561.195 | 136229527.6425
Option 1C |  |  | $ | 3099300374.8953 | 0 | 0 | -1907913.4859 | -10955549.9242 | -36707347.8628 | 3505542815.8076 | -54134376.632 | -3459137.595 | -3459137.595 | -3459137.595 | -3459137.595 | -3459137.595 | -3459137.595 | -3459137.595 | -3459137.595 | -3459137.595 | -3459137.595 | -3459137.595 | -3459137.595 | 128467931.205
Option 3 |  |  | $ | 3399530491.8045 | 0 | -318828.75 | -3844459.5 | -20101551 | -54764547.5625 | 3850559659.9014 | -10630488.8063 | -3409309.5563 | -3409309.5563 | -3409309.5563 | -3409309.5563 | -3409309.5563 | -3409309.5563 | -3409309.5563 | -3409309.5563 | -3409309.5563 | -3409309.5563 | -3409309.5563 | -3409309.5563 | 97948458.4969
Option 4 |  |  | $ | 3370410844.5063 | 0 | 0 | -4009606.2359 | -21009449.9242 | -58458212.4253 | 3844168232.2113 | -53726305.4982 | -3861390.4612 | -3861390.4612 | -3861390.4612 | -3861390.4612 | -3861390.4612 | -3861390.4612 | -3861390.4612 | -3861390.4612 | -3861390.4612 | -3861390.4612 | -3861390.4612 | -3861390.4612 | 132260357.0044
Option 5 |  |  | $ | 3389782422.2867 | Redacted to preserve confidentiality
Option 6 |  |  | $ | 3360662774.9886 | Redacted to preserve confidentiality
Option 7A |  |  | $ | 8442533113.4856 | Redacted to preserve confidentiality
Option 7B |  |  | $ | 8556387024.1629 | Redacted to preserve confidentiality
Option 7C |  |  | $ | 8470611932.3849 | Redacted to preserve confidentiality
Option 7D |  |  | $ | 8468389941.6657 | Redacted to preserve confidentiality
Capital cost calculation
Option | Components | TNSP | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B | Stage 1: line | 1 | $ | -11145145.9123 | 0 | 0 | -277188.0988 | -683575.197 | -1898379.7416 | -9837090.3425 | -11413204.2316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15671134.4475
Option 1A/1B | Stage 1: substation (inc. the 2 TFs) | 1 | $ | -31359588.4707 | 0 | 0 | -540318.3872 | -1433153.4772 | -4259254.1212 | -23964770.3475 | -38006036.0554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44332296.0525
Option 1A/1B | Stage 2: line | 1 | $ | -43303523.3569 | 0 | -375367.5 | -726279.75 | -2403831 | -8852124 | -72466696.5 | -7240791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59842308.3375
Option 1C | Stage 1: syncon | 1 | $ | -11586342.0874 | 0 | 0 | -1090407 | -6069048 | -14996609.25 | -494057.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14156325.9375
Option 1C | Stage 2: line | 1 | $ | -11145145.9123 | 0 | 0 | -277188.0988 | -683575.197 | -1898379.7416 | -9837090.3425 | -11413204.2316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15671134.4475
Option 1C | Stage 2: substation (inc. the 2 TFs) | 1 | $ | -31359588.4707 | 0 | 0 | -540318.3872 | -1433153.4772 | -4259254.1212 | -23964770.3475 | -38006036.0554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44332296.0525
Option 1C | Stage 3: syncon | 1 | $ | -9286069.5843 | 0 | 0 | 0 | -927062.25 | -5247618.75 | -12956110.5 | -420706.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12708473.7
Option 1C | Stage 4: 2 x syncons | 1 | $ | -18258732.2318 | 0 | 0 | 0 | -1842711 | -10305486 | -25458801 | -835292.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24987488.6625
Option 3 | Stage 1: SVC at Panorama | 1 | $ | -14750061.8176 | 0 | 0 | -287987.25 | -1827125.25 | -6948832.3125 | -10794448.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4964598.3281
Option 3 | Stage 1: syncons at Parkes | 1 | $ | -30721761.5829 | 0 | 0 | -2904112.5 | -16084221.75 | -39753836.25 | -1315237.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37535880
Option 3 | Stage 2: line | 1 | $ | -42560933.6421 | 0 | -318828.75 | -652359.75 | -2190204 | -8061879 | -72105225.75 | -7221179.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58857289.725
Option 4 | Stage 1: SVC at Panorama | 1 | $ | -14750061.8176 | 0 | 0 | -287987.25 | -1827125.25 | -6948832.3125 | -10794448.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4964598.3281
Option 4 | Stage 1: syncons at Parkes | 1 | $ | -30721761.5829 | 0 | 0 | -2904112.5 | -16084221.75 | -39753836.25 | -1315237.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37535880
Option 4 | Stage 2: line | 1 | $ | -11145145.9123 | 0 | 0 | -277188.0988 | -683575.197 | -1898379.7416 | -9837090.3425 | -11413204.2316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15671134.4475
Option 4 | Stage 2: substation (inc. the 2 TFs) | 1 | $ | -31359588.4707 | 0 | 0 | -540318.3872 | -1433153.4772 | -4259254.1212 | -23964770.3475 | -38006036.0554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44332296.0525
Option 4 | Stage 3: syncon | 1 | $ | -9898270.0376 | 0 | 0 | 0 | -981374.25 | -5597910 | -13815792.75 | -445674.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13546488.6375
Option 5 | Stage 1: syncons | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Stage 1: Panorama - 20MW/40MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Stage 1: Parkes - 15MW/30MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Reinvestment: Panorama - 20MW/40MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Reinvestment: Parkes - 15MW/30MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 1: syncons | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 1: Panorama - 20MW/40MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 1: Parkes - 15MW/30MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Reinvestment: Panorama - 20MW/40MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Reinvestment: Parkes - 15MW/30MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 2: substation (inc. the 2 TFs) | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 3: syncon | 1 | $ |  | Redacted to preserve confidentiality
Option 7A | Stage 1: Parkes BESS and PV | 0 | $ |  | Redacted to preserve confidentiality
Option 7A | Stage 1: Panorama BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7A | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 7B | Stage 1: Parkes BESS and PV | 0 | $ |  | Redacted to preserve confidentiality
Option 7B | Stage 1: Panorama BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7B | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 7C | Stage 1: Parkes BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7C | Stage 1: Panorama BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7C | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 7D | Stage 1: Parkes BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7D | Stage 1: Panorama BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7D | Syncons | 0 | $ |  | Redacted to preserve confidentiality
Option 7D | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Biodiversity offset costs | Bio costs component
Option 1A/1B | Stage 1: line | 1 | $ | -1467491.2794 | 0 | 0 | 0 | 0 | 0 | -3135000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2037750
Option 1A/1B | Stage 1: substation (inc. the 2 TFs) | 1 | $ | -3191266.921 | 0 | 0 | 0 | 0 | 0 | -6817500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4431375
Option 1C | Stage 2: line | 1 | $ | -1467491.2794 | 0 | 0 | 0 | 0 | 0 | -3135000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2037750
Option 1C | Stage 2: substation (inc. the 2 TFs) | 1 | $ | -3191266.921 | 0 | 0 | 0 | 0 | 0 | -6817500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4431375
Option 4 | Stage 2: line | 1 | $ | -1467491.2794 | 0 | 0 | 0 | 0 | 0 | -3135000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2037750
Option 4 | Stage 2: substation (inc. the 2 TFs) | 1 | $ | -3191266.921 | 0 | 0 | 0 | 0 | 0 | -6817500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4431375
Option 6 | Stage 2: line | 1 | $ | -1467491.2794 | 0 | 0 | 0 | 0 | 0 | -3135000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2037750
Option 6 | Stage 2: substation (inc. the 2 TFs) | 1 | $ | -3191266.921 | 0 | 0 | 0 | 0 | 0 | -6817500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4431375
Property allowances | Property allowances component
Option 1A/1B | Stage 1: line | 1 | $ | -8243228.5264 | 0 | 0 | 0 | 0 | 0 | -17610000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11446500
Option 1A/1B | Stage 1: substation (inc. the 2 TFs) | 1 | $ | -1552451.3008 | 0 | 0 | 0 | 0 | 0 | -3316500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2155725
Option 1C | Stage 2: line | 1 | $ | -8243228.5264 | 0 | 0 | 0 | 0 | 0 | -17610000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11446500
Option 1C | Stage 2: substation (inc. the 2 TFs) | 1 | $ | -1552451.3008 | 0 | 0 | 0 | 0 | 0 | -3316500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2155725
Option 4 | Stage 2: line | 1 | $ | -8243228.5264 | 0 | 0 | 0 | 0 | 0 | -17610000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11446500
Option 4 | Stage 2: substation (inc. the 2 TFs) | 1 | $ | -1552451.3008 | 0 | 0 | 0 | 0 | 0 | -3316500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2155725
Option 6 | Stage 2: line | 1 | $ | -8243228.5264 | 0 | 0 | 0 | 0 | 0 | -17610000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11446500
Option 6 | Stage 2: substation (inc. the 2 TFs) | 1 | $ | -1552451.3008 | 0 | 0 | 0 | 0 | 0 | -3316500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2155725
TNSP capital costs
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | -100262695.7675 | 0 | -375367.5 | -1543786.2359 | -4520559.6742 | -15009757.8628 | -137147557.19 | -56660031.287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139917088.8375
Option 1C |  |  | $ | -96090316.3141 | 0 | 0 | -1907913.4859 | -10955549.9242 | -36707347.8628 | -103589829.44 | -50675239.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131927068.8
Option 3 |  |  | $ | -88032757.0426 | 0 | -318828.75 | -3844459.5 | -20101551 | -54764547.5625 | -84214911.75 | -7221179.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101357768.0531
Option 4 |  |  | $ | -112329265.8487 | 0 | 0 | -4009606.2359 | -21009449.9242 | -58458212.4253 | -90606339.44 | -49864915.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136121747.4656
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
NNO capital costs
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
Operating cost calculation
Option | Components | TNSP | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B | Stage 1: line | 1 | $ | -5144351.6097 | 0 | 0 | 0 | 0 | 0 | 0 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522
Option 1A/1B | Stage 1: substation (inc. the 2 TFs) | 1 | $ | -14552929.7398 | 0 | 0 | 0 | 0 | 0 | 0 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478
Option 1A/1B | Stage 2: line | 1 | $ | -19644389.8975 | 0 | 0 | 0 | 0 | 0 | 0 | -1841301.795 | -1841301.795 | -1841301.795 | -1841301.795 | -1841301.795 | -1841301.795 | -1841301.795 | -1841301.795 | -1841301.795 | -1841301.795 | -1841301.795 | -1841301.795 | -1841301.795 | -1841301.795
Option 1C | Stage 1: syncon | 1 | $ | -5238673.4877 | 0 | 0 | 0 | 0 | 0 | -453002.43 | -453002.43 | -453002.43 | -453002.43 | -453002.43 | -453002.43 | -453002.43 | -453002.43 | -453002.43 | -453002.43 | -453002.43 | -453002.43 | -453002.43 | -453002.43 | -453002.43
Option 1C | Stage 2: line | 1 | $ | -5144351.6097 | 0 | 0 | 0 | 0 | 0 | 0 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522
Option 1C | Stage 2: substation (inc. the 2 TFs) | 1 | $ | -14552929.7398 | 0 | 0 | 0 | 0 | 0 | 0 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478
Option 1C | Stage 3: syncon | 1 | $ | -4171801.1771 | 0 | 0 | 0 | 0 | 0 | 0 | -391029.96 | -391029.96 | -391029.96 | -391029.96 | -391029.96 | -391029.96 | -391029.96 | -391029.96 | -391029.96 | -391029.96 | -391029.96 | -391029.96 | -391029.96 | -391029.96
Option 1C | Stage 4: 2 x syncons | 1 | $ | -8202624.255 | 0 | 0 | 0 | 0 | 0 | 0 | -768845.805 | -768845.805 | -768845.805 | -768845.805 | -768845.805 | -768845.805 | -768845.805 | -768845.805 | -768845.805 | -768845.805 | -768845.805 | -768845.805 | -768845.805 | -768845.805
Option 3 | Stage 1: SVC at Panorama | 1 | $ | -4592983.6868 | 0 | 0 | 0 | 0 | 0 | -397167.8663 | -397167.8663 | -397167.8663 | -397167.8663 | -397167.8663 | -397167.8663 | -397167.8663 | -397167.8663 | -397167.8663 | -397167.8663 | -397167.8663 | -397167.8663 | -397167.8663 | -397167.8663 | -397167.8663
Option 3 | Stage 1: syncons at Parkes | 1 | $ | -13890484.0325 | 0 | 0 | 0 | 0 | 0 | -1201148.16 | -1201148.16 | -1201148.16 | -1201148.16 | -1201148.16 | -1201148.16 | -1201148.16 | -1201148.16 | -1201148.16 | -1201148.16 | -1201148.16 | -1201148.16 | -1201148.16 | -1201148.16 | -1201148.16
Option 3 | Stage 2: line | 1 | $ | -19321038.5726 | 0 | 0 | 0 | 0 | 0 | 0 | -1810993.53 | -1810993.53 | -1810993.53 | -1810993.53 | -1810993.53 | -1810993.53 | -1810993.53 | -1810993.53 | -1810993.53 | -1810993.53 | -1810993.53 | -1810993.53 | -1810993.53 | -1810993.53
Option 4 | Stage 1: SVC at Panorama | 1 | $ | -4592983.6868 | 0 | 0 | 0 | 0 | 0 | -397167.8663 | -397167.8663 | -397167.8663 | -397167.8663 | -397167.8663 | -397167.8663 | -397167.8663 | -397167.8663 | -397167.8663 | -397167.8663 | -397167.8663 | -397167.8663 | -397167.8663 | -397167.8663 | -397167.8663
Option 4 | Stage 1: syncons at Parkes | 1 | $ | -13890484.0325 | 0 | 0 | 0 | 0 | 0 | -1201148.16 | -1201148.16 | -1201148.16 | -1201148.16 | -1201148.16 | -1201148.16 | -1201148.16 | -1201148.16 | -1201148.16 | -1201148.16 | -1201148.16 | -1201148.16 | -1201148.16 | -1201148.16 | -1201148.16
Option 4 | Stage 2: line | 1 | $ | -5144351.6097 | 0 | 0 | 0 | 0 | 0 | 0 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522 | -482188.7522
Option 4 | Stage 2: substation (inc. the 2 TFs) | 1 | $ | -14552929.7398 | 0 | 0 | 0 | 0 | 0 | 0 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478 | -1364070.6478
Option 4 | Stage 3: syncon | 1 | $ | -4446895.7152 | 0 | 0 | 0 | 0 | 0 | 0 | -416815.035 | -416815.035 | -416815.035 | -416815.035 | -416815.035 | -416815.035 | -416815.035 | -416815.035 | -416815.035 | -416815.035 | -416815.035 | -416815.035 | -416815.035 | -416815.035
Option 5 | Stage 1: syncons | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Stage 1: Panorama - 20MW/40MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Stage 1: Parkes - 15MW/30MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Reinvestment: Panorama - 20MW/40MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Reinvestment: Parkes - 15MW/30MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 1: syncons | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 1: Panorama - 20MW/40MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 1: Parkes - 15MW/30MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Reinvestment: Panorama - 20MW/40MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Reinvestment: Parkes - 15MW/30MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 2: substation (inc. the 2 TFs) | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 3: syncon | 1 | $ |  | Redacted to preserve confidentiality
Option 7A | Stage 1: Parkes BESS and PV | 0 | $ |  | Redacted to preserve confidentiality
Option 7A | Stage 1: Panorama BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7A | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 7B | Stage 1: Parkes BESS and PV | 0 | $ |  | Redacted to preserve confidentiality
Option 7B | Stage 1: Panorama BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7B | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 7C | Stage 1: Parkes BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7C | Stage 1: Panorama BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7C | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 7D | Stage 1: Parkes BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7D | Stage 1: Panorama BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7D | Syncons | 0 | $ |  | Redacted to preserve confidentiality
Option 7D | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
TNSP operating expenditure
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | -39341671.2469 | 0 | 0 | 0 | 0 | 0 | 0 | -3687561.195 | -3687561.195 | -3687561.195 | -3687561.195 | -3687561.195 | -3687561.195 | -3687561.195 | -3687561.195 | -3687561.195 | -3687561.195 | -3687561.195 | -3687561.195 | -3687561.195 | -3687561.195
Option 1C |  |  | $ | -37310380.2693 | 0 | 0 | 0 | 0 | 0 | -453002.43 | -3459137.595 | -3459137.595 | -3459137.595 | -3459137.595 | -3459137.595 | -3459137.595 | -3459137.595 | -3459137.595 | -3459137.595 | -3459137.595 | -3459137.595 | -3459137.595 | -3459137.595 | -3459137.595
Option 3 |  |  | $ | -37804506.2919 | 0 | 0 | 0 | 0 | 0 | -1598316.0263 | -3409309.5563 | -3409309.5563 | -3409309.5563 | -3409309.5563 | -3409309.5563 | -3409309.5563 | -3409309.5563 | -3409309.5563 | -3409309.5563 | -3409309.5563 | -3409309.5563 | -3409309.5563 | -3409309.5563 | -3409309.5563
Option 4 |  |  | $ | -42627644.784 | 0 | 0 | 0 | 0 | 0 | -1598316.0263 | -3861390.4612 | -3861390.4612 | -3861390.4612 | -3861390.4612 | -3861390.4612 | -3861390.4612 | -3861390.4612 | -3861390.4612 | -3861390.4612 | -3861390.4612 | -3861390.4612 | -3861390.4612 | -3861390.4612 | -3861390.4612
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
TNSP NNO operating expenditure
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
NNO operating expenditure
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
Avoided fuel consumption from generation dispatch
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
Avoided voluntary load curtailment
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding - outside of CW NSW
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding in CW NSW
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 3232701071.4787 | 0 | 0 | 0 | 0 | 0 | 3609585647.6776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 3525367755.139 | 0 | 0 | 0 | 0 | 0 | 3936372887.6776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 3525367755.139 | 0 | 0 | 0 | 0 | 0 | 3936372887.6776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
Avoided costs for non RIT-T proponent parties
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
NNO receipts received from TNSP
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality

## Low
Low
NPV results
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | -124584581.4023 | 0 | 0 | -1362510.8099 | -3527881.1237 | -10262723.1047 | -107801434.4834 | -85442499.4783 | -3077099 | -3077099 | -3077099 | -3077099 | -3077099 | -3077099 | -3077099 | -3077099 | -3077099 | -3077099 | -3077099 | -3077099 | 130380868.5
Option 1C |  |  | $ | -102959871.924 | 0 | 0 | -1817345 | -10115080 | -24994348.75 | 1385569.0796 | -2117514.8599 | -4282885.1737 | -11017727.1547 | -108556438.5334 | -86197503.5283 | -3832103.05 | -3832103.05 | -3832103.05 | -3832103.05 | -3832103.05 | -3832103.05 | -3832103.05 | -3832103.05 | 173751736.0125
Option 3 |  |  | $ | -98593996.5418 | 0 | 0 | -5320166.25 | -29852245 | -77837780.9375 | -19882668.1642 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | 68170270.5031
Option 4 |  |  | $ | -98593996.5418 | 0 | 0 | -5320166.25 | -29852245 | -77837780.9375 | -19882668.1642 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | 68170270.5031
Option 5 |  |  | $ | -143059733.5251 | Redacted to preserve confidentiality
Option 6 |  |  | $ | -143059733.5251 | Redacted to preserve confidentiality
Option 7A |  |  | $ | -174178461.687 | Redacted to preserve confidentiality
Option 7B |  |  | $ | -204607824.0937 | Redacted to preserve confidentiality
Option 7C |  |  | $ | -227517306.4552 | Redacted to preserve confidentiality
Option 7D |  |  | $ | -40331950.8193 | Redacted to preserve confidentiality
Capital cost calculation
Option | Components | TNSP | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B | Stage 1: line | 1 | $ | -20821942.7524 | 0 | 0 | -461980.1646 | -1139291.995 | -3163966.2361 | -16395150.5709 | -19022007.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26118557.4125
Option 1A/1B | Stage 1: substation (inc. the 2 TFs) | 1 | $ | -58184499.361 | 0 | 0 | -900530.6453 | -2388589.1287 | -7098756.8686 | -39941283.9125 | -63343393.4256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73887160.0875
Option 1A/1B | Stage 2: line | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C | Stage 1: syncon | 1 | $ | -23033314.5297 | 0 | 0 | -1817345 | -10115080 | -24994348.75 | -823428.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23593876.5625
Option 1C | Stage 2: line | 1 | $ | -12914210.9104 | 0 | 0 | 0 | 0 | 0 | 0 | -461980.1646 | -1139291.995 | -3163966.2361 | -16395150.5709 | -19022007.0526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30136797.0144
Option 1C | Stage 2: substation (inc. the 2 TFs) | 1 | $ | -35994814.192 | 0 | 0 | 0 | 0 | 0 | 0 | -900530.6453 | -2388589.1287 | -7098756.8686 | -39941283.9125 | -63343393.4256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85254415.4856
Option 1C | Stage 3: syncon | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C | Stage 4: 2 x syncons | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Stage 1: SVC at Panorama | 1 | $ | -21976395.903 | 0 | 0 | -479978.75 | -3045208.75 | -11581387.1875 | -17990747.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8274330.5469
Option 3 | Stage 1: syncons at Parkes | 1 | $ | -61074747.6382 | 0 | 0 | -4840187.5 | -26807036.25 | -66256393.75 | -2192062.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62559800
Option 3 | Stage 2: line | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Stage 1: SVC at Panorama | 1 | $ | -21976395.903 | 0 | 0 | -479978.75 | -3045208.75 | -11581387.1875 | -17990747.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8274330.5469
Option 4 | Stage 1: syncons at Parkes | 1 | $ | -61074747.6382 | 0 | 0 | -4840187.5 | -26807036.25 | -66256393.75 | -2192062.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62559800
Option 4 | Stage 2: line | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Stage 2: substation (inc. the 2 TFs) | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Stage 3: syncon | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Stage 1: syncons | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Stage 1: Panorama - 20MW/40MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Stage 1: Parkes - 15MW/30MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Reinvestment: Panorama - 20MW/40MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Reinvestment: Parkes - 15MW/30MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 1: syncons | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 1: Panorama - 20MW/40MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 1: Parkes - 15MW/30MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Reinvestment: Panorama - 20MW/40MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Reinvestment: Parkes - 15MW/30MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 2: substation (inc. the 2 TFs) | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 3: syncon | 1 | $ |  | Redacted to preserve confidentiality
Option 7A | Stage 1: Parkes BESS and PV | 0 | $ |  | Redacted to preserve confidentiality
Option 7A | Stage 1: Panorama BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7A | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 7B | Stage 1: Parkes BESS and PV | 0 | $ |  | Redacted to preserve confidentiality
Option 7B | Stage 1: Panorama BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7B | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 7C | Stage 1: Parkes BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7C | Stage 1: Panorama BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7C | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 7D | Stage 1: Parkes BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7D | Stage 1: Panorama BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7D | Syncons | 0 | $ |  | Redacted to preserve confidentiality
Option 7D | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Biodiversity offset costs | Bio costs component
Option 1A/1B | Stage 1: line | 1 | $ | -2780032.8071 | 0 | 0 | 0 | 0 | 0 | -5225000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3396250
Option 1A/1B | Stage 1: substation (inc. the 2 TFs) | 1 | $ | -6045573.7361 | 0 | 0 | 0 | 0 | 0 | -11362500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7385625
Option 1C | Stage 2: line | 1 | $ | -1733558.9765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5225000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3918750
Option 1C | Stage 2: substation (inc. the 2 TFs) | 1 | $ | -3769868.6834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11362500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8521875
Option 4 | Stage 2: line | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Stage 2: substation (inc. the 2 TFs) | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 | Stage 2: line | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 | Stage 2: substation (inc. the 2 TFs) | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Property allowances | Property allowances component
Option 1A/1B | Stage 1: line | 1 | $ | -15616069.4524 | 0 | 0 | 0 | 0 | 0 | -29350000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19077500
Option 1A/1B | Stage 1: substation (inc. the 2 TFs) | 1 | $ | -2940982.0749 | 0 | 0 | 0 | 0 | 0 | -5527500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3592875
Option 1C | Stage 2: line | 1 | $ | -9737790.6145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -29350000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22012500
Option 1C | Stage 2: substation (inc. the 2 TFs) | 1 | $ | -1833922.9173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5527500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4145625
Option 4 | Stage 2: line | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Stage 2: substation (inc. the 2 TFs) | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 | Stage 2: line | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 6 | Stage 2: substation (inc. the 2 TFs) | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TNSP capital costs
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | -106389100.1839 | 0 | 0 | -1362510.8099 | -3527881.1237 | -10262723.1047 | -107801434.4834 | -82365400.4783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133457967.5
Option 1C |  |  | $ | -89017480.8238 | 0 | 0 | -1817345 | -10115080 | -24994348.75 | -823428.75 | -1362510.8099 | -3527881.1237 | -10262723.1047 | -107801434.4834 | -82365400.4783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177583839.0625
Option 3 |  |  | $ | -83051143.5413 | 0 | 0 | -5320166.25 | -29852245 | -77837780.9375 | -20182810 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70834130.5469
Option 4 |  |  | $ | -83051143.5413 | 0 | 0 | -5320166.25 | -29852245 | -77837780.9375 | -20182810 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70834130.5469
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
NNO capital costs
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
Operating cost calculation
Option | Components | TNSP | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B | Stage 1: line | 1 | $ | -4752125.5057 | 0 | 0 | 0 | 0 | 0 | 0 | -803647.9204 | -803647.9204 | -803647.9204 | -803647.9204 | -803647.9204 | -803647.9204 | -803647.9204 | -803647.9204 | -803647.9204 | -803647.9204 | -803647.9204 | -803647.9204 | -803647.9204 | -803647.9204
Option 1A/1B | Stage 1: substation (inc. the 2 TFs) | 1 | $ | -13443355.7126 | 0 | 0 | 0 | 0 | 0 | 0 | -2273451.0796 | -2273451.0796 | -2273451.0796 | -2273451.0796 | -2273451.0796 | -2273451.0796 | -2273451.0796 | -2273451.0796 | -2273451.0796 | -2273451.0796 | -2273451.0796 | -2273451.0796 | -2273451.0796 | -2273451.0796
Option 1A/1B | Stage 2: line | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C | Stage 1: syncon | 1 | $ | -4990389.4853 | 0 | 0 | 0 | 0 | 0 | -755004.05 | -755004.05 | -755004.05 | -755004.05 | -755004.05 | -755004.05 | -755004.05 | -755004.05 | -755004.05 | -755004.05 | -755004.05 | -755004.05 | -755004.05 | -755004.05 | -755004.05
Option 1C | Stage 2: line | 1 | $ | -2877213.1992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -803647.9204 | -803647.9204 | -803647.9204 | -803647.9204 | -803647.9204 | -803647.9204 | -803647.9204 | -803647.9204 | -803647.9204 | -803647.9204
Option 1C | Stage 2: substation (inc. the 2 TFs) | 1 | $ | -8139389.5112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2273451.0796 | -2273451.0796 | -2273451.0796 | -2273451.0796 | -2273451.0796 | -2273451.0796 | -2273451.0796 | -2273451.0796 | -2273451.0796 | -2273451.0796
Option 1C | Stage 3: syncon | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C | Stage 4: 2 x syncons | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 | Stage 1: SVC at Panorama | 1 | $ | -4375301.7917 | 0 | 0 | 0 | 0 | 0 | -661946.4438 | -661946.4438 | -661946.4438 | -661946.4438 | -661946.4438 | -661946.4438 | -661946.4438 | -661946.4438 | -661946.4438 | -661946.4438 | -661946.4438 | -661946.4438 | -661946.4438 | -661946.4438 | -661946.4438
Option 3 | Stage 1: syncons at Parkes | 1 | $ | -13232152.3043 | 0 | 0 | 0 | 0 | 0 | -2001913.6 | -2001913.6 | -2001913.6 | -2001913.6 | -2001913.6 | -2001913.6 | -2001913.6 | -2001913.6 | -2001913.6 | -2001913.6 | -2001913.6 | -2001913.6 | -2001913.6 | -2001913.6 | -2001913.6
Option 3 | Stage 2: line | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Stage 1: SVC at Panorama | 1 | $ | -4375301.7917 | 0 | 0 | 0 | 0 | 0 | -661946.4438 | -661946.4438 | -661946.4438 | -661946.4438 | -661946.4438 | -661946.4438 | -661946.4438 | -661946.4438 | -661946.4438 | -661946.4438 | -661946.4438 | -661946.4438 | -661946.4438 | -661946.4438 | -661946.4438
Option 4 | Stage 1: syncons at Parkes | 1 | $ | -13232152.3043 | 0 | 0 | 0 | 0 | 0 | -2001913.6 | -2001913.6 | -2001913.6 | -2001913.6 | -2001913.6 | -2001913.6 | -2001913.6 | -2001913.6 | -2001913.6 | -2001913.6 | -2001913.6 | -2001913.6 | -2001913.6 | -2001913.6 | -2001913.6
Option 4 | Stage 2: line | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Stage 2: substation (inc. the 2 TFs) | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 | Stage 3: syncon | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 | Stage 1: syncons | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Stage 1: Panorama - 20MW/40MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Stage 1: Parkes - 15MW/30MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Reinvestment: Panorama - 20MW/40MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Reinvestment: Parkes - 15MW/30MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 5 | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 1: syncons | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 1: Panorama - 20MW/40MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 1: Parkes - 15MW/30MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Reinvestment: Panorama - 20MW/40MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Reinvestment: Parkes - 15MW/30MWh BESS | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 2: substation (inc. the 2 TFs) | 1 | $ |  | Redacted to preserve confidentiality
Option 6 | Stage 3: syncon | 1 | $ |  | Redacted to preserve confidentiality
Option 7A | Stage 1: Parkes BESS and PV | 0 | $ |  | Redacted to preserve confidentiality
Option 7A | Stage 1: Panorama BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7A | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 7B | Stage 1: Parkes BESS and PV | 0 | $ |  | Redacted to preserve confidentiality
Option 7B | Stage 1: Panorama BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7B | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 7C | Stage 1: Parkes BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7C | Stage 1: Panorama BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7C | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
Option 7D | Stage 1: Parkes BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7D | Stage 1: Panorama BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 7D | Syncons | 0 | $ |  | Redacted to preserve confidentiality
Option 7D | Stage 2: line | 1 | $ |  | Redacted to preserve confidentiality
TNSP operating expenditure
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | -18195481.2183 | 0 | 0 | 0 | 0 | 0 | 0 | -3077099 | -3077099 | -3077099 | -3077099 | -3077099 | -3077099 | -3077099 | -3077099 | -3077099 | -3077099 | -3077099 | -3077099 | -3077099 | -3077099
Option 1C |  |  | $ | -16006992.1957 | 0 | 0 | 0 | 0 | 0 | -755004.05 | -755004.05 | -755004.05 | -755004.05 | -755004.05 | -3832103.05 | -3832103.05 | -3832103.05 | -3832103.05 | -3832103.05 | -3832103.05 | -3832103.05 | -3832103.05 | -3832103.05 | -3832103.05
Option 3 |  |  | $ | -17607454.096 | 0 | 0 | 0 | 0 | 0 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438
Option 4 |  |  | $ | -17607454.096 | 0 | 0 | 0 | 0 | 0 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438 | -2663860.0438
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
TNSP NNO operating expenditure
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
NNO operating expenditure
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
Avoided fuel consumption from generation dispatch
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
Avoided voluntary load curtailment
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding - outside of CW NSW
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding in CW NSW
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 2064601.0955 | 0 | 0 | 0 | 0 | 1.3301e-09 | 2964001.8796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 2064601.0955 | 0 | 0 | 0 | 0 | 1.3301e-09 | 2964001.8796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 2064601.0955 | 0 | 0 | 0 | 0 | 1.3301e-09 | 2964001.8796 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
Avoided costs for non RIT-T proponent parties
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality
NNO receipts received from TNSP
Option |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  |  | $ |  | Redacted to preserve confidentiality
Option 6 |  |  | $ |  | Redacted to preserve confidentiality
Option 7A |  |  | $ |  | Redacted to preserve confidentiality
Option 7B |  |  | $ |  | Redacted to preserve confidentiality
Option 7C |  |  | $ |  | Redacted to preserve confidentiality
Option 7D |  |  | $ |  | Redacted to preserve confidentiality

## Weighted
Scenario weighting settings |  |  | Unit | Central | High | Low
Scenario weighting |  |  | % | 50% | 25% | 25%
Weighted | NPV results
NPV results
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  | $ | -159516159.0137 | 0 | -344086.875 | -1755765.0854 | -5025816.649 | -16324625.4837 | -152668952.7117 | -76679251.3114 | -4149539.1787 | -4149539.1787 | -4149539.1787 | -4149539.1787 | -4149539.1787 | -4149539.1787 | -4149539.1787 | -4149539.1787 | -4149539.1787 | -4149539.1787 | -4149539.1787 | -4149539.1787 | 157472284.1306
Option 1C |  | $ | 1438011747.7388 | 0 | 0 | -2203256.9454 | -10724841.9306 | -29528252.8951 | 1823506374.261 | -48541974.2843 | -4086388.4122 | -8650469.9074 | -38174142.2521 | -24488159.1408 | -3616338.0213 | -3616338.0213 | -3616338.0213 | -3616338.0213 | -3616338.0213 | -3616338.0213 | -3616338.0213 | -3616338.0213 | 146357875.5694
Option 3 |  | $ | 1516971771.4101 | 0 | -79707.1875 | -4419222.9375 | -24429347 | -64285694.5 | 1941946324.3694 | -4824037.73 | -4043972.4175 | -7958422.4175 | -50653986.9175 | -8605284.9375 | -3791165.4375 | -3791165.4375 | -3791165.4375 | -3791165.4375 | -3791165.4375 | -3791165.4375 | -3791165.4375 | -3791165.4375 | 112865299.6813
Option 4 |  | $ | 1503015097.4051 | 0 | 0 | -4460509.6215 | -24656321.7311 | -65209110.7157 | 1940561019.9468 | -15708089.727 | -4108009.0932 | -6801945.8856 | -45817430.4371 | -36873856.4351 | -3927696.2437 | -3927696.2437 | -3927696.2437 | -3927696.2437 | -3927696.2437 | -3927696.2437 | -3927696.2437 | -3927696.2437 | 137740910.4781
Option 5 |  | $ | 1489423608.5292 | Redacted to preserve confidentiality
Option 6 |  | $ | 1475466934.5241 | Redacted to preserve confidentiality
Option 7A |  | $ | 3831209125.2235 | Redacted to preserve confidentiality
Option 7B |  | $ | 3860531021.7138 | Redacted to preserve confidentiality
Option 7C |  | $ | 3820143256.1006 | Redacted to preserve confidentiality
Option 7D |  | $ | 3919744793.8945 | Redacted to preserve confidentiality
Weighted | Calculation
TNSP capital costs
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  | $ | -127093872.6525 | 0 | -344086.875 | -1755765.0854 | -5025816.649 | -16324625.4837 | -152668952.7117 | -72529712.1326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161621823.3094
Option 1C |  | $ | -102544261.071 | 0 | 0 | -2203256.9454 | -10724841.9306 | -29528252.8951 | -69553259.8409 | -45955597.653 | -1500011.7809 | -6064093.2762 | -35587765.6208 | -20871821.1196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149974213.5906
Option 3 |  | $ | -97038228.6002 | 0 | -79707.1875 | -4419222.9375 | -24429347 | -64285694.5 | -34385106.9375 | -2240201.3125 | -1460136 | -5374586 | -48070150.5 | -4814119.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116656465.1188
Option 4 |  | $ | -109679665.4581 | 0 | 0 | -4460509.6215 | -24656321.7311 | -65209110.7157 | -35770411.36 | -13011233.0832 | -1411152.4495 | -4105089.2419 | -43120573.7934 | -32946160.1913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141668606.7219
Option 5 |  | $ |  | Redacted to preserve confidentiality
Option 6 |  | $ |  | Redacted to preserve confidentiality
Option 7A |  | $ |  | Redacted to preserve confidentiality
Option 7B |  | $ |  | Redacted to preserve confidentiality
Option 7C |  | $ |  | Redacted to preserve confidentiality
Option 7D |  | $ |  | Redacted to preserve confidentiality
NNO capital costs
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | $ |  | Redacted to preserve confidentiality
Option 6 |  | $ |  | Redacted to preserve confidentiality
Option 7A |  | $ |  | Redacted to preserve confidentiality
Option 7B |  | $ |  | Redacted to preserve confidentiality
Option 7C |  | $ |  | Redacted to preserve confidentiality
Option 7D |  | $ |  | Redacted to preserve confidentiality
TNSP operating expenditure
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  | $ | -32422286.3612 | 0 | 0 | 0 | 0 | 0 | 0 | -4149539.1787 | -4149539.1787 | -4149539.1787 | -4149539.1787 | -4149539.1787 | -4149539.1787 | -4149539.1787 | -4149539.1787 | -4149539.1787 | -4149539.1787 | -4149539.1787 | -4149539.1787 | -4149539.1787 | -4149539.1787
Option 1C |  | $ | -26021052.4254 | 0 | 0 | 0 | 0 | 0 | -604003.24 | -2586376.6312 | -2586376.6312 | -2586376.6312 | -2586376.6312 | -3616338.0213 | -3616338.0213 | -3616338.0213 | -3616338.0213 | -3616338.0213 | -3616338.0213 | -3616338.0213 | -3616338.0213 | -3616338.0213 | -3616338.0213
Option 3 |  | $ | -28107233.9952 | 0 | 0 | 0 | 0 | 0 | -2131088.035 | -2583836.4175 | -2583836.4175 | -2583836.4175 | -2583836.4175 | -3791165.4375 | -3791165.4375 | -3791165.4375 | -3791165.4375 | -3791165.4375 | -3791165.4375 | -3791165.4375 | -3791165.4375 | -3791165.4375 | -3791165.4375
Option 4 |  | $ | -29422471.1423 | 0 | 0 | 0 | 0 | 0 | -2131088.035 | -2696856.6437 | -2696856.6437 | -2696856.6437 | -2696856.6437 | -3927696.2437 | -3927696.2437 | -3927696.2437 | -3927696.2437 | -3927696.2437 | -3927696.2437 | -3927696.2437 | -3927696.2437 | -3927696.2437 | -3927696.2437
Option 5 |  | $ |  | Redacted to preserve confidentiality
Option 6 |  | $ |  | Redacted to preserve confidentiality
Option 7A |  | $ |  | Redacted to preserve confidentiality
Option 7B |  | $ |  | Redacted to preserve confidentiality
Option 7C |  | $ |  | Redacted to preserve confidentiality
Option 7D |  | $ |  | Redacted to preserve confidentiality
TNSP NNO operating expenditure
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | $ |  | Redacted to preserve confidentiality
Option 6 |  | $ |  | Redacted to preserve confidentiality
Option 7A |  | $ |  | Redacted to preserve confidentiality
Option 7B |  | $ |  | Redacted to preserve confidentiality
Option 7C |  | $ |  | Redacted to preserve confidentiality
Option 7D |  | $ |  | Redacted to preserve confidentiality
NNO operating expenditure
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | $ |  | Redacted to preserve confidentiality
Option 6 |  | $ |  | Redacted to preserve confidentiality
Option 7A |  | $ |  | Redacted to preserve confidentiality
Option 7B |  | $ |  | Redacted to preserve confidentiality
Option 7C |  | $ |  | Redacted to preserve confidentiality
Option 7D |  | $ |  | Redacted to preserve confidentiality
Avoided fuel consumption from generation dispatch
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | $ |  | Redacted to preserve confidentiality
Option 6 |  | $ |  | Redacted to preserve confidentiality
Option 7A |  | $ |  | Redacted to preserve confidentiality
Option 7B |  | $ |  | Redacted to preserve confidentiality
Option 7C |  | $ |  | Redacted to preserve confidentiality
Option 7D |  | $ |  | Redacted to preserve confidentiality
Avoided voluntary load curtailment
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | $ |  | Redacted to preserve confidentiality
Option 6 |  | $ |  | Redacted to preserve confidentiality
Option 7A |  | $ |  | Redacted to preserve confidentiality
Option 7B |  | $ |  | Redacted to preserve confidentiality
Option 7C |  | $ |  | Redacted to preserve confidentiality
Option 7D |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding - outside of CW NSW
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | $ |  | Redacted to preserve confidentiality
Option 6 |  | $ |  | Redacted to preserve confidentiality
Option 7A |  | $ |  | Redacted to preserve confidentiality
Option 7B |  | $ |  | Redacted to preserve confidentiality
Option 7C |  | $ |  | Redacted to preserve confidentiality
Option 7D |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding in CW NSW
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  | $ | 1566577061.2352 | 0 | 0 | 0 | 0 | 3.3252e-10 | 1893663637.3419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  | $ | 1642117234.0055 | 0 | 0 | 0 | 0 | 3.3252e-10 | 1978462519.3419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | $ | 1642117234.0055 | 0 | 0 | 0 | 0 | 3.3252e-10 | 1978462519.3419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | $ |  | Redacted to preserve confidentiality
Option 6 |  | $ |  | Redacted to preserve confidentiality
Option 7A |  | $ |  | Redacted to preserve confidentiality
Option 7B |  | $ |  | Redacted to preserve confidentiality
Option 7C |  | $ |  | Redacted to preserve confidentiality
Option 7D |  | $ |  | Redacted to preserve confidentiality
Avoided costs for non RIT-T proponent parties
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | $ |  | Redacted to preserve confidentiality
Option 6 |  | $ |  | Redacted to preserve confidentiality
Option 7A |  | $ |  | Redacted to preserve confidentiality
Option 7B |  | $ |  | Redacted to preserve confidentiality
Option 7C |  | $ |  | Redacted to preserve confidentiality
Option 7D |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | $ |  | Redacted to preserve confidentiality
Option 6 |  | $ |  | Redacted to preserve confidentiality
Option 7A |  | $ |  | Redacted to preserve confidentiality
Option 7B |  | $ |  | Redacted to preserve confidentiality
Option 7C |  | $ |  | Redacted to preserve confidentiality
Option 7D |  | $ |  | Redacted to preserve confidentiality
NNO receipts received from TNSP
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A/1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5 |  | $ |  | Redacted to preserve confidentiality
Option 6 |  | $ |  | Redacted to preserve confidentiality
Option 7A |  | $ |  | Redacted to preserve confidentiality
Option 7B |  | $ |  | Redacted to preserve confidentiality
Option 7C |  | $ |  | Redacted to preserve confidentiality
Option 7D |  | $ |  | Redacted to preserve confidentiality

## Timing sensitivity results
[8 empty] | 7D |  |  |  |  | 7D
NPV results - no change | [7 empty] | no change | 1 year delay | 2 year delay |  |  | no change | 1 year delay | 2 year delay
[6 empty] | 3 | no change | 2402.773 | 2401.8294 | 1930.0854 | 3 | no change | 258.4% | 258.3% | 227.2%
Option | Unit | Medium | High | Low | Weighted |  | 1 year forward | 539.2828 | 538.3392 | 66.5952 |  | 1 year forward | 116% | 115.9% | 102%
Option 3 | $NPV | 1383.4753 | 3399.5305 | -98.594 | 1516.9718 |  | 2 years forward | 69.1557 | 68.2121 | -403.5318 |  | 2 years forward | 101.8% | 101.8% | 89.52%
Option 7D | $NPV | 3625.4606 | 8468.3899 | -40.332 | 3919.7448
NPV results - 1 year NNO delay
Option | Unit | Medium | High | Low | Weighted
Option 3 | $NPV | 1383.4753 | 3399.5305 | -98.594 | 1516.9718
Option 7D | $NPV | 3628.9548 | 8453.396 | -36.1008 | 3918.8012
NPV results - 2 year NNO delay
Option | Unit | Medium | High | Low | Weighted
Option 3 | $NPV | 1383.4753 | 3399.5305 | -98.594 | 1516.9718
Option 7D | $NPV | 3208.4593 | 7403.4279 | -32.1176 | 3447.0572
NPV results - 2 year NNO delay, 1 year network components forward
Option | Unit | Medium | High | Low | Weighted
Option 3 | $NPV | 3141.9661 | 7342.6824 | -108.2575 | 3379.5893
Option 7D | $NPV | 3208.4593 | 7399.9371 | -32.1176 | 3446.1845
NPV results - 2 year NNO delay, 2 year network components forward
Option | Unit | Medium | High | Low | Weighted
Option 3 | $NPV | 3558.1693 | 8387.2565 | -108.2575 | 3848.8344
Option 7D | $NPV | 3208.4593 | 7396.4092 | -32.1176 | 3445.3026
NPV results - 1 year NNO delay, 2 year network components forward
Option | Unit | Medium | High | Low | Weighted
Option 3 | $NPV | 3558.1693 | 8387.2565 | -108.2575 | 3848.8344
Option 7D | $NPV | 3628.9548 | 8446.3773 | -36.1008 | 3917.0465
NPV results - 1 year NNO delay, 1 year network components forward
Option | Unit | Medium | High | Low | Weighted
Option 3 | $NPV | 3141.9661 | 7342.6824 | -108.2575 | 3379.5893
Option 7D | $NPV | 3628.9548 | 8449.9051 | -36.1008 | 3917.9285
NPV results - no delay, 1 year network components forward
Option | Unit | Medium | High | Low | Weighted
Option 3 | $NPV | 3141.9661 | 7342.6824 | -108.2575 | 3379.5893
Option 7D | $NPV | 3625.4606 | 8464.8991 | -40.332 | 3918.8721
NPV results - no delay, 2 year network components forward
Option | Unit | Medium | High | Low | Weighted
Option 3 | $NPV | 3558.1693 | 8387.2565 | -108.2575 | 3848.8344
Option 7D | $NPV | 3625.4606 | 8461.3713 | -40.332 | 3917.9901