## Overview of the model
North West Slopes PADR economic assessment
Legend applied throughout the model template
Table Row Name
Input Cell
Calculation cell
Parameter Cell
Output Cell

## Results
Scenarios |  |  |  |  | S1 | S2 | S3
General inputs and sensitivities |  |  |  | Unit | Central | Low | High
Commercial discount rate |  |  |  | % | 5.5% | 7.5% | 2.23%
VCR |  |  |  | $/MWh | 46931 | 32851.7 | 61010.3
Cost inputs and sensitivities |  |  |  | Unit | Central | Low | High
Network capital costs |  |  |  | Factor | 1 | 1.25 | 0.75
NNO capital costs |  |  |  | Factor | 1 | 1 | 1
Operating and maintenance costs |  |  |  | Factor | 1 | 1.25 | 0.75
Market benefit inputs and sensitivities |  |  |  | Unit | Central | Low | High
Avoided fuel consumption from generation dispatch |  |  |  | Factor | 1 | 0.7 | 1.3
Avoided voluntary load curtailment |  |  |  | Factor | 1 | 0.7 | 1.3
Avoided involuntary load shedding |  |  |  | Factor | 1 | 0.7 | 1.3
Avoided costs for non RIT-T proponent parties |  |  |  | Factor | 1 | 0.7 | 1.3
Avoided unrelated TNSP expenditure (wood pole replacement) |  |  |  | Factor | 1 | 0.7 | 1.3
Avoided unrelated TNSP expenditure (market benefits) |  |  |  | Factor | 1 | 0.7 | 1.3
Scenario weighting settings |  |  |  | Unit | Central | Low | High
Scenario weighting |  |  |  | % | 50% | 25% | 25%
NPV results
Option | Unit | Central | Low | High | Weighted | Rank | % from 1st
Option 1A | $NPV | 68.7429 | 10.0854 | 290.0547 | 109.4064 | 10 | 20.26%
Option 1B | $NPV | 331.615 | 10.0854 | 677.4638 | 337.6948 | 6 | 62.54%
Option 2A | $NPV | 107.9995 | -27.5123 | 284.2094 | 118.174 | 9 | 21.88%
Option 2B | $NPV | 194.1704 | -42.9161 | 400.4013 | 186.4565 | 7 | 34.53%
Option 2C | $NPV | 177.0042 | -27.4899 | 416.2898 | 185.7021 | 8 | 34.39%
Option 2D | $NPV | 52.0662 | -93.1316 | 244.5958 | 63.8992 | 11 | 11.83%
Option 3A | $NPV | 439.1746 | -21.096 | 784.0028 | 410.314 | 3 | 75.99%
Option 3B | $NPV | 381.3515 | -21.096 | 731.2864 | 368.2233 | 5 | 68.19%
Option 3C | $NPV | 419.1833 | -20.5088 | 773.4396 | 397.8243 | 4 | 73.67%
Option 5A | $NPV | 534.2383 | 0.91848 | 959.257 | 507.163 | 2 | 93.92%
Option 5B | $NPV | 566.9444 | 19.3535 | 1006.6905 | 539.9832 | 1 | 100%
S1 | Central | [10 empty] | S2 | Low | [10 empty] | S3 | High | [10 empty] | Weighted
NPV result | Central | [10 empty] | NPV result | Low | [10 empty] | NPV result | High | [10 empty] | NPV result | Weighted
NPV breakdown | Central | [10 empty] | NPV breakdown | Low | [10 empty] | NPV breakdown | High | [10 empty] | NPV breakdown | Weighted
Option | Option 1A | Option 1B | Option 2A | Option 2B | Option 2C | Option 2D | Option 3A | Option 3B | Option 3C | Option 5A | Option 5B | Option | Option 1A | Option 1B | Option 2A | Option 2B | Option 2C | Option 2D | Option 3A | Option 3B | Option 3C | Option 5A | Option 5B | Option | Option 1A | Option 1B | Option 2A | Option 2B | Option 2C | Option 2D | Option 3A | Option 3B | Option 3C | Option 5A | Option 5B | Option | Option 1A | Option 1B | Option 2A | Option 2B | Option 2C | Option 2D | Option 3A | Option 3B | Option 3C | Option 5A | Option 5B
TNSP capital costs | -166.4751 | -148.5616 | -101.7299 | -82.3869 | -124.1263 | -146.5436 | -89.3913 | -139.1237 | -109.3756 | Redacted to preserve confidentiality |  | TNSP capital costs | -65.4645 | -65.4645 | -57.8468 | -67.2678 | -57.8243 | -112.9502 | -76.3647 | -76.3647 | -75.7776 | Redacted to preserve confidentiality |  | TNSP capital costs | -110.4401 | -94.6454 | -65.8076 | -52.0866 | -77.3995 | -93.1834 | -56.5234 | -100.0878 | -66.8504 | Redacted to preserve confidentiality |  | TNSP capital costs | -127.2137 | -114.3083 | -81.7786 | -71.032 | -95.8691 | -124.8052 | -77.9177 | -113.675 | -90.3448 | Redacted to preserve confidentiality
NNO capital costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | NNO capital costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | NNO capital costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | NNO capital costs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality
TNSP operating expenditure | -43.029 | -32.1637 | -22.5359 | -17.6099 | -23.098 | -33.6556 | -24.6122 | -32.7029 | -24.6192 | Redacted to preserve confidentiality |  | TNSP operating expenditure | -14.2673 | -14.2673 | -7.6873 | -9.6738 | -7.6873 | -18.2031 | -17.0138 | -17.0138 | -17.0138 | Redacted to preserve confidentiality |  | TNSP operating expenditure | -46.5685 | -34.8915 | -24.8406 | -19.4066 | -25.5797 | -37.0783 | -26.5711 | -35.7231 | -26.8073 | Redacted to preserve confidentiality |  | TNSP operating expenditure | -36.7234 | -28.3716 | -19.3999 | -16.0751 | -19.8658 | -30.6482 | -23.2023 | -29.5356 | -23.2649 | Redacted to preserve confidentiality
TNSP payments to NNO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | TNSP payments to NNO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | TNSP payments to NNO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | TNSP payments to NNO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality
NNO operating expenditure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | NNO operating expenditure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | NNO operating expenditure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | NNO operating expenditure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality
Avoided fuel consumption from generation dispatch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | Avoided fuel consumption from generation dispatch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | Avoided fuel consumption from generation dispatch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | Avoided fuel consumption from generation dispatch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality
Avoided voluntary load curtailment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | Avoided voluntary load curtailment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | Avoided voluntary load curtailment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | Avoided voluntary load curtailment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality
Avoided involuntary load shedding outside of NW Slopes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | Avoided involuntary load shedding outside of NW Slopes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | Avoided involuntary load shedding outside of NW Slopes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | Avoided involuntary load shedding outside of NW Slopes | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality
Avoided involuntary load shedding in NW Slopes | 278.2469 | 512.3403 | 232.2654 | 293.5741 | 324.2285 | 232.2654 | 552.5733 | 552.5733 | 552.5733 | Redacted to preserve confidentiality |  | Avoided involuntary load shedding in NW Slopes | 89.8172 | 89.8172 | 38.0218 | 33.6268 | 38.0218 | 38.0218 | 71.8745 | 71.8745 | 71.8745 | Redacted to preserve confidentiality |  | Avoided involuntary load shedding in NW Slopes | 447.0633 | 807.0007 | 374.8576 | 471.1319 | 519.269 | 374.8576 | 866.3237 | 866.3237 | 866.3237 | Redacted to preserve confidentiality |  | Avoided involuntary load shedding in NW Slopes | 273.3436 | 480.3746 | 219.3525 | 272.9767 | 301.437 | 219.3525 | 510.8362 | 510.8362 | 510.8362 | Redacted to preserve confidentiality
Avoided costs for non RIT-T proponent parties | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | Avoided costs for non RIT-T proponent parties | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | Avoided costs for non RIT-T proponent parties | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | Avoided costs for non RIT-T proponent parties | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (wood pole replacement) | 0 | 0 | 0 | 0.59308 | 0 | 0 | 0.60469 | 0.60469 | 0.60469 | Redacted to preserve confidentiality |  | Avoided unrelated TNSP expenditure (wood pole replacement) | 0 | 0 | 0 | 0.39865 | 0 | 0 | 0.40799 | 0.40799 | 0.40799 | Redacted to preserve confidentiality |  | Avoided unrelated TNSP expenditure (wood pole replacement) | 0 | 0 | 0 | 0.76261 | 0 | 0 | 0.77357 | 0.77357 | 0.77357 | Redacted to preserve confidentiality |  | Avoided unrelated TNSP expenditure (wood pole replacement) | 0 | 0 | 0 | 0.58686 | 0 | 0 | 0.59773 | 0.59773 | 0.59773 | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (market benefits) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | Avoided unrelated TNSP expenditure (market benefits) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | Avoided unrelated TNSP expenditure (market benefits) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | Avoided unrelated TNSP expenditure (market benefits) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality
NNO receipts received from TNSP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | NNO receipts received from TNSP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | NNO receipts received from TNSP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality |  | NNO receipts received from TNSP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Redacted to preserve confidentiality
NPV | 68.7429 | 331.615 | 107.9995 | 194.1704 | 177.0042 | 52.0662 | 439.1746 | 381.3515 | 419.1833 | 534.2383 | 566.9444 | NPV | 10.0854 | 10.0854 | -27.5123 | -42.9161 | -27.4899 | -93.1316 | -21.096 | -21.096 | -20.5088 | 0.91848 | 19.3535 | NPV | 290.0547 | 677.4638 | 284.2094 | 400.4013 | 416.2898 | 244.5958 | 784.0028 | 731.2864 | 773.4396 | 959.257 | 1006.6905 | NPV | 109.4064 | 337.6948 | 118.174 | 186.4565 | 185.7021 | 63.8992 | 410.314 | 368.2233 | 397.8243 | 507.163 | 539.9832
Benefit time series | Central | [10 empty] | Benefit time series | Low | [10 empty] | Benefit time series | High | [10 empty] | Benefit time series | Weighted
Sensitivities 7.5.2 - 7.5.5
Option | Unit | Central | Low | High | Weighted | Rank
Option 1A | $NPV | 68.7429 | 10.0854 | 290.0547 | 109.4064 | 10
Option 1B | $NPV | 331.615 | 10.0854 | 677.4638 | 337.6948 | 6
Option 2A | $NPV | 107.9995 | -27.5123 | 284.2094 | 118.174 | 9
Option 2B | $NPV | 194.1704 | -42.9161 | 400.4013 | 186.4565 | 7
Option 2C | $NPV | 177.0042 | -27.4899 | 416.2898 | 185.7021 | 8
Option 2D | $NPV | 52.0662 | -93.1316 | 244.5958 | 63.8992 | 12
Option 3A | $NPV | 439.1746 | -21.096 | 784.0028 | 410.314 | 3
Option 3B | $NPV | 381.3515 | -21.096 | 731.2864 | 368.2233 | 5
Option 3C | $NPV | 419.1833 | -20.5088 | 773.4396 | 397.8243 | 4
Option 4 | $NPV | 85.5538 | -53.897 | 268.1602 | 96.3427 | 11
Option 5A | $NPV | 534.2383 | 0.91848 | 959.257 | 507.163 | 2
Option 5B | $NPV | 566.9444 | 19.3535 | 1006.6905 | 539.9832 | 1
Low demand forecast in central scenario
| Central | Sensitivity
Option 1A | 68.7429 | -67.3788
Option 1B | 331.615 | -38.5999
Option 2A | 107.9995 | -62.8508
Option 2B | 194.1704 | -45.0162
Option 2C | 177.0042 | -85.8094
Option 2D | 52.0662 | -118.7842
Option 3A | 439.1746 | 1.0945
Option 3B | 381.3515 | -56.7286
Option 3C | 419.1833 | -18.8968
Option 4 | 85.5538 | -85.2966
Option 5A | 534.2383 | 3.091
Option 5B | 566.9444 | 22.1494
Battery reinvestment costs
| Weighted | Sensitivity
Option 1A | 109.4064 | 109.4064
Option 1B | 337.6948 | 337.6948
Option 2A | 118.174 | 118.174
Option 2B | 186.4565 | 186.4565
Option 2C | 185.7021 | 185.7021
Option 2D | 63.8992 | 63.8992
Option 3A | 410.314 | 410.314
Option 3B | 368.2233 | 368.2233
Option 3C | 397.8243 | 397.8243
Option 4 | 96.3427 | 96.3427
Option 5A | 507.163 | 515.9395
Option 5B | 539.9832 | 546.4648
High capex
| Option 1A | 27.1241
| Option 1B | 294.4746
| Option 2A | 82.5671
| Option 2B | 173.5737
| Option 2C | 145.9726
| Option 2D | 15.4303
| Option 3A | 416.8267
| Option 3B | 346.5705
| Option 3C | 391.8394
| Option 4 | 55.4926
| Option 5A | 518.4428
| Option 5B | 551.1488
Low capex
| Option 1A | 110.3616
| Option 1B | 368.7554
| Option 2A | 133.432
| Option 2B | 214.7671
| Option 2C | 208.0357
| Option 2D | 88.7021
| Option 3A | 461.5224
| Option 3B | 416.1324
| Option 3C | 446.5272
| Option 4 | 115.6149
| Option 5A | 550.0339
| Option 5B | 582.7399
High discount rate
| Option 1A | 42.1012
| Option 1B | 279.4966
| Option 2A | 83.0756
| Option 2B | 161.2066
| Option 2C | 140.8494
| Option 2D | 27.9825
| Option 3A | 383.2981
| Option 3B | 331.717
| Option 3C | 362.1697
| Option 4 | 60.8116
| Option 5A | 473.352
| Option 5B | 500.7592
Low discount rate
| Option 1A | 134.5501
| Option 1B | 448.0539
| Option 2A | 167.4877
| Option 2B | 268.0458
| Option 2C | 262.1321
| Option 2D | 114.6697
| Option 3A | 556.5849
| Option 3B | 486.2964
| Option 3C | 542.5006
| Option 4 | 146.0888
| Option 5A | 660.2187
| Option 5B | 704.5881

## Chart tables (hidden)
Chart tables
First ranked option |  | Option 5B
Real
Option 5B | #REF! |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Option 5B | #REF! |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Option 5B | #REF! |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Option 5B | #REF! |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Discounted |  |  | 1 | 0.94787 | 0.89845 | 0.85161 | 0.80722 | 0.76513 | 0.72525 | 0.68744 | 0.6516 | 0.61763 | 0.58543 | 0.55491 | 0.52598 | 0.49856 | 0.47257 | 0.44793 | 0.42458 | 0.40245 | 0.38147 | 0.36158 | 0.34273 | 0.32486 | 0.30793 | 0.29187 | 0.27666 | 0.26223 | 0.24856 | 0.2356 | 0.22332 | 0.21168
Option 5B | #REF! |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Option 5B | #REF! |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Option 5B | #REF! |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
#REF! |  |  | #VALUE! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Option 5B | #REF! |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Discounted |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5B | #REF! |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
#REF! |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#REF! |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#REF! |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#REF! |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#REF! |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#REF! |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Option 5B | #REF! |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
#REF! |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#REF! |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#REF! |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#REF! |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#REF! |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#REF! |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Option 5B | #REF! |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
#REF! |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#REF! |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#REF! |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#REF! |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#REF! |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
#REF! |  |  | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Option 5B | #REF! |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! |  |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!

## General inputs
General parameter and option inputs
General parameters
Parameter | Unit | Value
First year of analysis | Year | 2022
Discount year | Year | 2022
Analysis period | Years | 20
Option inputs
Option | Stage | Short description of component
Base |  | No investment
Option 1A | 1 | Install 3rd Narrabri Tx
Option 1A | 1 | Upgrade 969 line to 160 MVA rating
Option 1A | 1 | Install +50 MVAr (capacitive) -20MVAr (inductive) SVC Gunnedah
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating
Option 1A | 1 | Upgrade 968 line to 160 MVA rating
Option 1A | 2 | Install +60 MVAr -20MVAr SVC at Narrabri
Option 1B | 1 | Install 3rd Narrabri Tx
Option 1B | 1 | Upgrade 969 line to 160 MVA rating
Option 1B | 1 | Install +50 MVAr (capacitive) -20MVAr (inductive) SVC Gunnedah
Option 1B | 1 | Upgrade 9UH line to 100 MVA rating
Option 1B | 2 | Build new 132 kV line between Tamworth and Narrabri
Option 2A | 1 | Install 3rd Narrabri Tx
Option 2A | 1 | Build new 160 MVA 132 kV line between Tamworth 330 and Gunnedah
Option 2A | 1 | Upgrade 969 line to 135 MVA rating
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating
Option 2A | 2 | Install +50 MVAr -20 MVAr SVC Narrabri 132
Option 2B | 1 | Install 3rd Narrabri Tx
Option 2B | 1 | Build new double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating
Option 2B | 2 | Install +50 MVAr -20 MVAr SVC Narrabri 132
Option 2C | 1 | Install 3rd Narrabri Tx
Option 2C | 1 | Build new 160 MVA 132 kV line between Tamworth 330 and Gunnedah
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating
Option 2C | 2 | Build new 132 kV line between Gunnedah and Narrabri
Option 2D | 1 | Install 3rd Narrabri Tx
Option 2D | 1 | Build new 330 kV line between Tamworth and Gunnedah operated at 132 kV
Option 2D | 1 | Upgrade 969 line to 135 MVA rating
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating
Option 2D | 2 | Install +50 MVAr -20 MVAr SVC Narrabri 132
Option 3A | 1 | Install 3rd Narrabri Tx
Option 3A | 1 | Rebuild 969 line as double circuit
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating
Option 3A | 2 | Install +60 MVAr -20MVAr SVC at Narrabri
Option 3B | 1 | Install 3rd Narrabri Tx
Option 3B | 1 | Rebuild 969 line as double circuit
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating
Option 3B | 2 | Install 50 MW (50 MWh) BESS at Narrabri 132
Option 3C | 1 | Install 3rd Narrabri Tx
Option 3C | 1 | Rebuild 969 line as double circuit
Option 3C | 2 | Build new 132 kV line between Gunnedah and Narrabri
Option 5A | 1 | Install 3rd Narrabri Tx
Option 5A | 1 | BESS
Option 5A | 2 | Rebuild 969 line as double circuit
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating
Option 5B | 1 | Install 3rd Narrabri Tx
Option 5B | 1 | BESS
Option 5B | 2 | Rebuild 969 line as double circuit
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating

## CBA inputs
CBA cost inputs
All years in the input sheet are expressed as financial years. ie 2022 refers to FY2021/22 that covers the period from 1 July 2021 to 30 June 2022
Capital costs |  |  | S1 | S2 | S3
Option name | Stage | Capex component | Commission year - central | Commission year - low | Commission year - high | Asset life | 1 if TNSP owns asset | Amount | Build year 1 | Build year 2 | Build year 3 | Build year 4 | Build year 5 | Build year 6
Option 1A | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 579744.0386 | 3465484.9208 | 4126950.7706
Option 1A | 1 | Upgrade 969 line to 160 MVA rating | 2026 | 2026 | 2026 | 35 | 1 | 50949682.23 | 466189.595 | 1313773.949 | 49169718.686
Option 1A | 1 | 50 MVAr SVC Gunnedah | 2026 | 2026 | 2026 | 40 | 1 | 18433159.02 | 1270571.3167 | 6682283.4849 | 10480304.2184
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating | 2029 | #N/A | 2029 | 35 | 1 | 38267169.36 | 188539.3946 | 188024.2644 | 536844.2295 | 590933.4024 | 27683721.36 | 9079106.7092
Option 1A | 1 | Upgrade 968 line to 160 MVA rating | 2028 | #N/A | 2028 | 35 | 1 | 148683015.7 | 906966.4008 | 1440809.2298 | 2842677.6499 | 97336044.2365 | 46156518.1829
Option 1A | 2 | 60 MVAr SVC at Narrabri | 2030 | #N/A | 2030 | 40 | 1 | 19661063.47 | 1047577.2064 | 6968417.1091 | 11645069.1544
Option 1B | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 579744.0386 | 3465484.9208 | 4126950.7706
Option 1B | 1 | Upgrade 969 line to 160 MVA rating | 2026 | 2026 | 2026 | 35 | 1 | 50949682.23 | 466189.595 | 1313773.949 | 49169718.686
Option 1B | 1 | 50 MVAr SVC Gunnedah | 2026 | 2026 | 2026 | 40 | 1 | 18433159.02 | 1270571.3167 | 6682283.4849 | 10480304.2184
Option 1B | 1 | Upgrade 9UH line | 2027 | #N/A | 2027 | 35 | 1 | 38267169.36 | 258001.2811 | 500494.2924 | 808645.708 | 36700028.0785
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 102474742 | 2908464 | 8324816 | 14915149 | 28412076 | 40615937 | 7298300
Option 2A | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 579744.0386 | 3465484.9208 | 4126950.7706
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 2029 | 2029 | 2029 | 50 | 1 | 46979527.87 | 304770.178 | 540678.4002 | 15488846.5297 | 11723872.4983 | 17921537.2786 | 999822.9853
Option 2A | 1 | Upgrade 969 line to 135 MVA rating | 2028 | #N/A | 2028 | 35 | 1 | 50949682.21 | 290073.5228 | 384387.0441 | 909168.7657 | 11910563.8167 | 37455489.0607
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating | 2029 | #N/A | 2029 | 35 | 1 | 38267169.38 | 175072.3038 | 174593.965 | 436997.4065 | 548723.8766 | 9553535.5044 | 27378246.3238
Option 2A | 2 | 50 MVAr SVC Narrabri 132 | 2030 | #N/A | 2030 | 40 | 1 | 19661063 | 1047577 | 6968417 | 11645069
Option 2B | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 579744.0386 | 3465484.9208 | 4126950.7706
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 2029 | 2029 | 2029 | 50 | 1 | 62070491.37 | 320034.0032 | 571518.4188 | 15432611.1821 | 12294119.0011 | 28721538.8356 | 4730669.9292
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating | 2028 | #N/A | 2028 | 35 | 1 | 38267169.38 | 217867.7512 | 288704.5415 | 682856.3841 | 8945758.697 | 28131982.0061
Option 2B | 2 | 50 MVAr SVC Narrabri 132 | 2030 | #N/A | 2030 | 40 | 1 | 19661063 | 1047577 | 6968417 | 11645069
Option 2C | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 579744.0386 | 3465484.9208 | 4126950.7706
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 2029 | 2029 | 2029 | 50 | 1 | 46979527.87 | 299740.7353 | 530361.4973 | 15403787.3431 | 11638033.0977 | 18079886.6859 | 1027718.5108
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating | 2028 | #N/A | 2028 | 35 | 1 | 50949682.21 | 290073.5228 | 384387.0441 | 909168.7657 | 11910563.8167 | 37455489.0607
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 67112099 | 2061255 | 5874755 | 11012628 | 13927173 | 32722750 | 1513538
Option 2D | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 579744.0386 | 3465484.9208 | 4126950.7706
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 2029 | 2029 | 2029 | 50 | 1 | 126867927.18 | 367611.5549 | 900058.0332 | 19402788.6187 | 18887254.8947 | 84355949.4593 | 2954264.6191
Option 2D | 1 | Upgrade 969 line to 135 MVA rating | 2028 | #N/A | 2028 | 35 | 1 | 50949682.21 | 290073.5228 | 384387.0441 | 909168.7657 | 11910563.8167 | 37455489.0607
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating | 2028 | #N/A | 2028 | 35 | 1 | 38267169.38 | 217867.7512 | 288704.5415 | 682856.3841 | 8945758.697 | 28131982.0061
Option 2D | 2 | 50 MVAr SVC Narrabri 132 | 2030 | #N/A | 2030 | 40 | 1 | 19661063 | 1047577 | 6968417 | 11645069
Option 3A | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 579744.0386 | 3465484.9208 | 4126950.7706
Option 3A | 1 | Rebuild 969 line as double circuit | 2027 | 2027 | 2027 | 50 | 1 | 93863549.26 | 1066900.8057 | 2677884.0458 | 23319227.1721 | 66799537.2363
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating | 2028 | #N/A | 2028 | 35 | 1 | 38267169.37 | 222819.2901 | 314834.4414 | 698375.8392 | 12858725.5815 | 24172414.2178
Option 3A | 2 | 60 MVAr SVC at Narrabri 132 | 2030 | #N/A | 2030 | 40 | 1 | 19661063 | 1047577 | 6968417 | 11645069
Option 3B | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 579744.0386 | 3465484.9208 | 4126950.7706
Option 3B | 1 | Rebuild 969 line as double circuit | 2027 | 2027 | 2027 | 50 | 1 | 93863549.26 | 1066900.8057 | 2677884.0458 | 23319227.1721 | 66799537.2363
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating | 2028 | #N/A | 2028 | 35 | 1 | 38267169.37 | 222819.2901 | 314834.4414 | 698375.8392 | 12858725.5815 | 24172414.2178
Option 3B | 2 | Install 50 MW (50 MWh) BESS at Narrabri 132 | 2030 | #N/A | 2030 | 15 | 1 | 87940861 | 3715501 | 23997962 | 58524277 | 1703121
Option 3C | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 579744.0386 | 3465484.9208 | 4126950.7706
Option 3C | 1 | Rebuild 969 line as double circuit | 2027 | 2027 | 2027 | 50 | 1 | 93863549.24 | 1039451.6631 | 2462340.6453 | 15490781.9213 | 74870975.0103
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 67112099 | 2061255 | 5874755 | 11012628 | 13927173 | 32722750 | 1513538
Option 5A | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 579744.0386 | 3465484.9208 | 4126950.7706
Option 5A | 1 | BESS | Redacted to preserve confidentiality |  |  |  | 0 |  | Redacted to preserve confidentiality
Option 5A | 2 | Rebuild 969 line as double circuit | 2030 | #N/A | 2030 | 50 | 1 | 93863549.26 | 1066900.8057 | 2677884.0458 | 23319227.1721 | 66799537.2363
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating | 2030 | #N/A | 2030 | 35 | 1 | 38267169.37 | 222819.2901 | 314834.4414 | 698375.8392 | 12858725.5815 | 24172414.2178
Option 5B | 1 | 3rd Narrabri Tx | 2026 | 2026 | 2026 | 40 | 1 | 8172179.73 | 579744.0386 | 3465484.9208 | 4126950.7706
Option 5B | 1 | BESS | Redacted to preserve confidentiality |  |  |  | 0 |  | Redacted to preserve confidentiality
Option 5B | 2 | Rebuild 969 line as double circuit | 2030 | #N/A | 2030 | 50 | 1 | 93863549.26 | 1066900.8057 | 2677884.0458 | 23319227.1721 | 66799537.2363
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating | 2030 | #N/A | 2030 | 35 | 1 | 38267169.37 | 222819.2901 | 314834.4414 | 698375.8392 | 12858725.5815 | 24172414.2178
Biodiversity offset costs
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 12600000 | 0 | 0 | 0 | 12600000 | 0 | 0
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 2029 | 2029 | 2029 | 50 | 1 | 8100000 | 0 | 0 | 0 | 8100000 | 0 | 0
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 2029 | 2029 | 2029 | 50 | 1 | 8100000 | 0 | 0 | 0 | 8100000 | 0 | 0
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 2029 | 2029 | 2029 | 50 | 1 | 8100000 | 0 | 0 | 0 | 8100000 | 0 | 0
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 15800000 | 0 | 0 | 0 | 15800000 | 0 | 0
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 2029 | 2029 | 2029 | 50 | 1 | 8100000 | 0 | 0 | 0 | 8100000 | 0 | 0
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 15800000 | 0 | 0 | 0 | 15800000 | 0 | 0
Option 4 | 1 | 132 kV line between NETI and Gunnedah 132 kV | 2029 | 2029 | 2029 | 50 | 1 | 10580000 | 0 | 0 | 0 | 10580000 | 0 | 0
Property allowances
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 44720000 | 0 | 0 | 0 | 0 | 0 | 44720000
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 2029 | 2029 | 2029 | 50 | 1 | 19200000 | 0 | 0 | 0 | 0 | 19200000 | 0
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 2029 | 2029 | 2029 | 50 | 1 | 19200000 | 0 | 0 | 0 | 0 | 19200000 | 0
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 2029 | 2029 | 2029 | 50 | 1 | 19200000 | 0 | 0 | 0 | 0 | 19200000 | 0
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 23140000 | 0 | 0 | 0 | 0 | 23140000 | 0
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 2029 | 2029 | 2029 | 50 | 1 | 24340000 | 0 | 0 | 0 | 0 | 24340000 | 0
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 2030 | #N/A | 2030 | 50 | 1 | 23140000 | 0 | 0 | 0 | 0 | 23140000 | 0
Option 4 | 1 | 132 kV line between NETI and Gunnedah 132 kV | 2029 | 2029 | 2029 | 50 | 1 | 21000000 | 0 | 0 | 0 | 0 | 21000000 | 0
Operating and maintenance costs
Option | Stage | Capex component |  | TNSP owned | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  |  |  | $
Option 1A | 1 | 3rd Narrabri Tx |  | 1 | $ | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946
Option 1A | 1 | Upgrade 969 line to 160 MVA rating |  | 1 | $ | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446
Option 1A | 1 | 50 MVAr SVC Gunnedah |  | 1 | $ | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating |  | 1 | $ | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872
Option 1A | 1 | Upgrade 968 line to 160 MVA rating |  | 1 | $ | 2973660.314 | 2973660.314 | 2973660.314 | 2973660.314 | 2973660.314 | 2973660.314 | 2973660.314 | 2973660.314 | 2973660.314 | 2973660.314 | 2973660.314 | 2973660.314 | 2973660.314 | 2973660.314 | 2973660.314 | 2973660.314 | 2973660.314 | 2973660.314 | 2973660.314 | 2973660.314
Option 1A | 2 | 60 MVAr SVC at Narrabri |  | 1 | $ | 393221.2694 | 393221.2694 | 393221.2694 | 393221.2694 | 393221.2694 | 393221.2694 | 393221.2694 | 393221.2694 | 393221.2694 | 393221.2694 | 393221.2694 | 393221.2694 | 393221.2694 | 393221.2694 | 393221.2694 | 393221.2694 | 393221.2694 | 393221.2694 | 393221.2694 | 393221.2694
Option 1B | 1 | 3rd Narrabri Tx |  | 1 | $ | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946
Option 1B | 1 | Upgrade 969 line to 160 MVA rating |  | 1 | $ | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446 | 1018993.6446
Option 1B | 1 | 50 MVAr SVC Gunnedah |  | 1 | $ | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804 | 368663.1804
Option 1B | 1 | Upgrade 9UH line |  | 1 | $ | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872 | 765343.3872
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri |  | 1 | $ | 2049494.84 | 2049494.84 | 2049494.84 | 2049494.84 | 2049494.84 | 2049494.84 | 2049494.84 | 2049494.84 | 2049494.84 | 2049494.84 | 2049494.84 | 2049494.84 | 2049494.84 | 2049494.84 | 2049494.84 | 2049494.84 | 2049494.84 | 2049494.84 | 2049494.84 | 2049494.84
Option 2A | 1 | 3rd Narrabri Tx |  | 1 | $ | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah |  | 1 | $ | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574
Option 2A | 1 | Upgrade 969 line to 135 MVA rating |  | 1 | $ | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating |  | 1 | $ | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876
Option 2A | 2 | 50 MVAr SVC Narrabri 132 |  | 1 | $ | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26
Option 2B | 1 | 3rd Narrabri Tx |  | 1 | $ | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line |  | 1 | $ | 1241409.8274 | 1241409.8274 | 1241409.8274 | 1241409.8274 | 1241409.8274 | 1241409.8274 | 1241409.8274 | 1241409.8274 | 1241409.8274 | 1241409.8274 | 1241409.8274 | 1241409.8274 | 1241409.8274 | 1241409.8274 | 1241409.8274 | 1241409.8274 | 1241409.8274 | 1241409.8274 | 1241409.8274 | 1241409.8274
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating |  | 1 | $ | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876
Option 2B | 2 | 50 MVAr SVC Narrabri 132 |  | 1 | $ | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26
Option 2C | 1 | 3rd Narrabri Tx |  | 1 | $ | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah |  | 1 | $ | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574 | 939590.5574
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating |  | 1 | $ | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri |  | 1 | $ | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98
Option 2D | 1 | 3rd Narrabri Tx |  | 1 | $ | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV |  | 1 | $ | 2537358.5436 | 2537358.5436 | 2537358.5436 | 2537358.5436 | 2537358.5436 | 2537358.5436 | 2537358.5436 | 2537358.5436 | 2537358.5436 | 2537358.5436 | 2537358.5436 | 2537358.5436 | 2537358.5436 | 2537358.5436 | 2537358.5436 | 2537358.5436 | 2537358.5436 | 2537358.5436 | 2537358.5436 | 2537358.5436
Option 2D | 1 | Upgrade 969 line to 135 MVA rating |  | 1 | $ | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442 | 1018993.6442
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating |  | 1 | $ | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876 | 765343.3876
Option 2D | 2 | 50 MVAr SVC Narrabri 132 |  | 1 | $ | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26
Option 3A | 1 | 3rd Narrabri Tx |  | 1 | $ | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946
Option 3A | 1 | Rebuild 969 line as double circuit |  | 1 | $ | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating |  | 1 | $ | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874
Option 3A | 2 | 60 MVAr SVC at Narrabri 132 |  | 1 | $ | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26 | 393221.26
Option 3B | 1 | 3rd Narrabri Tx |  | 1 | $ | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946
Option 3B | 1 | Rebuild 969 line as double circuit |  | 1 | $ | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852 | 1877270.9852
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating |  | 1 | $ | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874 | 765343.3874
Option 3B | 2 | Install 50 MW (50 MWh) BESS at Narrabri 132 |  | 1 | $ | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22
Option 3B | 2 | 3rd Narrabri Tx |  | 1 | $ | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22 | 1758817.22
Option 3C | 1 | Rebuild 969 line as double circuit |  | 1 | $ | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946 | 163443.5946
Option 3C | 1 | New 132 kV line between Gunnedah and Narrabri |  | 1 | $ | 1877270.9848 | 1877270.9848 | 1877270.9848 | 1877270.9848 | 1877270.9848 | 1877270.9848 | 1877270.9848 | 1877270.9848 | 1877270.9848 | 1877270.9848 | 1877270.9848 | 1877270.9848 | 1877270.9848 | 1877270.9848 | 1877270.9848 | 1877270.9848 | 1877270.9848 | 1877270.9848 | 1877270.9848 | 1877270.9848
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri |  | 1 | $ | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98 | 1342241.98
Option 5A | 1 | 3rd Narrabri Tx |  | 1 | $ | Redacted to preserve confidentiality
Option 5A | 1 | BESS |  | 0 | $ | Redacted to preserve confidentiality
Option 5A | 2 | Rebuild 969 line as double circuit |  | 1 | $ | Redacted to preserve confidentiality
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating |  | 1 | $ | Redacted to preserve confidentiality
Option 5B | 1 | 3rd Narrabri Tx |  | 1 | $ | Redacted to preserve confidentiality
Option 5B | 1 | BESS |  | 0 | $ | Redacted to preserve confidentiality
Option 5B | 2 | Rebuild 969 line as double circuit |  | 1 | $ | Redacted to preserve confidentiality
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating |  | 1 | $ | Redacted to preserve confidentiality
0 | 0 | 0 |  | 0 | $
0 | 0 | 0 |  | 0 | $
0 | 0 | 0 |  | 0 | $
0 | 0 | 0 |  | 0 | $
0 | 0 | 0 |  | 0 | $
0 | 0 | 0 |  | 0 | $
0 | 0 | 0 |  | 0 | $
0 | 0 | 0 |  | 0 | $
TSNP network service payments to NNO proponents
Option |  |  |  |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  |  |  | $
Option 1A |  |  |  |  | $
Option 1B |  |  |  |  | $
Option 2A |  |  |  |  | $
Option 2B |  |  |  |  | $
Option 2C |  |  |  |  | $
Option 2D |  |  |  |  | $
Option 3A |  |  |  |  | $
Option 3B |  |  |  |  | $
Option 3C |  |  |  |  | $
Option 5A |  |  |  |  | $ | Redacted to preserve confidentiality
Option 5B |  |  |  |  | $ | Redacted to preserve confidentiality
NNO proponent receipts from TSNP
Option |  |  |  |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  |  |  | $
Option 1A |  |  |  |  | $
Option 1B |  |  |  |  | $
Option 2A |  |  |  |  | $
Option 2B |  |  |  |  | $
Option 2C |  |  |  |  | $
Option 2D |  |  |  |  | $
Option 3A |  |  |  |  | $
Option 3B |  |  |  |  | $
Option 3C |  |  |  |  | $
Option 5A |  |  |  |  | $ | Redacted to preserve confidentiality
Option 5B |  |  |  |  | $ | Redacted to preserve confidentiality
CBA benefit inputs
Avoided fuel consumption from generation dispatch
Option name |  |  |  |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  |  |  | $
Option 1A |  |  |  |  | $
Option 1B |  |  |  |  | $
Option 2A |  |  |  |  | $
Option 2B |  |  |  |  | $
Option 2C |  |  |  |  | $
Option 2D |  |  |  |  | $
Option 3A |  |  |  |  | $
Option 3B |  |  |  |  | $
Option 3C |  |  |  |  | $
Option 5A |  |  |  |  | $ | Redacted to preserve confidentiality
Option 5B |  |  |  |  | $ | Redacted to preserve confidentiality
Avoided voluntary load curtailment
Option name |  |  |  |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  |  |  | $
Option 1A |  |  |  |  | $
Option 1B |  |  |  |  | $
Option 2A |  |  |  |  | $
Option 2B |  |  |  |  | $
Option 2C |  |  |  |  | $
Option 2D |  |  |  |  | $
Option 3A |  |  |  |  | $
Option 3B |  |  |  |  | $
Option 3C |  |  |  |  | $
Option 5A |  |  |  |  | $ | Redacted to preserve confidentiality
Option 5B |  |  |  |  | $ | Redacted to preserve confidentiality
Avoided involuntary load shedding outside of NW Slopes
Option name |  |  |  |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  |  |  | $
Option 1A |  |  |  |  | $
Option 1B |  |  |  |  | $
Option 2A |  |  |  |  | $
Option 2B |  |  |  |  | $
Option 2C |  |  |  |  | $
Option 2D |  |  |  |  | $
Option 3A |  |  |  |  | $
Option 3B |  |  |  |  | $
Option 3C |  |  |  |  | $
Option 5A |  |  |  |  | $ | Redacted to preserve confidentiality
Option 5B |  |  |  |  | $ | Redacted to preserve confidentiality
Avoided involuntary load shedding in NW Slopes
Option name |  | S1 | Central |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  |  |  | MWh | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 4384.9586 | 4503.1613 | 6249.1594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1A |  |  |  |  | MWh | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 4384.9586 | 2251.5807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  |  | MWh | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  |  | MWh | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 4384.9586 | 3602.5291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  |  | MWh | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 4384.9586 | 1801.2645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  |  | MWh | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 4384.9586 | 900.6323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  |  | MWh | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 4384.9586 | 3602.5291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  |  | MWh | 0 | 23.049 | 64.8147 | 433.7698 | 3186.0645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  |  | MWh | 0 | 23.049 | 64.8147 | 433.7698 | 3186.0645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  |  | MWh | 0 | 23.049 | 64.8147 | 433.7698 | 3186.0645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  |  | MWh | Redacted to preserve confidentiality
Option 5B |  |  |  |  | MWh | Redacted to preserve confidentiality
Option name |  | S2 | Low |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  |  |  | MWh | 0 | 0 | 0 | 92.2972 | 972.526 | 1025.9467 | 1032.3356 | 1032.3356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1A |  |  |  |  | MWh | 0 | 0 | 0 | 92.2972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  |  | MWh | 0 | 0 | 0 | 92.2972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  |  | MWh | 0 | 0 | 0 | 92.2972 | 972.526 | 1025.9467 | 206.4671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  |  | MWh | 0 | 0 | 0 | 92.2972 | 972.526 | 1025.9467 | 412.9342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  |  | MWh | 0 | 0 | 0 | 92.2972 | 972.526 | 1025.9467 | 206.4671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  |  | MWh | 0 | 0 | 0 | 92.2972 | 972.526 | 1025.9467 | 206.4671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  |  | MWh | 0 | 0 | 0 | 92.2972 | 729.3945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  |  | MWh | 0 | 0 | 0 | 92.2972 | 729.3945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  |  | MWh | 0 | 0 | 0 | 92.2972 | 729.3945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  |  | MWh | Redacted to preserve confidentiality
Option 5B |  |  |  |  | MWh | Redacted to preserve confidentiality
Option name |  | S3 | High |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  |  |  | MWh | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 4384.9586 | 4503.1613 | 6249.1594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1A |  |  |  |  | MWh | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 4384.9586 | 2251.5807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  |  | MWh | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  |  | MWh | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 4384.9586 | 3602.5291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  |  | MWh | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 4384.9586 | 1801.2645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  |  | MWh | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 4384.9586 | 900.6323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  |  | MWh | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 4384.9586 | 3602.5291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  |  | MWh | 0 | 23.049 | 64.8147 | 433.7698 | 3186.0645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  |  | MWh | 0 | 23.049 | 64.8147 | 433.7698 | 3186.0645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  |  | MWh | 0 | 23.049 | 64.8147 | 433.7698 | 3186.0645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  |  | MWh | Redacted to preserve confidentiality
Option 5B |  |  |  |  | MWh | Redacted to preserve confidentiality
Option name |  | S4 | 0 |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1A |  |  |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 4 |  |  |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5B |  |  |  |  | MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoided costs for non RIT-T proponent parties
Option name |  |  |  |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  |  |  | $
Option 5A |  |  |  |  | $ | Redacted to preserve confidentiality
Option 5B |  |  |  |  | $ | Redacted to preserve confidentiality
Option name |  | S2 | Low |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 1A |  |  |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 1B |  |  |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 2A |  |  |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 2B |  |  |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 2C |  |  |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 2D |  |  |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 3A |  |  |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 3B |  |  |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 3C |  |  |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 4 |  |  |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 5A |  |  |  |  | $ |  | 646336043.7571 | 2233755490.6357 | 3651706179.4703 | 5220239693.2638 | 5260498419.1359 | 7555876248.6694 | 7810890107.425 | 5169758809.8905 | 1792511240.9768 | 1283668173.3394 | 4377947167.4037 | 6487440094.5777 | 4008964925.0482 | 13568040587.1763 | 6907014740.7582 | 12482410381.7222 | 3209262068.7746 | 1467014509.7441 | 2563209475.0998
Option 5B |  |  |  |  | $ |  | 646332703.2554 | 2233758695.5106 | 3652488995.3589 | 5215665240.626 | 5264693083.5836 | 7551909827.578 | 7831745972.7964 | 5170385831.3106 | 1792169934.0839 | 1268515173.6863 | 4387124275.5625 | 6487350871.6023 | 4007840293.4182 | 13570076604.634 | 6907035903.0056 | 12482479380.0909 | 3211015298.3284 | 1466120496.8396 | 2563053854.3829
Option name |  | S3 | High |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 1A |  |  |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 1B |  |  |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 2A |  |  |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 2B |  |  |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 2C |  |  |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 2D |  |  |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 3A |  |  |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 3B |  |  |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 3C |  |  |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 4 |  |  |  |  | $ |  | 646338593.6665 | 2233745194.5906 | 3642433494.8213 | 5248591283.7671 | 5205066394.451 | 7580981675.288 | 7858359432.9438 | 5184736438.7015 | 1794420113.3187 | 1252198868.4719 | 4468044545.0252 | 6487761425.6506 | 4011420252.1721 | 13557627995.4011 | 6911117720.5983 | 12489445213.4444 | 3206147013.2838 | 1463692645.2204 | 2562839389.4418
Option 5A |  |  |  |  | $ |  | 646336043.7571 | 2233755490.6357 | 3651706179.4703 | 5220239693.2638 | 5260498419.1359 | 7555876248.6694 | 7810890107.425 | 5169758809.8905 | 1792511240.9768 | 1283668173.3394 | 4377947167.4037 | 6487440094.5777 | 4008964925.0482 | 13568040587.1763 | 6907014740.7582 | 12482410381.7222 | 3209262068.7746 | 1467014509.7441 | 2563209475.0998
Option 5B |  |  |  |  | $ |  | 646332703.2554 | 2233758695.5106 | 3652488995.3589 | 5215665240.626 | 5264693083.5836 | 7551909827.578 | 7831745972.7964 | 5170385831.3106 | 1792169934.0839 | 1268515173.6863 | 4387124275.5625 | 6487350871.6023 | 4007840293.4182 | 13570076604.634 | 6907035903.0056 | 12482479380.0909 | 3211015298.3284 | 1466120496.8396 | 2563053854.3829
Option name |  | S4 | 0 |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  |  |  | $
Option 1A |  |  |  |  | $
Option 1B |  |  |  |  | $
Option 2A |  |  |  |  | $
Option 2B |  |  |  |  | $
Option 2C |  |  |  |  | $
Option 2D |  |  |  |  | $
Option 3A |  |  |  |  | $
Option 3B |  |  |  |  | $
Option 3C |  |  |  |  | $
Option 4 |  |  |  |  | $
Option 5A |  |  |  |  | $
Option 5B |  |  |  |  | $
Avoided unrelated TNSP expenditure (wood pole replacement)
Option name |  | S1 | Central |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172
Option 1A |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172
Option 1B |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172
Option 2A |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172
Option 2B |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172
Option 2D |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172
Option 3A |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  |  | $ | Redacted to preserve confidentiality
Option 5B |  |  |  |  | $ | Redacted to preserve confidentiality
Option name |  | S2 | Low |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 9925.0392 | 9925.0392 | 9925.0392 | 9925.0392 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 466476.8436
Option 1A |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 9925.0392 | 9925.0392 | 9925.0392 | 9925.0392 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 466476.8436
Option 1B |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 9925.0392 | 9925.0392 | 9925.0392 | 9925.0392 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 466476.8436
Option 2A |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 9925.0392 | 9925.0392 | 9925.0392 | 9925.0392 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 466476.8436
Option 2B |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 9925.0392 | 9925.0392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 9925.0392 | 9925.0392 | 9925.0392 | 9925.0392 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 466476.8436
Option 2D |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 9925.0392 | 9925.0392 | 9925.0392 | 9925.0392 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 466476.8436
Option 3A |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  |  | $ | Redacted to preserve confidentiality
Option 5B |  |  |  |  | $ | Redacted to preserve confidentiality
Option name |  | S3 | High |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 4755.7834 | 4755.7834 | 4755.7834 | 4755.7834 | 33290.4841 | 33290.4841 | 33290.4841 | 33290.4841 | 33290.4841 | 85604.1019 | 85604.1019 | 85604.1019 | 85604.1019 | 85604.1019 | 223521.8217
Option 1A |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 4755.7834 | 4755.7834 | 4755.7834 | 4755.7834 | 33290.4841 | 33290.4841 | 33290.4841 | 33290.4841 | 33290.4841 | 85604.1019 | 85604.1019 | 85604.1019 | 85604.1019 | 85604.1019 | 223521.8217
Option 1B |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 4755.7834 | 4755.7834 | 4755.7834 | 4755.7834 | 33290.4841 | 33290.4841 | 33290.4841 | 33290.4841 | 33290.4841 | 85604.1019 | 85604.1019 | 85604.1019 | 85604.1019 | 85604.1019 | 223521.8217
Option 2A |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 4755.7834 | 4755.7834 | 4755.7834 | 4755.7834 | 33290.4841 | 33290.4841 | 33290.4841 | 33290.4841 | 33290.4841 | 85604.1019 | 85604.1019 | 85604.1019 | 85604.1019 | 85604.1019 | 223521.8217
Option 2B |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 4755.7834 | 4755.7834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 4755.7834 | 4755.7834 | 4755.7834 | 4755.7834 | 33290.4841 | 33290.4841 | 33290.4841 | 33290.4841 | 33290.4841 | 85604.1019 | 85604.1019 | 85604.1019 | 85604.1019 | 85604.1019 | 223521.8217
Option 2D |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 4755.7834 | 4755.7834 | 4755.7834 | 4755.7834 | 33290.4841 | 33290.4841 | 33290.4841 | 33290.4841 | 33290.4841 | 85604.1019 | 85604.1019 | 85604.1019 | 85604.1019 | 85604.1019 | 223521.8217
Option 3A |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  |  | $ | Redacted to preserve confidentiality
Option 5B |  |  |  |  | $ | Redacted to preserve confidentiality
Option name |  | S4 | 0 |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  |  |  | $
Option 1A |  |  |  |  | $
Option 1B |  |  |  |  | $
Option 2A |  |  |  |  | $
Option 2B |  |  |  |  | $
Option 2C |  |  |  |  | $
Option 2D |  |  |  |  | $
Option 3A |  |  |  |  | $
Option 3B |  |  |  |  | $
Option 3C |  |  |  |  | $
Option 4 |  |  |  |  | $
Option 5A |  |  |  |  | $
Option 5B |  |  |  |  | $
Avoided unrelated TNSP expenditure (market benefits)
Option name |  |  |  |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  |  |  | $
Option 1A |  |  |  |  | $
Option 1B |  |  |  |  | $
Option 2A |  |  |  |  | $
Option 2B |  |  |  |  | $
Option 2C |  |  |  |  | $
Option 2D |  |  |  |  | $
Option 3A |  |  |  |  | $
Option 3B |  |  |  |  | $
Option 3C |  |  |  |  | $
Option 5A |  |  |  |  | $ | Redacted to preserve confidentiality
Option 5B |  |  |  |  | $ | Redacted to preserve confidentiality
Full unserved energy inputs under core assumptions (ie, not zeroed out after 2028/29, as outlined in section 6.1 of the PADR)
Option name |  |  |  |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  |  |  | $ | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 4384.9586 | 4503.1613 | 6249.1594 | 13404.3707 | 13461.5673 | 13483.3135 | 13560.4619 | 13563.1915 | 13566.6936 | 13492.2464 | 13192.64 | 13474.257 | 13531.4007 | 13724.2337 | 15197.3363
Option 1A |  |  |  |  | $ | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 4384.9586 | 2251.5807 | 0
Option 1B |  |  |  |  | $ | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 0 | 0 | 0
Option 2A |  |  |  |  | $ | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 4384.9586 | 3602.5291 | 0
Option 2B |  |  |  |  | $ | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 4384.9586 | 1801.2645 | 0
Option 2C |  |  |  |  | $ | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 4384.9586 | 900.6323 | 0
Option 2D |  |  |  |  | $ | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 4384.9586 | 3602.5291 | 0
Option 3A |  |  |  |  | $ | 0 | 23.049 | 64.8147 | 433.7698 | 3186.0645 | 0 | 0 | 0
Option 3B |  |  |  |  | $ | 0 | 23.049 | 64.8147 | 433.7698 | 3186.0645 | 0 | 0 | 0
Option 3C |  |  |  |  | $ | 0 | 23.049 | 64.8147 | 433.7698 | 3186.0645 | 0 | 0 | 0
Option 5A |  |  |  |  | $ | Redacted to preserve confidentiality
Option 5B |  |  |  |  | $ | Redacted to preserve confidentiality
Option name |  |  |  |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  |  |  | $ | 0 | 0 | 0 | 92.2972 | 972.526 | 1025.9467 | 1032.3356 | 1032.3356 | 1032.3356 | 1032.3356 | 1032.3356 | 1032.3356 | 1032.3356 | 1032.3356 | 1032.3356 | 1032.3356 | 1032.3356 | 1032.3356 | 1032.3356 | 1032.3356
Option 1A |  |  |  |  | $ | 0 | 0 | 0 | 92.2972 | 0 | 0 | 0 | 0
Option 1B |  |  |  |  | $ | 0 | 0 | 0 | 92.2972 | 0 | 0 | 0 | 0
Option 2A |  |  |  |  | $ | 0 | 0 | 0 | 92.2972 | 972.526 | 1025.9467 | 206.4671 | 0
Option 2B |  |  |  |  | $ | 0 | 0 | 0 | 92.2972 | 972.526 | 1025.9467 | 412.9342 | 0
Option 2C |  |  |  |  | $ | 0 | 0 | 0 | 92.2972 | 972.526 | 1025.9467 | 206.4671 | 0
Option 2D |  |  |  |  | $ | 0 | 0 | 0 | 92.2972 | 972.526 | 1025.9467 | 206.4671 | 0
Option 3A |  |  |  |  | $ | 0 | 0 | 0 | 92.2972 | 729.3945 | 0 | 0 | 0
Option 3B |  |  |  |  | $ | 0 | 0 | 0 | 92.2972 | 729.3945 | 0 | 0 | 0
Option 3C |  |  |  |  | $ | 0 | 0 | 0 | 92.2972 | 729.3945 | 0 | 0 | 0
Option 5A |  |  |  |  | $ | Redacted to preserve confidentiality
Option 5B |  |  |  |  | $ | Redacted to preserve confidentiality
Option name |  |  |  |  | Unit | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Base |  |  |  |  | $ | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 4384.9586 | 4503.1613 | 6249.1594 | 13404.3707 | 13461.5673 | 13483.3135 | 13560.4619 | 13563.1915 | 13566.6936 | 13492.2464 | 13192.64 | 13474.257 | 13531.4007 | 13724.2337 | 15197.3363
Option 1A |  |  |  |  | $ | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 4384.9586 | 2251.5807 | 0
Option 1B |  |  |  |  | $ | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 0 | 0 | 0
Option 2A |  |  |  |  | $ | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 4384.9586 | 3602.5291 | 0
Option 2B |  |  |  |  | $ | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 4384.9586 | 1801.2645 | 0
Option 2C |  |  |  |  | $ | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 4384.9586 | 900.6323 | 0
Option 2D |  |  |  |  | $ | 0 | 23.049 | 64.8147 | 433.7698 | 4248.086 | 4384.9586 | 3602.5291 | 0
Option 3A |  |  |  |  | $ | 0 | 23.049 | 64.8147 | 433.7698 | 3186.0645 | 0 | 0 | 0
Option 3B |  |  |  |  | $ | 0 | 23.049 | 64.8147 | 433.7698 | 3186.0645 | 0 | 0 | 0
Option 3C |  |  |  |  | $ | 0 | 23.049 | 64.8147 | 433.7698 | 3186.0645 | 0 | 0 | 0
Option 5A |  |  |  |  | $ | Redacted to preserve confidentiality
Option 5B |  |  |  |  | $ | Redacted to preserve confidentiality

## Central
S1 |  | Central
NPV results
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 68742850.382 | 0 | -3412010.7456 | -13090375.849 | -67156495.5543 | -99478078.0585 | -76438917.169 | 85096647.2601 | 276344125.8982 | -5683325.3902 | -5683325.3902 | -5683325.3902 | -5683325.3902 | -5683325.3902 | -5683325.3902 | -5683325.3902 | -5683325.3902 | -5683325.3902 | -5683325.3902 | -5683325.3902 | 164964479.9457
Option 1B |  |  |  | $ | 331615015.1525 | 0 | -2574506.2314 | -14870500.6472 | -72910435.383 | -53166277.4981 | 162461972.722 | 168405482.8172 | 238944555.3667 | -4365938.6468 | -4365938.6468 | -4365938.6468 | -4365938.6468 | -4365938.6468 | -4365938.6468 | -4365938.6468 | -4365938.6468 | -4365938.6468 | -4365938.6468 | -4365938.6468 | 182566621.3681
Option 2A |  |  |  | $ | 107999538.6782 | 0 | -1349660.0431 | -4565144.33 | -20961963.4725 | -32446603.7862 | -85341582.4382 | 5738649.1769 | 278746858.9897 | -3280592.4438 | -3280592.4438 | -3280592.4438 | -3280592.4438 | -3280592.4438 | -3280592.4438 | -3280592.4438 | -3280592.4438 | -3280592.4438 | -3280592.4438 | -3280592.4438 | 124975768.7686
Option 2B |  |  |  | $ | 194170396.1145 | 0 | -1117645.793 | -4325707.8812 | -20242418.3368 | -29503321.2927 | -77264541.4363 | 114174844.263 | 279471823.4068 | -2555628.0267 | -2508887.7692 | -2508887.7692 | -2508887.7692 | -2508887.7692 | -2508887.7692 | -2423197.297 | -2423197.297 | -2423197.297 | -2423197.297 | -2423197.297 | 105563231.1274
Option 2C |  |  |  | $ | 177004153.4449 | 0 | -1169558.2966 | -6441488.4622 | -26314661.8794 | -42824668.509 | -104625992.3411 | 110997385.1496 | 289643733.3773 | -3464269.7762 | -3464269.7762 | -3464269.7762 | -3464269.7762 | -3464269.7762 | -3464269.7762 | -3464269.7762 | -3464269.7762 | -3464269.7762 | -3464269.7762 | -3464269.7762 | 167575293.2516
Option 2D |  |  |  | $ | 52066175.8428 | 0 | -1455296.8676 | -5038634.5396 | -25121764.5392 | -48007021.0031 | -175494441.1207 | 30397110.4793 | 277149091.0035 | -4878360.43 | -4878360.43 | -4878360.43 | -4878360.43 | -4878360.43 | -4878360.43 | -4878360.43 | -4878360.43 | -4878360.43 | -4878360.43 | -4878360.43 | 185205668.5752
Option 3A |  |  |  | $ | 439174557.0832 | 0 | -1869464.1344 | -6458203.4081 | -28144553.7819 | -29979975.4723 | 178537576.7742 | 201571178.6997 | 278835962.2492 | -3191489.1843 | -3144748.9268 | -3144748.9268 | -3144748.9268 | -3144748.9268 | -3144748.9268 | -3059058.4546 | -3059058.4546 | -3059058.4546 | -3059058.4546 | -3059058.4546 | 104497690.832
Option 3B |  |  |  | $ | 381351469.7041 | 0 | -1869464.1344 | -6458203.4081 | -28144553.7819 | -33695476.4723 | 155587191.7742 | 150015318.6997 | 288777910.2492 | -4557085.1443 | -4510344.8868 | -4510344.8868 | -4510344.8868 | -4510344.8868 | -4510344.8868 | -4424654.4146 | -4424654.4146 | -4424654.4146 | -4424654.4146 | -4424654.4146 | 106957522.972
Option 3C |  |  |  | $ | 419183269.4893 | 0 | -1619195.7017 | -7989080.5661 | -25492487.6919 | -36205315.6647 | 174030394.9924 | 153442189.0875 | 289732836.637 | -3375166.5165 | -3328426.259 | -3328426.259 | -3328426.259 | -3328426.259 | -3328426.259 | -3242735.7868 | -3242735.7868 | -3242735.7868 | -3242735.7868 | -3242735.7868 | 148190563.0038
Option 5A |  |  |  | $ | 534238309.2772 | Redacted to preserve confidentiality
Option 5B |  |  |  | $ | 566944357.3683 | Redacted to preserve confidentiality
Capital cost calculation
Option | Stage | Components | TNSP | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A | 1 | 3rd Narrabri Tx | 1 | $ | -5404727.9612 | 0 | -579744.0386 | -3465484.9208 | -4126950.7706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4903307.838
Option 1A | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -33495155.7649 | 0 | -466189.595 | -1313773.949 | -49169718.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27658398.9249
Option 1A | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -12134190.4723 | 0 | -1270571.3167 | -6682283.4849 | -10480304.2184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11059895.412
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -20350891.1431 | 0 | -188539.3946 | -188024.2644 | -536844.2295 | -590933.4024 | -27683721.36 | -9079106.7092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24053649.312
Option 1A | 1 | Upgrade 968 line to 160 MVA rating | 1 | $ | -86205869.101 | 0 | -906966.4008 | -1440809.2298 | -2842677.6499 | -97336044.2365 | -46156518.1829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89209809.42
Option 1A | 2 | 60 MVAr SVC at Narrabri | 1 | $ | -8884281.8121 | 0 | 0 | 0 | 0 | 0 | -1047577.2064 | -6968417.1091 | -11645069.1544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13762744.429
Option 1B | 1 | 3rd Narrabri Tx | 1 | $ | -5404727.9612 | 0 | -579744.0386 | -3465484.9208 | -4126950.7706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4903307.838
Option 1B | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -33495155.7649 | 0 | -466189.595 | -1313773.949 | -49169718.686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27658398.9249
Option 1B | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -12134190.4723 | 0 | -1270571.3167 | -6682283.4849 | -10480304.2184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11059895.412
Option 1B | 1 | Upgrade 9UH line | 1 | $ | -23101119.5996 | 0 | -258001.2811 | -500494.2924 | -808645.708 | -36700028.0785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21866953.92
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | -49795048.5147 | 0 | 0 | -2908464 | -8324816 | -14915149 | -28412076 | -40615937 | -7298300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77880803.92
Option 2A | 1 | 3rd Narrabri Tx | 1 | $ | -5404727.9612 | 0 | -579744.0386 | -3465484.9208 | -4126950.7706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4903307.838
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -25296134.4421 | 0 | -304770.178 | -540678.4002 | -15488846.5297 | -11723872.4983 | -17921537.2786 | -999822.9853 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34764850.6238
Option 2A | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | -28614050.3662 | 0 | -290073.5228 | -384387.0441 | -909168.7657 | -11910563.8167 | -37455489.0607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30569809.326
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -19606303.1977 | 0 | -175072.3038 | -174593.965 | -436997.4065 | -548723.8766 | -9553535.5044 | -27378246.3238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24053649.3246
Option 2A | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -8884281.5878 | 0 | 0 | 0 | 0 | 0 | -1047577 | -6968417 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13762744.1
Option 2B | 1 | 3rd Narrabri Tx | 1 | $ | -5404727.9612 | 0 | -579744.0386 | -3465484.9208 | -4126950.7706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4903307.838
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -32682099.4666 | 0 | -320034.0032 | -571518.4188 | -15432611.1821 | -12294119.0011 | -28721538.8356 | -4730669.9292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45932163.6138
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -21491374.7179 | 0 | -217867.7512 | -288704.5415 | -682856.3841 | -8945758.697 | -28131982.0061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22960301.628
Option 2B | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -8884281.5878 | 0 | 0 | 0 | 0 | 0 | -1047577 | -6968417 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13762744.1
Option 2C | 1 | 3rd Narrabri Tx | 1 | $ | -5404727.9612 | 0 | -579744.0386 | -3465484.9208 | -4126950.7706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4903307.838
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -25281759.0696 | 0 | -299740.7353 | -530361.4973 | -15403787.3431 | -11638033.0977 | -18079886.6859 | -1027718.5108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34764850.6238
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating | 1 | $ | -28614050.3662 | 0 | -290073.5228 | -384387.0441 | -909168.7657 | -11910563.8167 | -37455489.0607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30569809.326
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -32730786.8425 | 0 | 0 | -2061255 | -5874755 | -11012628 | -13927173 | -32722750 | -1513538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51005195.24
Option 2D | 1 | 3rd Narrabri Tx | 1 | $ | -5404727.9612 | 0 | -579744.0386 | -3465484.9208 | -4126950.7706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4903307.838
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -65667236.3839 | 0 | -367611.5549 | -900058.0332 | -19402788.6187 | -18887254.8947 | -84355949.4593 | -2954264.6191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93882266.1132
Option 2D | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | -28614050.3662 | 0 | -290073.5228 | -384387.0441 | -909168.7657 | -11910563.8167 | -37455489.0607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30569809.326
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -21491374.7179 | 0 | -217867.7512 | -288704.5415 | -682856.3841 | -8945758.697 | -28131982.0061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22960301.628
Option 2D | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -8884281.5878 | 0 | 0 | 0 | 0 | 0 | -1047577 | -6968417 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13762744.1
Option 3A | 1 | 3rd Narrabri Tx | 1 | $ | -5404727.9612 | 0 | -579744.0386 | -3465484.9208 | -4126950.7706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4903307.838
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | -53440543.6801 | 0 | -1066900.8057 | -2677884.0458 | -23319227.1721 | -66799537.2363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65704484.482
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -21661772.2175 | 0 | -222819.2901 | -314834.4414 | -698375.8392 | -12858725.5815 | -24172414.2178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22960301.622
Option 3A | 2 | 60 MVAr SVC at Narrabri 132 | 1 | $ | -8884281.5878 | 0 | 0 | 0 | 0 | 0 | -1047577 | -6968417 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13762744.1
Option 3B | 1 | 3rd Narrabri Tx | 1 | $ | -5404727.9612 | 0 | -579744.0386 | -3465484.9208 | -4126950.7706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4903307.838
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | -53440543.6801 | 0 | -1066900.8057 | -2677884.0458 | -23319227.1721 | -66799537.2363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65704484.482
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -21661772.2175 | 0 | -222819.2901 | -314834.4414 | -698375.8392 | -12858725.5815 | -24172414.2178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22960301.622
Option 3B | 2 | Install 50 MW (50 MWh) BESS at Narrabri 132 | 1 | $ | -58616641.1488 | 0 | 0 | 0 | 0 | -3715501 | -23997962 | -58524277 | -1703121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17588172.2
Option 3C | 1 | 3rd Narrabri Tx | 1 | $ | -5404727.9612 | 0 | -579744.0386 | -3465484.9208 | -4126950.7706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4903307.838
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | -53069458.8203 | 0 | -1039451.6631 | -2462340.6453 | -15490781.9213 | -74870975.0103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65704484.468
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -32730786.8425 | 0 | 0 | -2061255 | -5874755 | -11012628 | -13927173 | -32722750 | -1513538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51005195.24
Option 5A | 1 | 3rd Narrabri Tx | 1 | $ | -5404727.9612 | 0 | -579744.0386 | -3465484.9208 | -4126950.7706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4903307.838
Option 5A | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | -39949083.1912 | 0 | 0 | 0 | 0 | -1066900.8057 | -2677884.0458 | -23319227.1721 | -66799537.2363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71336297.4376
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -17828363.9123 | 0 | 0 | 0 | -222819.2901 | -314834.4414 | -698375.8392 | -12858725.5815 | -24172414.2178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25146997.0146
Option 5B | 1 | 3rd Narrabri Tx | 1 | $ | -5404727.9612 | 0 | -579744.0386 | -3465484.9208 | -4126950.7706 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4903307.838
Option 5B | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | -39949083.1912 | 0 | 0 | 0 | 0 | -1066900.8057 | -2677884.0458 | -23319227.1721 | -66799537.2363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71336297.4376
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -17828363.9123 | 0 | 0 | 0 | -222819.2901 | -314834.4414 | -698375.8392 | -12858725.5815 | -24172414.2178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25146997.0146
Biodiversity offset costs
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | -6178211.8152 | 0 | 0 | 0 | 0 | 0 | -12600000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9576000
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -4371150.7572 | 0 | 0 | 0 | 0 | -8100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5994000
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -4371150.7572 | 0 | 0 | 0 | 0 | -8100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5994000
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -4371150.7572 | 0 | 0 | 0 | 0 | -8100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5994000
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -7747281.4825 | 0 | 0 | 0 | 0 | 0 | -15800000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12008000
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -4371150.7572 | 0 | 0 | 0 | 0 | -8100000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5994000
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -7747281.4825 | 0 | 0 | 0 | 0 | 0 | -15800000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12008000
Property allowances
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | -18453114.3759 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -44720000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33987200
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -9553264.3617 | 0 | 0 | 0 | 0 | 0 | -19200000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14208000
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -9553264.3617 | 0 | 0 | 0 | 0 | 0 | -19200000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14208000
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -9553264.3617 | 0 | 0 | 0 | 0 | 0 | -19200000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14208000
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -10423314.6603 | 0 | 0 | 0 | 0 | 0 | 0 | -23140000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17586400
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -12110752.8418 | 0 | 0 | 0 | 0 | 0 | -24340000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18011600
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -10423314.6603 | 0 | 0 | 0 | 0 | 0 | 0 | -23140000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17586400
TNSP capital costs
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | -166475116.2547 | 0 | -3412010.7456 | -13090375.849 | -67156495.5543 | -97926977.6389 | -74887816.7494 | -16047523.8183 | -11645069.1544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170647805.3359
Option 1B |  |  |  | $ | -148561568.5038 | 0 | -2574506.2314 | -14870500.6472 | -72910435.383 | -51615177.0785 | -41012076 | -40615937 | -52018300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186932560.0149
Option 2A |  |  |  | $ | -101729912.674 | 0 | -1349660.0431 | -4565144.33 | -20961963.4725 | -32283160.1916 | -85178138.8436 | -35346486.3091 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128256361.2124
Option 2B |  |  |  | $ | -82386898.8525 | 0 | -1117645.793 | -4325707.8812 | -20242418.3368 | -29339877.6981 | -77101097.8417 | -11699086.9292 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107760517.1798
Option 2C |  |  |  | $ | -124126335.5012 | 0 | -1169558.2966 | -6441488.4622 | -26314661.8794 | -42661224.9144 | -104462548.7465 | -56890468.5108 | -1513538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171039563.0278
Option 2D |  |  |  | $ | -146543574.6162 | 0 | -1455296.8676 | -5038634.5396 | -25121764.5392 | -47843577.4085 | -175330997.5261 | -9922681.6191 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190084029.0052
Option 3A |  |  |  | $ | -89391325.4466 | 0 | -1869464.1344 | -6458203.4081 | -28144553.7819 | -79658262.8179 | -25219991.2178 | -6968417 | -11645069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107330838.042
Option 3B |  |  |  | $ | -139123685.0077 | 0 | -1869464.1344 | -6458203.4081 | -28144553.7819 | -83373763.8179 | -48170376.2178 | -58524277 | -1703121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111156266.142
Option 3C |  |  |  | $ | -109375569.7668 | 0 | -1619195.7017 | -7989080.5661 | -25492487.6919 | -85883603.0103 | -29727173 | -55862750 | -1513538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151207387.546
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
NNO capital costs
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Operating cost calculation
Option | Stage | Component | TNSP | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A | 1 | 3rd Narrabri Tx | 1 | $ | -1456236.6871 | 0 | 0 | 0 | 0 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946
Option 1A | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -9078948.201 | 0 | 0 | 0 | 0 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446
Option 1A | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -3284685.7644 | 0 | 0 | 0 | 0 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -5060544.7764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -765343.3872 | -765343.3872 | -765343.3872 | -765343.3872 | -765343.3872 | -765343.3872 | -765343.3872 | -765343.3872 | -765343.3872 | -765343.3872 | -765343.3872 | -765343.3872 | -765343.3872
Option 1A | 1 | Upgrade 968 line to 160 MVA rating | 1 | $ | -21818843.1412 | 0 | 0 | 0 | 0 | 0 | 0 | -2973660.314 | -2973660.314 | -2973660.314 | -2973660.314 | -2973660.314 | -2973660.314 | -2973660.314 | -2973660.314 | -2973660.314 | -2973660.314 | -2973660.314 | -2973660.314 | -2973660.314 | -2973660.314
Option 1A | 2 | 60 MVAr SVC at Narrabri | 1 | $ | -2329712.7087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -393221.2694 | -393221.2694 | -393221.2694 | -393221.2694 | -393221.2694 | -393221.2694 | -393221.2694 | -393221.2694 | -393221.2694 | -393221.2694 | -393221.2694 | -393221.2694
Option 1B | 1 | 3rd Narrabri Tx | 1 | $ | -1456236.6871 | 0 | 0 | 0 | 0 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946
Option 1B | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -9078948.201 | 0 | 0 | 0 | 0 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446 | -1018993.6446
Option 1B | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -3284685.7644 | 0 | 0 | 0 | 0 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804 | -368663.1804
Option 1B | 1 | Upgrade 9UH line | 1 | $ | -6201197.3968 | 0 | 0 | 0 | 0 | 0 | -765343.3872 | -765343.3872 | -765343.3872 | -765343.3872 | -765343.3872 | -765343.3872 | -765343.3872 | -765343.3872 | -765343.3872 | -765343.3872 | -765343.3872 | -765343.3872 | -765343.3872 | -765343.3872 | -765343.3872
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | -12142614.2144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2049494.84 | -2049494.84 | -2049494.84 | -2049494.84 | -2049494.84 | -2049494.84 | -2049494.84 | -2049494.84 | -2049494.84 | -2049494.84 | -2049494.84 | -2049494.84
Option 2A | 1 | 3rd Narrabri Tx | 1 | $ | -1456236.6871 | 0 | 0 | 0 | 0 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -6212688.5353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -939590.5574 | -939590.5574 | -939590.5574 | -939590.5574 | -939590.5574 | -939590.5574 | -939590.5574 | -939590.5574 | -939590.5574 | -939590.5574 | -939590.5574 | -939590.5574 | -939590.5574
Option 2A | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | -7476732.423 | 0 | 0 | 0 | 0 | 0 | 0 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -5060544.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876
Option 2A | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -2329712.653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26
Option 2B | 1 | 3rd Narrabri Tx | 1 | $ | -1456236.6871 | 0 | 0 | 0 | 0 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -8208354.7365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1241409.8274 | -1241409.8274 | -1241409.8274 | -1241409.8274 | -1241409.8274 | -1241409.8274 | -1241409.8274 | -1241409.8274 | -1241409.8274 | -1241409.8274 | -1241409.8274 | -1241409.8274 | -1241409.8274
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -5615606.8817 | 0 | 0 | 0 | 0 | 0 | 0 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876
Option 2B | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -2329712.653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26
Option 2C | 1 | 3rd Narrabri Tx | 1 | $ | -1456236.6871 | 0 | 0 | 0 | 0 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -6212688.5353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -939590.5574 | -939590.5574 | -939590.5574 | -939590.5574 | -939590.5574 | -939590.5574 | -939590.5574 | -939590.5574 | -939590.5574 | -939590.5574 | -939590.5574 | -939590.5574 | -939590.5574
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating | 1 | $ | -7476732.423 | 0 | 0 | 0 | 0 | 0 | 0 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -7952362.8103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1342241.98 | -1342241.98 | -1342241.98 | -1342241.98 | -1342241.98 | -1342241.98 | -1342241.98 | -1342241.98 | -1342241.98 | -1342241.98 | -1342241.98 | -1342241.98
Option 2D | 1 | 3rd Narrabri Tx | 1 | $ | -1456236.6871 | 0 | 0 | 0 | 0 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -16777327.3257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2537358.5436 | -2537358.5436 | -2537358.5436 | -2537358.5436 | -2537358.5436 | -2537358.5436 | -2537358.5436 | -2537358.5436 | -2537358.5436 | -2537358.5436 | -2537358.5436 | -2537358.5436 | -2537358.5436
Option 2D | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | -7476732.423 | 0 | 0 | 0 | 0 | 0 | 0 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442 | -1018993.6442
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -5615606.8817 | 0 | 0 | 0 | 0 | 0 | 0 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876 | -765343.3876
Option 2D | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -2329712.653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26
Option 3A | 1 | 3rd Narrabri Tx | 1 | $ | -1456236.6871 | 0 | 0 | 0 | 0 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | -15210594.54 | 0 | 0 | 0 | 0 | 0 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -5615606.8803 | 0 | 0 | 0 | 0 | 0 | 0 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874
Option 3A | 2 | 60 MVAr SVC at Narrabri 132 | 1 | $ | -2329712.653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26 | -393221.26
Option 3B | 1 | 3rd Narrabri Tx | 1 | $ | -1456236.6871 | 0 | 0 | 0 | 0 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | -15210594.54 | 0 | 0 | 0 | 0 | 0 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -5615606.8803 | 0 | 0 | 0 | 0 | 0 | 0 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874
Option 3B | 2 | Install 50 MW (50 MWh) BESS at Narrabri 132 | 1 | $ | -10420440.4712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1758817.22 | -1758817.22 | -1758817.22 | -1758817.22 | -1758817.22 | -1758817.22 | -1758817.22 | -1758817.22 | -1758817.22 | -1758817.22 | -1758817.22 | -1758817.22
Option 3B | 2 | 3rd Narrabri Tx | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | -1456236.6871 | 0 | 0 | 0 | 0 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946
Option 3C | 1 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -15210594.5367 | 0 | 0 | 0 | 0 | 0 | -1877270.9848 | -1877270.9848 | -1877270.9848 | -1877270.9848 | -1877270.9848 | -1877270.9848 | -1877270.9848 | -1877270.9848 | -1877270.9848 | -1877270.9848 | -1877270.9848 | -1877270.9848 | -1877270.9848 | -1877270.9848 | -1877270.9848
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -7952362.8103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1342241.98 | -1342241.98 | -1342241.98 | -1342241.98 | -1342241.98 | -1342241.98 | -1342241.98 | -1342241.98 | -1342241.98 | -1342241.98 | -1342241.98 | -1342241.98
Option 5A | 1 | 3rd Narrabri Tx | 1 | $ | -1456236.6871 | 0 | 0 | 0 | 0 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946
Option 5A | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | -11122241.8834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -4534419.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874
Option 5B | 1 | 3rd Narrabri Tx | 1 | $ | -1456236.6871 | 0 | 0 | 0 | 0 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946 | -163443.5946
Option 5B | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | -11122241.8834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852 | -1877270.9852
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -4534419.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874 | -765343.3874
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TNSP operating expenditure
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | -43028971.2788 | 0 | 0 | 0 | 0 | -1551100.4196 | -1551100.4196 | -4524760.7336 | -5290104.1208 | -5683325.3902 | -5683325.3902 | -5683325.3902 | -5683325.3902 | -5683325.3902 | -5683325.3902 | -5683325.3902 | -5683325.3902 | -5683325.3902 | -5683325.3902 | -5683325.3902 | -5683325.3902
Option 1B |  |  |  | $ | -32163682.2638 | 0 | 0 | 0 | 0 | -1551100.4196 | -2316443.8068 | -2316443.8068 | -2316443.8068 | -4365938.6468 | -4365938.6468 | -4365938.6468 | -4365938.6468 | -4365938.6468 | -4365938.6468 | -4365938.6468 | -4365938.6468 | -4365938.6468 | -4365938.6468 | -4365938.6468 | -4365938.6468
Option 2A |  |  |  | $ | -22535915.0774 | 0 | 0 | 0 | 0 | -163443.5946 | -163443.5946 | -1182437.2388 | -2887371.1838 | -3280592.4438 | -3280592.4438 | -3280592.4438 | -3280592.4438 | -3280592.4438 | -3280592.4438 | -3280592.4438 | -3280592.4438 | -3280592.4438 | -3280592.4438 | -3280592.4438 | -3280592.4438
Option 2B |  |  |  | $ | -17609910.9584 | 0 | 0 | 0 | 0 | -163443.5946 | -163443.5946 | -928786.9822 | -2170196.8096 | -2563418.0696 | -2563418.0696 | -2563418.0696 | -2563418.0696 | -2563418.0696 | -2563418.0696 | -2563418.0696 | -2563418.0696 | -2563418.0696 | -2563418.0696 | -2563418.0696 | -2563418.0696
Option 2C |  |  |  | $ | -23098020.4557 | 0 | 0 | 0 | 0 | -163443.5946 | -163443.5946 | -1182437.2388 | -2122027.7962 | -3464269.7762 | -3464269.7762 | -3464269.7762 | -3464269.7762 | -3464269.7762 | -3464269.7762 | -3464269.7762 | -3464269.7762 | -3464269.7762 | -3464269.7762 | -3464269.7762 | -3464269.7762
Option 2D |  |  |  | $ | -33655615.9706 | 0 | 0 | 0 | 0 | -163443.5946 | -163443.5946 | -1947780.6264 | -4485139.17 | -4878360.43 | -4878360.43 | -4878360.43 | -4878360.43 | -4878360.43 | -4878360.43 | -4878360.43 | -4878360.43 | -4878360.43 | -4878360.43 | -4878360.43 | -4878360.43
Option 3A |  |  |  | $ | -24612150.7603 | 0 | 0 | 0 | 0 | -163443.5946 | -2040714.5798 | -2806057.9672 | -2806057.9672 | -3199279.2272 | -3199279.2272 | -3199279.2272 | -3199279.2272 | -3199279.2272 | -3199279.2272 | -3199279.2272 | -3199279.2272 | -3199279.2272 | -3199279.2272 | -3199279.2272 | -3199279.2272
Option 3B |  |  |  | $ | -32702878.5785 | 0 | 0 | 0 | 0 | -163443.5946 | -2040714.5798 | -2806057.9672 | -2806057.9672 | -4564875.1872 | -4564875.1872 | -4564875.1872 | -4564875.1872 | -4564875.1872 | -4564875.1872 | -4564875.1872 | -4564875.1872 | -4564875.1872 | -4564875.1872 | -4564875.1872 | -4564875.1872
Option 3C |  |  |  | $ | -24619194.0341 | 0 | 0 | 0 | 0 | -163443.5946 | -2040714.5794 | -2040714.5794 | -2040714.5794 | -3382956.5594 | -3382956.5594 | -3382956.5594 | -3382956.5594 | -3382956.5594 | -3382956.5594 | -3382956.5594 | -3382956.5594 | -3382956.5594 | -3382956.5594 | -3382956.5594 | -3382956.5594
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
TNSP NNO operating expenditure
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
NNO operating expenditure
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided fuel consumption from generation dispatch
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided voluntary load curtailment
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding outside of NW Slopes
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding in NW Slopes
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 278246937.9156 | 0 | 0 | 0 | 0 | 0 | 0 | 105668931.812 | 293279299.1735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 512340265.9201 | 0 | 0 | 0 | 0 | 0 | 205790492.5288 | 211337863.624 | 293279299.1735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 232265366.4295 | 0 | 0 | 0 | 0 | 0 | 0 | 42267572.7248 | 293279299.1735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 293574128.411 | 0 | 0 | 0 | 0 | 0 | 0 | 126802718.1744 | 293279299.1735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 324228509.4017 | 0 | 0 | 0 | 0 | 0 | 0 | 169070290.8992 | 293279299.1735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 232265366.4295 | 0 | 0 | 0 | 0 | 0 | 0 | 42267572.7248 | 293279299.1735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 552573345.6501 | 0 | 0 | 0 | 0 | 49841730.9401 | 205790492.5288 | 211337863.624 | 293279299.1735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 552573345.6501 | 0 | 0 | 0 | 0 | 49841730.9401 | 205790492.5288 | 211337863.624 | 293279299.1735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 552573345.6501 | 0 | 0 | 0 | 0 | 49841730.9401 | 205790492.5288 | 211337863.624 | 293279299.1735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided costs for non RIT-T proponent parties
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (wood pole replacement)
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 593077.5145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 604687.6401 | 0 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172
Option 3B |  |  |  | $ | 604687.6401 | 0 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172
Option 3C |  |  |  | $ | 604687.6401 | 0 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (market benefits)
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
NNO receipts received from TNSP
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality

## Low
S2 |  | Low
NPV results
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 10085354.9564 | 0 | -2895631.1878 | -14326927.9435 | -79721217.0937 | 30010255.8916 | 31765218.8614 | 31975104.0944 | 31975104.0944 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | 52588127.1941
Option 1B |  |  |  | $ | 10085354.9564 | 0 | -2895631.1878 | -14326927.9435 | -79721217.0937 | 30010255.8916 | 31765218.8614 | 31975104.0944 | 31975104.0944 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | 52588127.1941
Option 2A |  |  |  | $ | -27512335.2435 | 0 | -1105642.7707 | -5007704.1513 | -24519746.6253 | -24984145.1161 | -46606226.0915 | 25677100.4702 | 32535186.9289 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | 73458905.3873
Option 2B |  |  |  | $ | -42916104.8482 | 0 | -1124722.5522 | -5046254.1746 | -24449452.4408 | -25696953.2447 | -60106228.0377 | 14230745.8665 | 32164860.3688 | -1749119.25 | -1707434.0853 | -1707434.0853 | -1707434.0853 | -1707434.0853 | -1707434.0853 | -1631011.2833 | -1631011.2833 | -1631011.2833 | -1631011.2833 | -1631011.2833 | 87367306.3278
Option 2C |  |  |  | $ | -27489863.8558 | 0 | -1099355.9673 | -4994808.0227 | -24413422.6421 | -24876845.8654 | -46804162.8506 | 25642231.0634 | 32535186.9289 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | 73458905.3873
Option 2D |  |  |  | $ | -93131564.1322 | 0 | -1184194.4919 | -5456928.6926 | -29412174.2366 | -33938373.1117 | -136074241.3173 | 23234048.428 | 30537976.9461 | -3376002.6727 | -3376002.6727 | -3376002.6727 | -3376002.6727 | -3376002.6727 | -3376002.6727 | -3376002.6727 | -3376002.6727 | -3376002.6727 | -3376002.6727 | -3376002.6727 | 150112964.7663
Option 3A |  |  |  | $ | -21095964.3661 | 0 | -2058306.0554 | -7679211.2083 | -34307722.4284 | -75716443.1846 | 31160148.6886 | 31370033.9216 | 31370033.9216 | -2543945.6973 | -2502260.5325 | -2502260.5325 | -2502260.5325 | -2502260.5325 | -2502260.5325 | -2425837.7305 | -2425837.7305 | -2425837.7305 | -2425837.7305 | -2425837.7305 | 86035380.9658
Option 3B |  |  |  | $ | -21095964.3661 | 0 | -2058306.0554 | -7679211.2083 | -34307722.4284 | -75716443.1846 | 31160148.6886 | 31370033.9216 | 31370033.9216 | -2543945.6973 | -2502260.5325 | -2502260.5325 | -2502260.5325 | -2502260.5325 | -2502260.5325 | -2425837.7305 | -2425837.7305 | -2425837.7305 | -2425837.7305 | -2425837.7305 | 86035380.9658
Option 3C |  |  |  | $ | -20508784.7594 | 0 | -2023994.6271 | -7409781.9576 | -24522165.8649 | -85805740.4021 | 31160148.6891 | 31370033.9221 | 31370033.9221 | -2543945.6968 | -2502260.532 | -2502260.532 | -2502260.532 | -2502260.532 | -2502260.532 | -2425837.73 | -2425837.73 | -2425837.73 | -2425837.73 | -2425837.73 | 86035380.9488
Option 5A |  |  |  | $ | 918484.3756 | Redacted to preserve confidentiality
Option 5B |  |  |  | $ | 19353478.6991 | Redacted to preserve confidentiality
S2 |  | Calculation
Capital cost calculation
Option | Stage | Components | TNSP | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A | 1 | 3rd Narrabri Tx | 1 | $ | -7024063.341 | 0 | -724680.0482 | -4331856.1511 | -5158688.4632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6129134.7975
Option 1A | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -42688392.3381 | 0 | -582736.9937 | -1642217.4363 | -61462148.3575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34572998.6561
Option 1A | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -15752047.6578 | 0 | -1588214.1459 | -8352854.3561 | -13100380.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13824869.265
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1A | 1 | Upgrade 968 line to 160 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1A | 2 | 60 MVAr SVC at Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B | 1 | 3rd Narrabri Tx | 1 | $ | -7024063.341 | 0 | -724680.0482 | -4331856.1511 | -5158688.4632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6129134.7975
Option 1B | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -42688392.3381 | 0 | -582736.9937 | -1642217.4363 | -61462148.3575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34572998.6561
Option 1B | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -15752047.6578 | 0 | -1588214.1459 | -8352854.3561 | -13100380.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13824869.265
Option 1B | 1 | Upgrade 9UH line | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | 3rd Narrabri Tx | 1 | $ | -7024063.341 | 0 | -724680.0482 | -4331856.1511 | -5158688.4632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6129134.7975
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -32914330.1568 | 0 | -380962.7225 | -675848.0002 | -19361058.1621 | -14654840.6228 | -22401921.5982 | -1249778.7316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43456063.2798
Option 2A | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | 1 | 3rd Narrabri Tx | 1 | $ | -7024063.341 | 0 | -724680.0482 | -4331856.1511 | -5158688.4632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6129134.7975
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -42335326.11 | 0 | -400042.504 | -714398.0235 | -19290763.9776 | -15367648.7514 | -35901923.5444 | -5913337.4116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57415204.5173
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 1 | 3rd Narrabri Tx | 1 | $ | -7024063.341 | 0 | -724680.0482 | -4331856.1511 | -5158688.4632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6129134.7975
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -32891858.7691 | 0 | -374675.9191 | -662951.8717 | -19254734.1789 | -14547541.3721 | -22599858.3573 | -1284648.1385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43456063.2798
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | 3rd Narrabri Tx | 1 | $ | -7024063.341 | 0 | -724680.0482 | -4331856.1511 | -5158688.4632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6129134.7975
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -84745613.5372 | 0 | -459514.4437 | -1125072.5415 | -24253485.7734 | -23609068.6184 | -105444936.8241 | -3692830.7739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117352832.6415
Option 2D | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | 1 | 3rd Narrabri Tx | 1 | $ | -7024063.341 | 0 | -724680.0482 | -4331856.1511 | -5158688.4632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6129134.7975
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | -69340670.6502 | 0 | -1333626.0072 | -3347355.0573 | -29149033.9652 | -83499421.5454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82130605.6025
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | 2 | 60 MVAr SVC at Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | 1 | 3rd Narrabri Tx | 1 | $ | -7024063.341 | 0 | -724680.0482 | -4331856.1511 | -5158688.4632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6129134.7975
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | -69340670.6502 | 0 | -1333626.0072 | -3347355.0573 | -29149033.9652 | -83499421.5454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82130605.6025
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | 2 | Install 50 MW (50 MWh) BESS at Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 1 | 3rd Narrabri Tx | 1 | $ | -7024063.341 | 0 | -724680.0482 | -4331856.1511 | -5158688.4632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6129134.7975
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | -68753491.0468 | 0 | -1299314.5789 | -3077925.8066 | -19363477.4017 | -93588718.7629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82130605.585
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | 1 | 3rd Narrabri Tx | 1 | $ | -7024063.341 | 0 | -724680.0482 | -4331856.1511 | -5158688.4632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6129134.7975
Option 5A | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5B | 1 | 3rd Narrabri Tx | 1 | $ | -7024063.341 | 0 | -724680.0482 | -4331856.1511 | -5158688.4632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6129134.7975
Option 5B | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Biodiversity offset costs
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -5685484.8763 | 0 | 0 | 0 | 0 | -10125000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7492500
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -5685484.8763 | 0 | 0 | 0 | 0 | -10125000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7492500
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -5685484.8763 | 0 | 0 | 0 | 0 | -10125000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7492500
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -5685484.8763 | 0 | 0 | 0 | 0 | -10125000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7492500
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Property allowances
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -12222899.3536 | 0 | 0 | 0 | 0 | 0 | -24000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17760000
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -12222899.3536 | 0 | 0 | 0 | 0 | 0 | -24000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17760000
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -12222899.3536 | 0 | 0 | 0 | 0 | 0 | -24000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17760000
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -15495071.3681 | 0 | 0 | 0 | 0 | 0 | -30425000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22514500
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TNSP capital costs
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | -65464503.3369 | 0 | -2895631.1878 | -14326927.9435 | -79721217.0937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54527002.7186
Option 1B |  |  |  | $ | -65464503.3369 | 0 | -2895631.1878 | -14326927.9435 | -79721217.0937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54527002.7186
Option 2A |  |  |  | $ | -57846777.7276 | 0 | -1105642.7707 | -5007704.1513 | -24519746.6253 | -24779840.6228 | -46401921.5982 | -1249778.7316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74837698.0773
Option 2B |  |  |  | $ | -67267773.6808 | 0 | -1124722.5522 | -5046254.1746 | -24449452.4408 | -25492648.7514 | -59901923.5444 | -5913337.4116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88796839.3148
Option 2C |  |  |  | $ | -57824306.3399 | 0 | -1099355.9673 | -4994808.0227 | -24413422.6421 | -24672541.3721 | -46599858.3573 | -1284648.1385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74837698.0773
Option 2D |  |  |  | $ | -112950233.1225 | 0 | -1184194.4919 | -5456928.6926 | -29412174.2366 | -33734068.6184 | -135869936.8241 | -3692830.7739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153488967.439
Option 3A |  |  |  | $ | -76364733.9911 | 0 | -2058306.0554 | -7679211.2083 | -34307722.4284 | -83499421.5454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88259740.4
Option 3B |  |  |  | $ | -76364733.9911 | 0 | -2058306.0554 | -7679211.2083 | -34307722.4284 | -83499421.5454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88259740.4
Option 3C |  |  |  | $ | -75777554.3877 | 0 | -2023994.6271 | -7409781.9576 | -24522165.8649 | -93588718.7629 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88259740.3825
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
NNO capital costs
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Operating cost calculation
Option | Stage | Component | TNSP | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A | 1 | 3rd Narrabri Tx | 1 | $ | -1503385.3337 | 0 | 0 | 0 | 0 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932
Option 1A | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -9372897.7521 | 0 | 0 | 0 | 0 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558
Option 1A | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -3391034.1965 | 0 | 0 | 0 | 0 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1A | 1 | Upgrade 968 line to 160 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1A | 2 | 60 MVAr SVC at Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B | 1 | 3rd Narrabri Tx | 1 | $ | -1503385.3337 | 0 | 0 | 0 | 0 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932
Option 1B | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -9372897.7521 | 0 | 0 | 0 | 0 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558 | -1273742.0558
Option 1B | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -3391034.1965 | 0 | 0 | 0 | 0 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755 | -460828.9755
Option 1B | 1 | Upgrade 9UH line | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | 3rd Narrabri Tx | 1 | $ | -1503385.3337 | 0 | 0 | 0 | 0 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -6183952.5913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1174488.1968 | -1174488.1968 | -1174488.1968 | -1174488.1968 | -1174488.1968 | -1174488.1968 | -1174488.1968 | -1174488.1968 | -1174488.1968 | -1174488.1968 | -1174488.1968 | -1174488.1968 | -1174488.1968
Option 2A | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | 1 | 3rd Narrabri Tx | 1 | $ | -1503385.3337 | 0 | 0 | 0 | 0 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -8170388.1106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1551762.2843 | -1551762.2843 | -1551762.2843 | -1551762.2843 | -1551762.2843 | -1551762.2843 | -1551762.2843 | -1551762.2843 | -1551762.2843 | -1551762.2843 | -1551762.2843 | -1551762.2843 | -1551762.2843
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 1 | 3rd Narrabri Tx | 1 | $ | -1503385.3337 | 0 | 0 | 0 | 0 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -6183952.5913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1174488.1967 | -1174488.1967 | -1174488.1967 | -1174488.1967 | -1174488.1967 | -1174488.1967 | -1174488.1967 | -1174488.1967 | -1174488.1967 | -1174488.1967 | -1174488.1967 | -1174488.1967 | -1174488.1967
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | 3rd Narrabri Tx | 1 | $ | -1503385.3337 | 0 | 0 | 0 | 0 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -16699726.0851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3171698.1795 | -3171698.1795 | -3171698.1795 | -3171698.1795 | -3171698.1795 | -3171698.1795 | -3171698.1795 | -3171698.1795 | -3171698.1795 | -3171698.1795 | -3171698.1795 | -3171698.1795 | -3171698.1795
Option 2D | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | 1 | 3rd Narrabri Tx | 1 | $ | -1503385.3337 | 0 | 0 | 0 | 0 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | -15510369.4239 | 0 | 0 | 0 | 0 | 0 | -2346588.7315 | -2346588.7315 | -2346588.7315 | -2346588.7315 | -2346588.7315 | -2346588.7315 | -2346588.7315 | -2346588.7315 | -2346588.7315 | -2346588.7315 | -2346588.7315 | -2346588.7315 | -2346588.7315 | -2346588.7315 | -2346588.7315
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A | 2 | 60 MVAr SVC at Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | 1 | 3rd Narrabri Tx | 1 | $ | -1503385.3337 | 0 | 0 | 0 | 0 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | -15510369.4239 | 0 | 0 | 0 | 0 | 0 | -2346588.7315 | -2346588.7315 | -2346588.7315 | -2346588.7315 | -2346588.7315 | -2346588.7315 | -2346588.7315 | -2346588.7315 | -2346588.7315 | -2346588.7315 | -2346588.7315 | -2346588.7315 | -2346588.7315 | -2346588.7315 | -2346588.7315
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B | 2 | Install 50 MW (50 MWh) BESS at Narrabri 132 | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C | 1 | 3rd Narrabri Tx | 1 | $ | -1503385.3337 | 0 | 0 | 0 | 0 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | -15510369.4206 | 0 | 0 | 0 | 0 | 0 | -2346588.731 | -2346588.731 | -2346588.731 | -2346588.731 | -2346588.731 | -2346588.731 | -2346588.731 | -2346588.731 | -2346588.731 | -2346588.731 | -2346588.731 | -2346588.731 | -2346588.731 | -2346588.731 | -2346588.731
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | 1 | 3rd Narrabri Tx | 1 | $ | -1503385.3337 | 0 | 0 | 0 | 0 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932
Option 5A | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5B | 1 | 3rd Narrabri Tx | 1 | $ | -1503385.3337 | 0 | 0 | 0 | 0 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932 | -204304.4932
Option 5B | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TNSP operating expenditure
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | -14267317.2823 | 0 | 0 | 0 | 0 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245
Option 1B |  |  |  | $ | -14267317.2823 | 0 | 0 | 0 | 0 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245 | -1938875.5245
Option 2A |  |  |  | $ | -7687337.925 | 0 | 0 | 0 | 0 | -204304.4932 | -204304.4932 | -204304.4932 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69
Option 2B |  |  |  | $ | -9673773.4443 | 0 | 0 | 0 | 0 | -204304.4932 | -204304.4932 | -204304.4932 | -1756066.7775 | -1756066.7775 | -1756066.7775 | -1756066.7775 | -1756066.7775 | -1756066.7775 | -1756066.7775 | -1756066.7775 | -1756066.7775 | -1756066.7775 | -1756066.7775 | -1756066.7775 | -1756066.7775
Option 2C |  |  |  | $ | -7687337.925 | 0 | 0 | 0 | 0 | -204304.4932 | -204304.4932 | -204304.4932 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69 | -1378792.69
Option 2D |  |  |  | $ | -18203111.4188 | 0 | 0 | 0 | 0 | -204304.4932 | -204304.4932 | -204304.4932 | -3376002.6727 | -3376002.6727 | -3376002.6727 | -3376002.6727 | -3376002.6727 | -3376002.6727 | -3376002.6727 | -3376002.6727 | -3376002.6727 | -3376002.6727 | -3376002.6727 | -3376002.6727 | -3376002.6727
Option 3A |  |  |  | $ | -17013754.7576 | 0 | 0 | 0 | 0 | -204304.4932 | -2550893.2248 | -2550893.2248 | -2550893.2248 | -2550893.2248 | -2550893.2248 | -2550893.2248 | -2550893.2248 | -2550893.2248 | -2550893.2248 | -2550893.2248 | -2550893.2248 | -2550893.2248 | -2550893.2248 | -2550893.2248 | -2550893.2248
Option 3B |  |  |  | $ | -17013754.7576 | 0 | 0 | 0 | 0 | -204304.4932 | -2550893.2248 | -2550893.2248 | -2550893.2248 | -2550893.2248 | -2550893.2248 | -2550893.2248 | -2550893.2248 | -2550893.2248 | -2550893.2248 | -2550893.2248 | -2550893.2248 | -2550893.2248 | -2550893.2248 | -2550893.2248 | -2550893.2248
Option 3C |  |  |  | $ | -17013754.7543 | 0 | 0 | 0 | 0 | -204304.4932 | -2550893.2242 | -2550893.2242 | -2550893.2242 | -2550893.2242 | -2550893.2242 | -2550893.2242 | -2550893.2242 | -2550893.2242 | -2550893.2242 | -2550893.2242 | -2550893.2242 | -2550893.2242 | -2550893.2242 | -2550893.2242 | -2550893.2242
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
TNSP NNO operating expenditure
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
NNO operating expenditure
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided fuel consumption from generation dispatch
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided voluntary load curtailment
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding outside of NW Slopes
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding in NW Slopes
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 89817175.5755 | 0 | 0 | 0 | 0 | 31949131.4161 | 33704094.3859 | 33913979.6189 | 33913979.6189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 89817175.5755 | 0 | 0 | 0 | 0 | 31949131.4161 | 33704094.3859 | 33913979.6189 | 33913979.6189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 38021780.409 | 0 | 0 | 0 | 0 | 0 | 0 | 27131183.6951 | 33913979.6189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 33626789.6628 | 0 | 0 | 0 | 0 | 0 | 0 | 20348387.7713 | 33913979.6189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 38021780.409 | 0 | 0 | 0 | 0 | 0 | 0 | 27131183.6951 | 33913979.6189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 38021780.409 | 0 | 0 | 0 | 0 | 0 | 0 | 27131183.6951 | 33913979.6189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 71874530.6778 | 0 | 0 | 0 | 0 | 7987282.854 | 33704094.3859 | 33913979.6189 | 33913979.6189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 71874530.6778 | 0 | 0 | 0 | 0 | 7987282.854 | 33704094.3859 | 33913979.6189 | 33913979.6189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 71874530.6778 | 0 | 0 | 0 | 0 | 7987282.854 | 33704094.3859 | 33913979.6189 | 33913979.6189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided costs for non RIT-T proponent parties
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (wood pole replacement)
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 398652.6141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6947.5275 | 6947.5275 | 48632.6922 | 48632.6922 | 48632.6922 | 48632.6922 | 48632.6922 | 125055.4942 | 125055.4942 | 125055.4942 | 125055.4942 | 125055.4942 | 326533.7905
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 407993.7048 | 0 | 0 | 0 | 0 | 0 | 6947.5275 | 6947.5275 | 6947.5275 | 6947.5275 | 48632.6922 | 48632.6922 | 48632.6922 | 48632.6922 | 48632.6922 | 125055.4942 | 125055.4942 | 125055.4942 | 125055.4942 | 125055.4942 | 326533.7905
Option 3B |  |  |  | $ | 407993.7048 | 0 | 0 | 0 | 0 | 0 | 6947.5275 | 6947.5275 | 6947.5275 | 6947.5275 | 48632.6922 | 48632.6922 | 48632.6922 | 48632.6922 | 48632.6922 | 125055.4942 | 125055.4942 | 125055.4942 | 125055.4942 | 125055.4942 | 326533.7905
Option 3C |  |  |  | $ | 407993.7048 | 0 | 0 | 0 | 0 | 0 | 6947.5275 | 6947.5275 | 6947.5275 | 6947.5275 | 48632.6922 | 48632.6922 | 48632.6922 | 48632.6922 | 48632.6922 | 125055.4942 | 125055.4942 | 125055.4942 | 125055.4942 | 125055.4942 | 326533.7905
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (market benefits)
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
NNO receipts received from TNSP
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality

## High
S3 |  | High
NPV results
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 290054719.7141 | 0 | -2559008.0592 | -9817781.8868 | -50367371.6658 | -74608558.5439 | -57329187.8768 | 121940397.9417 | 368561708.9691 | -4262494.0426 | -4262494.0426 | -4262494.0426 | -4262494.0426 | -4262494.0426 | -4262494.0426 | -4262494.0426 | -4262494.0426 | -4262494.0426 | -4262494.0426 | -4262494.0426 | 123723359.9592
Option 1B |  |  |  | $ | 677463808.1777 | 0 | -1930879.6735 | -11152875.4854 | -54682826.5372 | -39874708.1236 | 235031250.4324 | 242539937.1061 | 340512031.0704 | -3274453.9851 | -3274453.9851 | -3274453.9851 | -3274453.9851 | -3274453.9851 | -3274453.9851 | -3274453.9851 | -3274453.9851 | -3274453.9851 | -3274453.9851 | -3274453.9851 | 136924966.026
Option 2A |  |  |  | $ | 284209357.9452 | 0 | -1012245.0324 | -3423858.2475 | -15721472.6044 | -24334952.8396 | -64006186.8287 | 27551151.8813 | 370363758.7877 | -2460444.3328 | -2460444.3328 | -2460444.3328 | -2460444.3328 | -2460444.3328 | -2460444.3328 | -2460444.3328 | -2460444.3328 | -2460444.3328 | -2460444.3328 | -2460444.3328 | 93731826.5764
Option 2B |  |  |  | $ | 400401312.5597 | 0 | -838234.3448 | -3244280.9109 | -15181813.7526 | -22127490.9696 | -57948406.0772 | 155372628.1931 | 370907822.0868 | -1916381.0337 | -1879285.9229 | -1879285.9229 | -1879285.9229 | -1879285.9229 | -1879285.9229 | -1811278.2197 | -1811278.2197 | -1811278.2197 | -1811278.2197 | -1811278.2197 | 79188402.7008
Option 2C |  |  |  | $ | 416289839.9491 | 0 | -877168.7225 | -4831116.3467 | -19735996.4095 | -32118501.3818 | -78469494.2559 | 176236698.8568 | 378536414.5784 | -2598202.3322 | -2598202.3322 | -2598202.3322 | -2598202.3322 | -2598202.3322 | -2598202.3322 | -2598202.3322 | -2598202.3322 | -2598202.3322 | -2598202.3322 | -2598202.3322 | 125681469.9387
Option 2D |  |  |  | $ | 244595831.9874 | 0 | -1091472.6507 | -3778975.9047 | -18841323.4044 | -36005265.7523 | -131620830.8405 | 46044997.8581 | 369165432.798 | -3658770.3225 | -3658770.3225 | -3658770.3225 | -3658770.3225 | -3658770.3225 | -3658770.3225 | -3658770.3225 | -3658770.3225 | -3658770.3225 | -3658770.3225 | -3658770.3225 | 138904251.4314
Option 3A |  |  |  | $ | 784002778.0424 | 0 | -1402098.1008 | -4843652.556 | -21108415.3364 | 4927970.4128 | 247088293.4578 | 267414549.0043 | 370430926.2186 | -2393276.9019 | -2356181.7911 | -2356181.7911 | -2356181.7911 | -2356181.7911 | -2356181.7911 | -2288174.0879 | -2288174.0879 | -2288174.0879 | -2288174.0879 | -2288174.0879 | 78389247.4793
Option 3B |  |  |  | $ | 731286380.8847 | 0 | -1402098.1008 | -4843652.556 | -21108415.3364 | 2141344.6628 | 229875504.7078 | 228747654.0043 | 377887387.2186 | -3417473.8719 | -3380378.7611 | -3380378.7611 | -3380378.7611 | -3380378.7611 | -3380378.7611 | -3312371.0579 | -3312371.0579 | -3312371.0579 | -3312371.0579 | -3312371.0579 | 80234121.5843
Option 3C |  |  |  | $ | 773439564.37 | 0 | -1214396.7763 | -5991810.4246 | -19119365.7689 | 258965.2685 | 243707907.1214 | 231317806.7951 | 378603582.0095 | -2531034.9011 | -2493939.7903 | -2493939.7903 | -2493939.7903 | -2493939.7903 | -2493939.7903 | -2425932.0871 | -2425932.0871 | -2425932.0871 | -2425932.0871 | -2425932.0871 | 111158901.6081
Option 4 |  |  |  | $ | 268160196.4193 | 0 | -2087028.8901 | -5217602.8736 | -24218953.4228 | -42266559.0286 | -56788147.1717 | 27136469.4984 | 369991501.5632 | -2832701.5573 | -2832701.5573 | -2832701.5573 | -2832701.5573 | -2832701.5573 | -2832701.5573 | -2832701.5573 | -2832701.5573 | -2832701.5573 | -2832701.5573 | -2832701.5573 | 106487200.1935
Option 5A |  |  |  | $ | 959256971.1148 | Redacted to preserve confidentiality
Option 5B |  |  |  | $ | 1006690473.2486 | Redacted to preserve confidentiality
S3 |  | Calculation
Capital cost calculation
Option | Stage | Components | TNSP | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A | 1 | 3rd Narrabri Tx | 1 | $ | -3390742.2517 | 0 | -434808.0289 | -2599113.6906 | -3095213.0779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3677480.8785
Option 1A | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -22158428.9696 | 0 | -349642.1962 | -985330.4618 | -36877289.0145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20743799.1936
Option 1A | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -7629220.7233 | 0 | -952928.4875 | -5011712.6137 | -7860228.1638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8294921.559
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -13751506.5496 | 0 | -141404.5459 | -141018.1983 | -402633.1721 | -443200.0518 | -20762791.02 | -6809330.0319 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18040236.984
Option 1A | 1 | Upgrade 968 line to 160 MVA rating | 1 | $ | -57532211.8851 | 0 | -680224.8006 | -1080606.9224 | -2132008.2374 | -73002033.1774 | -34617388.6372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66907357.065
Option 1A | 2 | 60 MVAr SVC at Narrabri | 1 | $ | -5977975.0142 | 0 | 0 | 0 | 0 | 0 | -785682.9048 | -5226312.8318 | -8733801.8658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10322058.3218
Option 1B | 1 | 3rd Narrabri Tx | 1 | $ | -3390742.2517 | 0 | -434808.0289 | -2599113.6906 | -3095213.0779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3677480.8785
Option 1B | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -22158428.9696 | 0 | -349642.1962 | -985330.4618 | -36877289.0145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20743799.1936
Option 1B | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -7629220.7233 | 0 | -952928.4875 | -5011712.6137 | -7860228.1638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8294921.559
Option 1B | 1 | Upgrade 9UH line | 1 | $ | -15530894.5617 | 0 | -193500.9608 | -375370.7193 | -606484.281 | -27525021.0589 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16400215.44
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | -30218746.1074 | 0 | 0 | -2181348 | -6243612 | -11186361.75 | -21309057 | -30461952.75 | -5473725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58410602.94
Option 2A | 1 | 3rd Narrabri Tx | 1 | $ | -3390742.2517 | 0 | -434808.0289 | -2599113.6906 | -3095213.0779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3677480.8785
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -15081609.1095 | 0 | -228577.6335 | -405508.8001 | -11616634.8973 | -8792904.3737 | -13441152.9589 | -749867.239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26073637.9679
Option 2A | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | -19385270.0611 | 0 | -217555.1421 | -288290.2831 | -681876.5743 | -8932922.8625 | -28091616.7955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22927356.9945
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -13478280.0649 | 0 | -131304.2279 | -130945.4737 | -327748.0549 | -411542.9074 | -7165151.6283 | -20533684.7428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18040236.9934
Option 2A | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -5977974.8669 | 0 | 0 | 0 | 0 | 0 | -785682.75 | -5226312.75 | -8733801.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10322058.075
Option 2B | 1 | 3rd Narrabri Tx | 1 | $ | -3390742.2517 | 0 | -434808.0289 | -2599113.6906 | -3095213.0779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3677480.8785
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -19664263.7062 | 0 | -240025.5024 | -428638.8141 | -11574458.3866 | -9220589.2508 | -21541154.1267 | -3548002.4469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34449122.7104
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -14559843.7668 | 0 | -163400.8134 | -216528.4061 | -512142.2881 | -6709319.0228 | -21098986.5046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17220226.221
Option 2B | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -5977974.8669 | 0 | 0 | 0 | 0 | 0 | -785682.75 | -5226312.75 | -8733801.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10322058.075
Option 2C | 1 | 3rd Narrabri Tx | 1 | $ | -3390742.2517 | 0 | -434808.0289 | -2599113.6906 | -3095213.0779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3677480.8785
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -15076552.4714 | 0 | -224805.5514 | -397771.123 | -11552840.5073 | -8728524.8233 | -13559915.0144 | -770788.8831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26073637.9678
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating | 1 | $ | -19385270.0611 | 0 | -217555.1421 | -288290.2831 | -681876.5743 | -8932922.8625 | -28091616.7955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22927356.9945
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -19834259.0706 | 0 | 0 | -1545941.25 | -4406066.25 | -8259471 | -10445379.75 | -24542062.5 | -1135153.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38253896.43
Option 2D | 1 | 3rd Narrabri Tx | 1 | $ | -3390742.2517 | 0 | -434808.0289 | -2599113.6906 | -3095213.0779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3677480.8785
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -39799522.9057 | 0 | -275708.6662 | -675043.5249 | -14552091.464 | -14165441.171 | -63266962.0945 | -2215698.4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70411699.5849
Option 2D | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | -19385270.0611 | 0 | -217555.1421 | -288290.2831 | -681876.5743 | -8932922.8625 | -28091616.7955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22927356.9945
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -14559843.7668 | 0 | -163400.8134 | -216528.4061 | -512142.2881 | -6709319.0228 | -21098986.5046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17220226.221
Option 2D | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -5977974.8669 | 0 | 0 | 0 | 0 | 0 | -785682.75 | -5226312.75 | -8733801.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10322058.075
Option 3A | 1 | 3rd Narrabri Tx | 1 | $ | -3390742.2517 | 0 | -434808.0289 | -2599113.6906 | -3095213.0779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3677480.8785
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | -32534231.6993 | 0 | -800175.6043 | -2008413.0344 | -17489420.3791 | -50099652.9272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49278363.3615
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -14620432.3514 | 0 | -167114.4676 | -236125.831 | -523781.8794 | -9644044.1861 | -18129310.6633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17220226.2165
Option 3A | 2 | 60 MVAr SVC at Narrabri 132 | 1 | $ | -5977974.8669 | 0 | 0 | 0 | 0 | 0 | -785682.75 | -5226312.75 | -8733801.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10322058.075
Option 3B | 1 | 3rd Narrabri Tx | 1 | $ | -3390742.2517 | 0 | -434808.0289 | -2599113.6906 | -3095213.0779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3677480.8785
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | -32534231.6993 | 0 | -800175.6043 | -2008413.0344 | -17489420.3791 | -50099652.9272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49278363.3615
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -14620432.3514 | 0 | -167114.4676 | -236125.831 | -523781.8794 | -9644044.1861 | -18129310.6633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17220226.2165
Option 3B | 2 | Install 50 MW (50 MWh) BESS at Narrabri 132 | 1 | $ | -49542397.0301 | 0 | 0 | 0 | 0 | -2786625.75 | -17998471.5 | -43893207.75 | -1277340.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13191129.15
Option 3C | 1 | 3rd Narrabri Tx | 1 | $ | -3390742.2517 | 0 | -434808.0289 | -2599113.6906 | -3095213.0779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3677480.8785
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | -32406392.7962 | 0 | -779588.7474 | -1846755.4839 | -11618086.441 | -56153231.2577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49278363.351
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -19834259.0706 | 0 | 0 | -1545941.25 | -4406066.25 | -8259471 | -10445379.75 | -24542062.5 | -1135153.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38253896.43
Option 5A | 1 | 3rd Narrabri Tx | 1 | $ | -3390742.2517 | 0 | -434808.0289 | -2599113.6906 | -3095213.0779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3677480.8785
Option 5A | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | -25598400.6107 | 0 | 0 | 0 | 0 | -800175.6043 | -2008413.0344 | -17489420.3791 | -50099652.9272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53502223.0782
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -12422239.6669 | 0 | 0 | 0 | -167114.4676 | -236125.831 | -523781.8794 | -9644044.1861 | -18129310.6633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18860247.7609
Option 5B | 1 | 3rd Narrabri Tx | 1 | $ | -3390742.2517 | 0 | -434808.0289 | -2599113.6906 | -3095213.0779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3677480.8785
Option 5B | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | -25598400.6107 | 0 | 0 | 0 | 0 | -800175.6043 | -2008413.0344 | -17489420.3791 | -50099652.9272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53502223.0782
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -12422239.6669 | 0 | 0 | 0 | -167114.4676 | -236125.831 | -523781.8794 | -9644044.1861 | -18129310.6633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18860247.7609
Biodiversity offset costs
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | -3739885.4406 | 0 | 0 | 0 | 0 | 0 | -9450000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7182000
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -2605447.0726 | 0 | 0 | 0 | 0 | -6075000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4495500
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -2605447.0726 | 0 | 0 | 0 | 0 | -6075000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4495500
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -2605447.0726 | 0 | 0 | 0 | 0 | -6075000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4495500
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -4689697.616 | 0 | 0 | 0 | 0 | 0 | -11850000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9006000
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -2605447.0726 | 0 | 0 | 0 | 0 | -6075000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4495500
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -4689697.616 | 0 | 0 | 0 | 0 | 0 | -11850000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9006000
Property allowances
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | -11977446.1612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -33540000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25490400
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -5888283.3702 | 0 | 0 | 0 | 0 | 0 | -14400000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10656000
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -5888283.3702 | 0 | 0 | 0 | 0 | 0 | -14400000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10656000
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -5888283.3702 | 0 | 0 | 0 | 0 | 0 | -14400000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10656000
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -6529282.7537 | 0 | 0 | 0 | 0 | 0 | 0 | -17355000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13189800
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -7464625.8974 | 0 | 0 | 0 | 0 | 0 | -18255000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13508700
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -6529282.7537 | 0 | 0 | 0 | 0 | 0 | 0 | -17355000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13189800
TNSP capital costs
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | -110440085.3935 | 0 | -2559008.0592 | -9817781.8868 | -50367371.6658 | -73445233.2292 | -56165862.5621 | -12035642.8637 | -8733801.8658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127985854.0019
Option 1B |  |  |  | $ | -94645364.2155 | 0 | -1930879.6735 | -11152875.4854 | -54682826.5372 | -38711382.8089 | -30759057 | -30461952.75 | -39013725 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140199420.0111
Option 2A |  |  |  | $ | -65807606.7968 | 0 | -1012245.0324 | -3423858.2475 | -15721472.6044 | -24212370.1437 | -63883604.1327 | -26509864.7318 | -8733801.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96192270.9093
Option 2B |  |  |  | $ | -52086555.0343 | 0 | -838234.3448 | -3244280.9109 | -15181813.7526 | -22004908.2736 | -57825823.3813 | -8774315.1969 | -8733801.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80820387.8849
Option 2C |  |  |  | $ | -77399534.6672 | 0 | -877168.7225 | -4831116.3467 | -19735996.4095 | -31995918.6858 | -78346911.5599 | -42667851.3831 | -1135153.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128279672.2709
Option 2D |  |  |  | $ | -93183426.8222 | 0 | -1091472.6507 | -3778975.9047 | -18841323.4044 | -35882683.0564 | -131498248.1445 | -7442011.2143 | -8733801.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142563021.7539
Option 3A |  |  |  | $ | -56523381.1692 | 0 | -1402098.1008 | -4843652.556 | -21108415.3364 | -59743697.1134 | -18914993.4133 | -5226312.75 | -8733801.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80498128.5315
Option 3B |  |  |  | $ | -100087803.3325 | 0 | -1402098.1008 | -4843652.556 | -21108415.3364 | -62530322.8634 | -36127782.1633 | -43893207.75 | -1277340.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83367199.6065
Option 3C |  |  |  | $ | -66850374.4881 | 0 | -1214396.7763 | -5991810.4246 | -19119365.7689 | -64412702.2577 | -22295379.75 | -41897062.5 | -1135153.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113405540.6595
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
NNO capital costs
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Operating cost calculation
Option | Stage | Component | TNSP | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A | 1 | 3rd Narrabri Tx | 1 | $ | -1529819.5502 | 0 | 0 | 0 | 0 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959
Option 1A | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -9537702.6112 | 0 | 0 | 0 | 0 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335
Option 1A | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -3450659.1842 | 0 | 0 | 0 | 0 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853
Option 1A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -5621082.9787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -574007.5404 | -574007.5404 | -574007.5404 | -574007.5404 | -574007.5404 | -574007.5404 | -574007.5404 | -574007.5404 | -574007.5404 | -574007.5404 | -574007.5404 | -574007.5404 | -574007.5404
Option 1A | 1 | Upgrade 968 line to 160 MVA rating | 1 | $ | -23793930.5181 | 0 | 0 | 0 | 0 | 0 | 0 | -2230245.2355 | -2230245.2355 | -2230245.2355 | -2230245.2355 | -2230245.2355 | -2230245.2355 | -2230245.2355 | -2230245.2355 | -2230245.2355 | -2230245.2355 | -2230245.2355 | -2230245.2355 | -2230245.2355 | -2230245.2355
Option 1A | 2 | 60 MVAr SVC at Narrabri | 1 | $ | -2635297.2111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -294915.952 | -294915.952 | -294915.952 | -294915.952 | -294915.952 | -294915.952 | -294915.952 | -294915.952 | -294915.952 | -294915.952 | -294915.952 | -294915.952
Option 1B | 1 | 3rd Narrabri Tx | 1 | $ | -1529819.5502 | 0 | 0 | 0 | 0 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959
Option 1B | 1 | Upgrade 969 line to 160 MVA rating | 1 | $ | -9537702.6112 | 0 | 0 | 0 | 0 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335 | -764245.2335
Option 1B | 1 | 50 MVAr SVC Gunnedah | 1 | $ | -3450659.1842 | 0 | 0 | 0 | 0 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853 | -276497.3853
Option 1B | 1 | Upgrade 9UH line | 1 | $ | -6638017.5568 | 0 | 0 | 0 | 0 | 0 | -574007.5404 | -574007.5404 | -574007.5404 | -574007.5404 | -574007.5404 | -574007.5404 | -574007.5404 | -574007.5404 | -574007.5404 | -574007.5404 | -574007.5404 | -574007.5404 | -574007.5404 | -574007.5404 | -574007.5404
Option 1B | 2 | Second 132 kV line between Tamworth and Narrabri | 1 | $ | -13735340.5227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1537121.13 | -1537121.13 | -1537121.13 | -1537121.13 | -1537121.13 | -1537121.13 | -1537121.13 | -1537121.13 | -1537121.13 | -1537121.13 | -1537121.13 | -1537121.13
Option 2A | 1 | 3rd Narrabri Tx | 1 | $ | -1529819.5502 | 0 | 0 | 0 | 0 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959
Option 2A | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -6900845.5257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -704692.9181 | -704692.9181 | -704692.9181 | -704692.9181 | -704692.9181 | -704692.9181 | -704692.9181 | -704692.9181 | -704692.9181 | -704692.9181 | -704692.9181 | -704692.9181 | -704692.9181
Option 2A | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | -8153541.9006 | 0 | 0 | 0 | 0 | 0 | 0 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332
Option 2A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -5621082.9817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407
Option 2A | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -2635297.1481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945
Option 2B | 1 | 3rd Narrabri Tx | 1 | $ | -1529819.5502 | 0 | 0 | 0 | 0 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959
Option 2B | 1 | New double circuit 132 kV line between Tamworth and Gunnedah; decommission existing 969 line | 1 | $ | -9117564.4385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -931057.3706 | -931057.3706 | -931057.3706 | -931057.3706 | -931057.3706 | -931057.3706 | -931057.3706 | -931057.3706 | -931057.3706 | -931057.3706 | -931057.3706 | -931057.3706 | -931057.3706
Option 2B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -6123943.3776 | 0 | 0 | 0 | 0 | 0 | 0 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407
Option 2B | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -2635297.1481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945
Option 2C | 1 | 3rd Narrabri Tx | 1 | $ | -1529819.5502 | 0 | 0 | 0 | 0 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959
Option 2C | 1 | Second 132 kV line between Tamworth and Gunnedah | 1 | $ | -6900845.5257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -704692.918 | -704692.918 | -704692.918 | -704692.918 | -704692.918 | -704692.918 | -704692.918 | -704692.918 | -704692.918 | -704692.918 | -704692.918 | -704692.918 | -704692.918
Option 2C | 1 | Upgrade existing 969 line to 135 MVA rating | 1 | $ | -8153541.9006 | 0 | 0 | 0 | 0 | 0 | 0 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332
Option 2C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -8995460.881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1006681.485 | -1006681.485 | -1006681.485 | -1006681.485 | -1006681.485 | -1006681.485 | -1006681.485 | -1006681.485 | -1006681.485 | -1006681.485 | -1006681.485 | -1006681.485
Option 2D | 1 | 3rd Narrabri Tx | 1 | $ | -1529819.5502 | 0 | 0 | 0 | 0 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959
Option 2D | 1 | 330 kV line between Tamworth and Gunnedah operated at 132 kV | 1 | $ | -18635691.0622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1903018.9077 | -1903018.9077 | -1903018.9077 | -1903018.9077 | -1903018.9077 | -1903018.9077 | -1903018.9077 | -1903018.9077 | -1903018.9077 | -1903018.9077 | -1903018.9077 | -1903018.9077 | -1903018.9077
Option 2D | 1 | Upgrade 969 line to 135 MVA rating | 1 | $ | -8153541.9006 | 0 | 0 | 0 | 0 | 0 | 0 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332 | -764245.2332
Option 2D | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -6123943.3776 | 0 | 0 | 0 | 0 | 0 | 0 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407 | -574007.5407
Option 2D | 2 | 50 MVAr SVC Narrabri 132 | 1 | $ | -2635297.1481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945
Option 3A | 1 | 3rd Narrabri Tx | 1 | $ | -1529819.5502 | 0 | 0 | 0 | 0 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959
Option 3A | 1 | Rebuild 969 line as double circuit | 1 | $ | -16282047.9893 | 0 | 0 | 0 | 0 | 0 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389
Option 3A | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -6123943.376 | 0 | 0 | 0 | 0 | 0 | 0 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406
Option 3A | 2 | 60 MVAr SVC at Narrabri 132 | 1 | $ | -2635297.1481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945 | -294915.945
Option 3B | 1 | 3rd Narrabri Tx | 1 | $ | -1529819.5502 | 0 | 0 | 0 | 0 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959
Option 3B | 1 | Rebuild 969 line as double circuit | 1 | $ | -16282047.9893 | 0 | 0 | 0 | 0 | 0 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389
Option 3B | 1 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -6123943.376 | 0 | 0 | 0 | 0 | 0 | 0 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406
Option 3B | 2 | Install 50 MW (50 MWh) BESS at Narrabri 132 | 1 | $ | -11787272.1426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1319112.915 | -1319112.915 | -1319112.915 | -1319112.915 | -1319112.915 | -1319112.915 | -1319112.915 | -1319112.915 | -1319112.915 | -1319112.915 | -1319112.915 | -1319112.915
Option 3C | 1 | 3rd Narrabri Tx | 1 | $ | -1529819.5502 | 0 | 0 | 0 | 0 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959
Option 3C | 1 | Rebuild 969 line as double circuit | 1 | $ | -16282047.9858 | 0 | 0 | 0 | 0 | 0 | -1407953.2386 | -1407953.2386 | -1407953.2386 | -1407953.2386 | -1407953.2386 | -1407953.2386 | -1407953.2386 | -1407953.2386 | -1407953.2386 | -1407953.2386 | -1407953.2386 | -1407953.2386 | -1407953.2386 | -1407953.2386 | -1407953.2386
Option 3C | 2 | New 132 kV line between Gunnedah and Narrabri | 1 | $ | -8995460.881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1006681.485 | -1006681.485 | -1006681.485 | -1006681.485 | -1006681.485 | -1006681.485 | -1006681.485 | -1006681.485 | -1006681.485 | -1006681.485 | -1006681.485 | -1006681.485
Option 5A | 1 | 3rd Narrabri Tx | 1 | $ | -1529819.5502 | 0 | 0 | 0 | 0 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959
Option 5A | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 5A | 2 | Rebuild 969 line as double circuit | 1 | $ | -12581127.6671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389
Option 5A | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -5129191.7586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406
Option 5B | 1 | 3rd Narrabri Tx | 1 | $ | -1529819.5502 | 0 | 0 | 0 | 0 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959 | -122582.6959
Option 5B | 1 | BESS | 0 | $ |  | Redacted to preserve confidentiality
Option 5B | 2 | Rebuild 969 line as double circuit | 1 | $ | -12581127.6671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389 | -1407953.2389
Option 5B | 2 | Upgrade 9UH line to 100 MVA rating | 1 | $ | -5129191.7586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406 | -574007.5406
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TNSP operating expenditure
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | -46568492.0535 | 0 | 0 | 0 | 0 | -1163325.3147 | -1163325.3147 | -3393570.5502 | -3967578.0906 | -4262494.0426 | -4262494.0426 | -4262494.0426 | -4262494.0426 | -4262494.0426 | -4262494.0426 | -4262494.0426 | -4262494.0426 | -4262494.0426 | -4262494.0426 | -4262494.0426 | -4262494.0426
Option 1B |  |  |  | $ | -34891539.4251 | 0 | 0 | 0 | 0 | -1163325.3147 | -1737332.8551 | -1737332.8551 | -1737332.8551 | -3274453.9851 | -3274453.9851 | -3274453.9851 | -3274453.9851 | -3274453.9851 | -3274453.9851 | -3274453.9851 | -3274453.9851 | -3274453.9851 | -3274453.9851 | -3274453.9851 | -3274453.9851
Option 2A |  |  |  | $ | -24840587.1062 | 0 | 0 | 0 | 0 | -122582.6959 | -122582.6959 | -886827.9291 | -2165528.3879 | -2460444.3328 | -2460444.3328 | -2460444.3328 | -2460444.3328 | -2460444.3328 | -2460444.3328 | -2460444.3328 | -2460444.3328 | -2460444.3328 | -2460444.3328 | -2460444.3328 | -2460444.3328
Option 2B |  |  |  | $ | -19406624.5144 | 0 | 0 | 0 | 0 | -122582.6959 | -122582.6959 | -696590.2366 | -1627647.6072 | -1922563.5522 | -1922563.5522 | -1922563.5522 | -1922563.5522 | -1922563.5522 | -1922563.5522 | -1922563.5522 | -1922563.5522 | -1922563.5522 | -1922563.5522 | -1922563.5522 | -1922563.5522
Option 2C |  |  |  | $ | -25579667.8575 | 0 | 0 | 0 | 0 | -122582.6959 | -122582.6959 | -886827.9291 | -1591520.8472 | -2598202.3322 | -2598202.3322 | -2598202.3322 | -2598202.3322 | -2598202.3322 | -2598202.3322 | -2598202.3322 | -2598202.3322 | -2598202.3322 | -2598202.3322 | -2598202.3322 | -2598202.3322
Option 2D |  |  |  | $ | -37078293.0386 | 0 | 0 | 0 | 0 | -122582.6959 | -122582.6959 | -1460835.4698 | -3363854.3775 | -3658770.3225 | -3658770.3225 | -3658770.3225 | -3658770.3225 | -3658770.3225 | -3658770.3225 | -3658770.3225 | -3658770.3225 | -3658770.3225 | -3658770.3225 | -3658770.3225 | -3658770.3225
Option 3A |  |  |  | $ | -26571108.0635 | 0 | 0 | 0 | 0 | -122582.6959 | -1530535.9349 | -2104543.4754 | -2104543.4754 | -2399459.4204 | -2399459.4204 | -2399459.4204 | -2399459.4204 | -2399459.4204 | -2399459.4204 | -2399459.4204 | -2399459.4204 | -2399459.4204 | -2399459.4204 | -2399459.4204 | -2399459.4204
Option 3B |  |  |  | $ | -35723083.058 | 0 | 0 | 0 | 0 | -122582.6959 | -1530535.9349 | -2104543.4754 | -2104543.4754 | -3423656.3904 | -3423656.3904 | -3423656.3904 | -3423656.3904 | -3423656.3904 | -3423656.3904 | -3423656.3904 | -3423656.3904 | -3423656.3904 | -3423656.3904 | -3423656.3904 | -3423656.3904
Option 3C |  |  |  | $ | -26807328.4171 | 0 | 0 | 0 | 0 | -122582.6959 | -1530535.9346 | -1530535.9346 | -1530535.9346 | -2537217.4196 | -2537217.4196 | -2537217.4196 | -2537217.4196 | -2537217.4196 | -2537217.4196 | -2537217.4196 | -2537217.4196 | -2537217.4196 | -2537217.4196 | -2537217.4196 | -2537217.4196
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
TNSP NNO operating expenditure
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
NNO operating expenditure
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided fuel consumption from generation dispatch
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided voluntary load curtailment
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding outside of NW Slopes
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding in NW Slopes
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 447063297.161 | 0 | 0 | 0 | 0 | 0 | 0 | 137369611.3556 | 381263088.9255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 807000711.8183 | 0 | 0 | 0 | 0 | 0 | 267527640.2875 | 274739222.7112 | 381263088.9255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 374857551.8482 | 0 | 0 | 0 | 0 | 0 | 0 | 54947844.5422 | 381263088.9255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 471131878.932 | 0 | 0 | 0 | 0 | 0 | 0 | 164843533.6267 | 381263088.9255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 519269042.4738 | 0 | 0 | 0 | 0 | 0 | 0 | 219791378.169 | 381263088.9255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 374857551.8482 | 0 | 0 | 0 | 0 | 0 | 0 | 54947844.5422 | 381263088.9255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 866323700.9032 | 0 | 0 | 0 | 0 | 64794250.2222 | 267527640.2875 | 274739222.7112 | 381263088.9255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 866323700.9032 | 0 | 0 | 0 | 0 | 64794250.2222 | 267527640.2875 | 274739222.7112 | 381263088.9255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 866323700.9032 | 0 | 0 | 0 | 0 | 64794250.2222 | 267527640.2875 | 274739222.7112 | 381263088.9255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided costs for non RIT-T proponent parties
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (wood pole replacement)
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 762613.1764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6182.5185 | 6182.5185 | 43277.6293 | 43277.6293 | 43277.6293 | 43277.6293 | 43277.6293 | 111285.3325 | 111285.3325 | 111285.3325 | 111285.3325 | 111285.3325 | 290578.3682
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 773566.372 | 0 | 0 | 0 | 0 | 0 | 6182.5185 | 6182.5185 | 6182.5185 | 6182.5185 | 43277.6293 | 43277.6293 | 43277.6293 | 43277.6293 | 43277.6293 | 111285.3325 | 111285.3325 | 111285.3325 | 111285.3325 | 111285.3325 | 290578.3682
Option 3B |  |  |  | $ | 773566.372 | 0 | 0 | 0 | 0 | 0 | 6182.5185 | 6182.5185 | 6182.5185 | 6182.5185 | 43277.6293 | 43277.6293 | 43277.6293 | 43277.6293 | 43277.6293 | 111285.3325 | 111285.3325 | 111285.3325 | 111285.3325 | 111285.3325 | 290578.3682
Option 3C |  |  |  | $ | 773566.372 | 0 | 0 | 0 | 0 | 0 | 6182.5185 | 6182.5185 | 6182.5185 | 6182.5185 | 43277.6293 | 43277.6293 | 43277.6293 | 43277.6293 | 43277.6293 | 111285.3325 | 111285.3325 | 111285.3325 | 111285.3325 | 111285.3325 | 290578.3682
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (market benefits)
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality
NNO receipts received from TNSP
Option |  |  |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  |  |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  |  |  | $ |  | Redacted to preserve confidentiality
Option 5B |  |  |  | $ |  | Redacted to preserve confidentiality

## Weighted
Weighted | NPV results
NPV results
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  | $ | 109406443.8586 | 0 | -3069665.1845 | -12581365.3821 | -66100394.967 | -60888614.6923 | -44610450.8384 | 81027199.1391 | 238306266.215 | -4392005.0869 | -4392005.0869 | -4392005.0869 | -4392005.0869 | -4392005.0869 | -4392005.0869 | -4392005.0869 | -4392005.0869 | -4392005.0869 | -4392005.0869 | -4392005.0869 | 126560111.7612
Option 1B |  | $ | 337694798.3598 | 0 | -2493880.831 | -13805201.1808 | -70056228.5992 | -29049251.807 | 147930103.6845 | 152831501.7087 | 212594061.4745 | -3486301.7008 | -3486301.7008 | -3486301.7008 | -3486301.7008 | -3486301.7008 | -3486301.7008 | -3486301.7008 | -3486301.7008 | -3486301.7008 | -3486301.7008 | -3486301.7008 | 138661583.9891
Option 2A |  | $ | 118174025.0145 | 0 | -1204301.9723 | -4390462.7647 | -20541286.5437 | -28553076.382 | -70323894.4492 | 16176387.6764 | 240098165.924 | -2600105.4776 | -2600105.4776 | -2600105.4776 | -2600105.4776 | -2600105.4776 | -2600105.4776 | -2600105.4776 | -2600105.4776 | -2600105.4776 | -2600105.4776 | -2600105.4776 | 104285567.3752
Option 2B |  | $ | 186456499.9852 | 0 | -1049562.1208 | -4235487.7119 | -20029025.7167 | -26707771.6999 | -68145929.2469 | 99488265.6464 | 240504082.3173 | -2194189.0843 | -2151123.8866 | -2151123.8866 | -2151123.8866 | -2151123.8866 | -2151123.8866 | -2072171.0243 | -2072171.0243 | -2072171.0243 | -2072171.0243 | -2072171.0243 | 94420542.8209
Option 2C |  | $ | 185702070.7458 | 0 | -1078910.3208 | -5677225.3235 | -24194685.7026 | -35661171.0663 | -83631410.4472 | 105968425.0549 | 247589767.0655 | -2726383.6436 | -2726383.6436 | -2726383.6436 | -2726383.6436 | -2726383.6436 | -2726383.6436 | -2726383.6436 | -2726383.6436 | -2726383.6436 | -2726383.6436 | -2726383.6436 | 133572740.4573
Option 2D |  | $ | 63899154.8852 | 0 | -1296565.2194 | -4828293.4191 | -24624256.6798 | -41489420.2175 | -154670988.5998 | 32518316.8112 | 238500397.9378 | -4197873.4638 | -4197873.4638 | -4197873.4638 | -4197873.4638 | -4197873.4638 | -4197873.4638 | -4197873.4638 | -4197873.4638 | -4197873.4638 | -4197873.4638 | -4197873.4638 | 164857138.337
Option 3A |  | $ | 410313981.9607 | 0 | -1799833.1063 | -6359817.6451 | -27926311.3321 | -32687105.9291 | 158830898.9237 | 175481735.0813 | 239868221.1596 | -2830050.2419 | -2786985.0443 | -2786985.0443 | -2786985.0443 | -2786985.0443 | -2786985.0443 | -2708032.1819 | -2708032.1819 | -2708032.1819 | -2708032.1819 | -2708032.1819 | 93355002.5273
Option 3B |  | $ | 368223338.9817 | 0 | -1799833.1063 | -6359817.6451 | -27926311.3321 | -35241512.8666 | 143052509.2362 | 140037081.3313 | 246703310.4096 | -3768897.4644 | -3725832.2668 | -3725832.2668 | -3725832.2668 | -3725832.2668 | -3725832.2668 | -3646879.4044 | -3646879.4044 | -3646879.4044 | -3646879.4044 | -3646879.4044 | 95046137.1235
Option 3C |  | $ | 397824329.6473 | 0 | -1619195.7017 | -7344938.3786 | -23656626.7544 | -39489351.6158 | 155732211.4488 | 142393054.7231 | 247359822.3014 | -2956328.4077 | -2913263.2101 | -2913263.2101 | -2913263.2101 | -2913263.2101 | -2913263.2101 | -2834310.3477 | -2834310.3477 | -2834310.3477 | -2834310.3477 | -2834310.3477 | 123393852.1411
Option 5A |  | $ | 507163018.5112 | Redacted to preserve confidentiality
Option 5B |  | $ | 539983166.6711 | Redacted to preserve confidentiality
Weighted | Calculation
TNSP capital costs
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  | $ | -127213705.31 | 0 | -3069665.1845 | -12581365.3821 | -66100394.967 | -67324797.1268 | -51485374.0152 | -11032672.6251 | -8005985.0437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130952116.848
Option 1B |  | $ | -114308251.14 | 0 | -2493880.831 | -13805201.1808 | -70056228.5992 | -35485434.2415 | -28195802.25 | -27923456.6875 | -35762581.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142147885.6899
Option 2A |  | $ | -81778552.4681 | 0 | -1204301.9723 | -4390462.7647 | -20541286.5437 | -28389632.7874 | -70160450.8546 | -24613154.0204 | -8005984.9375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106885672.8528
Option 2B |  | $ | -71032031.6051 | 0 | -1049562.1208 | -4235487.7119 | -20029025.7167 | -26544328.1053 | -67982485.6523 | -9521456.6167 | -8005984.9375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96284565.3898
Option 2C |  | $ | -95869128.0024 | 0 | -1078910.3208 | -5677225.3235 | -24194685.7026 | -35497727.4717 | -83467966.8526 | -39433359.1358 | -1040557.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136299124.1009
Option 2D |  | $ | -124805202.2943 | 0 | -1296565.2194 | -4828293.4191 | -24624256.6798 | -41325976.6229 | -154507545.0052 | -7745051.3066 | -8005984.9375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169055011.8008
Option 3A |  | $ | -77917691.5134 | 0 | -1799833.1063 | -6359817.6451 | -27926311.3321 | -75639911.0736 | -17338743.9622 | -4790786.6875 | -8005984.9375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95854886.2539
Option 3B |  | $ | -113674976.8347 | 0 | -1799833.1063 | -6359817.6451 | -27926311.3321 | -78194318.0111 | -33117133.6497 | -40235440.4375 | -1170895.6875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98484868.0726
Option 3C |  | $ | -90344767.1024 | 0 | -1619195.7017 | -7344938.3786 | -23656626.7544 | -82442156.7603 | -20437431.4375 | -38405640.625 | -1040557.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126020014.0335
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
NNO capital costs
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
TNSP operating expenditure
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  | $ | -36723437.9734 | 0 | 0 | 0 | 0 | -1551100.4196 | -1551100.4196 | -3595491.8855 | -4121665.4642 | -4392005.0869 | -4392005.0869 | -4392005.0869 | -4392005.0869 | -4392005.0869 | -4392005.0869 | -4392005.0869 | -4392005.0869 | -4392005.0869 | -4392005.0869 | -4392005.0869 | -4392005.0869
Option 1B |  | $ | -28371555.3087 | 0 | 0 | 0 | 0 | -1551100.4196 | -2077273.9983 | -2077273.9983 | -2077273.9983 | -3486301.7008 | -3486301.7008 | -3486301.7008 | -3486301.7008 | -3486301.7008 | -3486301.7008 | -3486301.7008 | -3486301.7008 | -3486301.7008 | -3486301.7008 | -3486301.7008 | -3486301.7008
Option 2A |  | $ | -19399938.7965 | 0 | 0 | 0 | 0 | -163443.5946 | -163443.5946 | -864001.725 | -2329765.8614 | -2600105.4776 | -2600105.4776 | -2600105.4776 | -2600105.4776 | -2600105.4776 | -2600105.4776 | -2600105.4776 | -2600105.4776 | -2600105.4776 | -2600105.4776 | -2600105.4776 | -2600105.4776
Option 2B |  | $ | -16075054.9689 | 0 | 0 | 0 | 0 | -163443.5946 | -163443.5946 | -689617.1736 | -1931027.001 | -2201366.6172 | -2201366.6172 | -2201366.6172 | -2201366.6172 | -2201366.6172 | -2201366.6172 | -2201366.6172 | -2201366.6172 | -2201366.6172 | -2201366.6172 | -2201366.6172 | -2201366.6172
Option 2C |  | $ | -19865761.6735 | 0 | 0 | 0 | 0 | -163443.5946 | -163443.5946 | -864001.725 | -1803592.2824 | -2726383.6436 | -2726383.6436 | -2726383.6436 | -2726383.6436 | -2726383.6436 | -2726383.6436 | -2726383.6436 | -2726383.6436 | -2726383.6436 | -2726383.6436 | -2726383.6436 | -2726383.6436
Option 2D |  | $ | -30648159.0996 | 0 | 0 | 0 | 0 | -163443.5946 | -163443.5946 | -1390175.304 | -3927533.8476 | -4197873.4638 | -4197873.4638 | -4197873.4638 | -4197873.4638 | -4197873.4638 | -4197873.4638 | -4197873.4638 | -4197873.4638 | -4197873.4638 | -4197873.4638 | -4197873.4638 | -4197873.4638
Option 3A |  | $ | -23202291.0854 | 0 | 0 | 0 | 0 | -163443.5946 | -2040714.5798 | -2566888.1586 | -2566888.1586 | -2837227.7749 | -2837227.7749 | -2837227.7749 | -2837227.7749 | -2837227.7749 | -2837227.7749 | -2837227.7749 | -2837227.7749 | -2837227.7749 | -2837227.7749 | -2837227.7749 | -2837227.7749
Option 3B |  | $ | -29535648.7431 | 0 | 0 | 0 | 0 | -163443.5946 | -2040714.5798 | -2566888.1586 | -2566888.1586 | -3776074.9974 | -3776074.9974 | -3776074.9974 | -3776074.9974 | -3776074.9974 | -3776074.9974 | -3776074.9974 | -3776074.9974 | -3776074.9974 | -3776074.9974 | -3776074.9974 | -3776074.9974
Option 3C |  | $ | -23264867.8099 | 0 | 0 | 0 | 0 | -163443.5946 | -2040714.5794 | -2040714.5794 | -2040714.5794 | -2963505.9406 | -2963505.9406 | -2963505.9406 | -2963505.9406 | -2963505.9406 | -2963505.9406 | -2963505.9406 | -2963505.9406 | -2963505.9406 | -2963505.9406 | -2963505.9406 | -2963505.9406
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
TNSP NNO operating expenditure
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
NNO operating expenditure
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Avoided fuel consumption from generation dispatch
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Avoided voluntary load curtailment
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding outside of NW Slopes
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Avoided involuntary load shedding in NW Slopes
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  | $ | 273343587.142 | 0 | 0 | 0 | 0 | 7987282.854 | 8426023.5965 | 95655363.6496 | 250433916.7228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 480374604.8085 | 0 | 0 | 0 | 0 | 7987282.854 | 178203179.9328 | 182832232.3945 | 250433916.7228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 219352516.2791 | 0 | 0 | 0 | 0 | 0 | 0 | 41653543.4217 | 250433916.7228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 272976731.3542 | 0 | 0 | 0 | 0 | 0 | 0 | 109699339.4367 | 250433916.7228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 301436960.4216 | 0 | 0 | 0 | 0 | 0 | 0 | 146265785.9156 | 250433916.7228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 219352516.2791 | 0 | 0 | 0 | 0 | 0 | 0 | 41653543.4217 | 250433916.7228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 510836230.7203 | 0 | 0 | 0 | 0 | 43116248.7391 | 178203179.9328 | 182832232.3945 | 250433916.7228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ | 510836230.7203 | 0 | 0 | 0 | 0 | 43116248.7391 | 178203179.9328 | 182832232.3945 | 250433916.7228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  | $ | 510836230.7203 | 0 | 0 | 0 | 0 | 43116248.7391 | 178203179.9328 | 182832232.3945 | 250433916.7228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Avoided costs for non RIT-T proponent parties
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (wood pole replacement)
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 586855.2049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7177.5329 | 7177.5329 | 50242.7306 | 50242.7306 | 50242.7306 | 50242.7306 | 50242.7306 | 129195.593 | 129195.593 | 129195.593 | 129195.593 | 129195.593 | 337344.0483
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 597733.8392 | 0 | 0 | 0 | 0 | 0 | 7177.5329 | 7177.5329 | 7177.5329 | 7177.5329 | 50242.7306 | 50242.7306 | 50242.7306 | 50242.7306 | 50242.7306 | 129195.593 | 129195.593 | 129195.593 | 129195.593 | 129195.593 | 337344.0483
Option 3B |  | $ | 597733.8392 | 0 | 0 | 0 | 0 | 0 | 7177.5329 | 7177.5329 | 7177.5329 | 7177.5329 | 50242.7306 | 50242.7306 | 50242.7306 | 50242.7306 | 50242.7306 | 129195.593 | 129195.593 | 129195.593 | 129195.593 | 129195.593 | 337344.0483
Option 3C |  | $ | 597733.8392 | 0 | 0 | 0 | 0 | 0 | 7177.5329 | 7177.5329 | 7177.5329 | 7177.5329 | 50242.7306 | 50242.7306 | 50242.7306 | 50242.7306 | 50242.7306 | 129195.593 | 129195.593 | 129195.593 | 129195.593 | 129195.593 | 337344.0483
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
Avoided unrelated TNSP expenditure (market benefits)
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality
NNO receipts received from TNSP
Option |  | Unit | PV | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Option 1A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 1B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 2D |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3A |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3B |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 3C |  | $ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Option 5A |  | $ |  | Redacted to preserve confidentiality
Option 5B |  | $ |  | Redacted to preserve confidentiality

## Timing sensitivity results
NPV results - no change | [7 empty] | 5B |  |  |  |  | 5B
[8 empty] | no change | 1 year delay | 2 year delay |  |  | no change | 1 year delay | 2 year delay
Option | Unit | Central | Low | High | Weighted | 3A | no change | 129.6692 | 123.5866 | -13.1254 | 3A | no change | 131.6% | 130.1% | 96.8%
Option 3A | $NPV | 439.1746 | -21.096 | 784.0028 | 410.314 |  | 1 year forward | 24.6098 | 18.5272 | -118.1848 |  | 1 year forward | 104.8% | 103.6% | 77.07%
Option 5B | $NPV | 566.9444 | 19.3535 | 1006.6905 | 539.9832 |  | 2 years forward | 21.4775 | 15.3949 | -121.3171 |  | 2 years forward | 104.1% | 103% | 76.6%
NPV results - 1 year delay
Option | Unit | Central | Low | High | Weighted
Option 3A | $NPV | 439.1746 | -21.096 | 784.0028 | 410.314
Option 5B | $NPV | 559.1624 | 26.7353 | 990.5421 | 533.9006
NPV results - 2 year delay
Option | Unit | Central | Low | High | Weighted
Option 3A | $NPV | 439.1746 | -21.096 | 784.0028 | 410.314
Option 5B | $NPV | 407.4349 | 12.088 | 761.7967 | 397.1886
NPV results - 2 year delay, 1 year forward
Option | Unit | Central | Low | High | Weighted
Option 3A | $NPV | 555.139 | -11.6535 | 962.869 | 515.3734
Option 5B | $NPV | 407.4349 | 12.088 | 761.7967 | 397.1886
NPV results - 2 year delay, 2 year forward
Option | Unit | Central | Low | High | Weighted
Option 3A | $NPV | 558.7036 | -19.4721 | 976.0875 | 518.5057
Option 5B | $NPV | 407.4349 | 12.088 | 761.7967 | 397.1886
NPV results - 1 year delay, 2 year forward
Option | Unit | Central | Low | High | Weighted
Option 3A | $NPV | 558.7036 | -19.4721 | 976.0875 | 518.5057
Option 5B | $NPV | 559.1624 | 26.7353 | 990.5421 | 533.9006
NPV results - 1 year delay, 1 year forward
Option | Unit | Central | Low | High | Weighted
Option 3A | $NPV | 555.139 | -11.6535 | 962.869 | 515.3734
Option 5B | $NPV | 559.1624 | 26.7353 | 990.5421 | 533.9006
NPV results - no delay, 1 year forward
Option | Unit | Central | Low | High | Weighted
Option 3A | $NPV | 555.139 | -11.6535 | 962.869 | 515.3734
Option 5B | $NPV | 566.9444 | 19.3535 | 1006.6905 | 539.9832
NPV results - no delay, 2 years forward
Option | Unit | Central | Low | High | Weighted
Option 3A | $NPV | 558.7036 | -19.4721 | 976.0875 | 518.5057
Option 5B | $NPV | 566.9444 | 19.3535 | 1006.6905 | 539.9832

## Line 969 costs
|  |  |  | Annualised cost |  |  | Central
Optimal year of wood pole replacement | Mid point | Quantity | Replacement Cost (based on $125k/pole) | Central (S1) | Low (S2) | High (S3) | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
2026-2028 | 2027 | 1 | 125000 | -7790.0429 | -9925.0392 | -4755.7834 | [5 empty] | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429 | -7790.0429
2029-2033 | 2031 | 6 | 750000 | -46740.2575 | -59550.2354 | -28534.7006 | Central 2031: -46740.2575; Central 2032: -46740.2575; Central 2033: -46740.2575; Central 2034: -46740.2575; Central 2035: -46740.2575; Central 2036: -46740.2575; Central 2037: -46740.2575; Central 2038: -46740.2575; Central 2039: -46740.2575; Central 2040: -46740.2575; Central 2041: -46740.2575
2034-2038 | 2036 | 11 | 1375000 | -85690.4721 | -109175.4315 | -52313.6178 | Central 2036: -85690.4721; Central 2037: -85690.4721; Central 2038: -85690.4721; Central 2039: -85690.4721; Central 2040: -85690.4721; Central 2041: -85690.4721
2039-2043 | 2041 | 29 | 3625000 | -225911.2447 | -287826.1375 | -137917.7197 | Central 2041: -225911.2447
2044-2046 | 2045 | 19 | 2375000 | -148010.8155 | -188575.7453 | -90359.8854
Total |  | 66 | 8250000 | -514142.8327 | -655052.5889 | -313881.707 | 0 | 0 | 0 | 0 | 0 | 7790.0429 | 7790.0429 | 7790.0429 | 7790.0429 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 54530.3004 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 140220.7726 | 366132.0172
Asset life of wood poles | [6 empty] | Central 2022: Low
40 | [6 empty] | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
[12 empty] | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392 | -9925.0392
[16 empty] | -59550.2354 | -59550.2354 | -59550.2354 | -59550.2354 | -59550.2354 | -59550.2354 | -59550.2354 | -59550.2354 | -59550.2354 | -59550.2354 | -59550.2354
[21 empty] | -109175.4315 | -109175.4315 | -109175.4315 | -109175.4315 | -109175.4315 | -109175.4315
-287826.1375
[7 empty] | 0 | 0 | 0 | 0 | 0 | 9925.0392 | 9925.0392 | 9925.0392 | 9925.0392 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 69475.2746 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 178650.7061 | 466476.8436
High
[7 empty] | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
[12 empty] | -4755.7834 | -4755.7834 | -4755.7834 | -4755.7834 | -4755.7834 | -4755.7834 | -4755.7834 | -4755.7834 | -4755.7834 | -4755.7834 | -4755.7834 | -4755.7834 | -4755.7834 | -4755.7834 | -4755.7834
[16 empty] | -28534.7006 | -28534.7006 | -28534.7006 | -28534.7006 | -28534.7006 | -28534.7006 | -28534.7006 | -28534.7006 | -28534.7006 | -28534.7006 | -28534.7006
[21 empty] | -52313.6178 | -52313.6178 | -52313.6178 | -52313.6178 | -52313.6178 | -52313.6178
-137917.7197
[7 empty] | 0 | 0 | 0 | 0 | 0 | 4755.7834 | 4755.7834 | 4755.7834 | 4755.7834 | 33290.4841 | 33290.4841 | 33290.4841 | 33290.4841 | 33290.4841 | 85604.1019 | 85604.1019 | 85604.1019 | 85604.1019 | 85604.1019 | 223521.8217