## Queanbeyan BESS
Generator name | Capacity (MW) | (1) Ancillary service requirements | (2) Level and pattern of network congestion | (3) Impact on timing of expenditure on the network | (4) Impact on interconnector power transfer capability
Queanbeyan BESS | 10 | There were no new ancillary service contracts in Southern NSW in the 12 months prior to, or following, the commissioning of the Queanbeyan BESS. | The connection of Queanbeyan BESS has increased the generation capacity in Southern NSW. When Queanbeyan BESS is generating, it has the potential to increase the utilisation of surrounding Southern NSW 132 kV network lines 976/1 and 976/2 In the 12 months prior to the connection of Queanbeyan BESS, the constraint equation for avoiding overloading of line 976/1 and 977/1 during the outage of 977/1 or 976/1 constrained for approximately 0 hours, and in the 12 months following for approx 1.3 hours. There are many factors that impact line 976/1 and 977/1 overloading constraint equation: - the relative operation of the existing generating units in Southern NSW - NEM dispatch price in NSW. - network outages (planned and unplanned) significantly impact the power transfer limits. All of the above have a far greater impact on the utilisation of Southern NSW network, compared to a connection of any single BESS in Southern NSW. The constraints in the NEM dispatch system, can also not specifically by attributed to any single generator. Therefore, it cannot be said that the connection of Queanbeyan BESS has specifically had a material impact on network congestion in the surrounding 132 kV network, however it is a contributing factor. | No project timings have been affected by the inclusion of Queanbeyan BESS. | Queanbeyan BESS has positive contribution factor in constraint equation for overloading of line 976/1 and 977/1, which means it will increase loading on these line. Queanbeyan BESS is in Southern area of NSW and power transfer capability between Victoria and NSW and vice versa.