## Bomen SF
Generator name | Capacity (MW) | (1) Ancillary service requirements | (2) Level and pattern of network congestion | (3) Impact on timing of expenditure on the network | (4) Impact on interconnector power transfer capability
Bomen Solar Farm | 100 | There were no new ancillary service contracts in South East NSW in the 12 months prior to, or following, the commissioning of the Bomen SF. | The connection of Bomen SF has increased the generation capacity in South East NSW. When Bomen SF is generating, it has the potential to increase the utilisation of some South East NSW 132kV network lines (i.e. the utilisation of 132kV lines: 991 from Wagga North to Murrumburah, 990 from Wagga 132kV to Yass and 993 from Wagga to Gadara) . At present the connection of Bomen SF has no impact on any constraint equation in a nearby network. Connection of Bomen SF has not specifically had a material impact on network congestion in the main 330kV, 220kV and 132 kV system network. Localised historical transmission line flows were investigated surrounding Bomen SF in the South East 132kV network, showing congestion may occur due to impact of Bomen SF. This is managed by various runback and transfer trip schemes, such as: thermal overload of lines 990 and 993 and system strength in case of outage of lines 9R5, 9R6 and bus section CB 4102. | No project timings have been affected by the inclusion of Bomen SF. | Bomen SF is in South East area of NSW and does not have significant influence on Victoria interconnector power capability.