## Sunraysia SF
Generator name | Capacity (MW) | (1) Ancillary service requirements | (2) Level and pattern of network congestion | (3) Impact on timing of expenditure on the network | (4) Impact on interconnector power transfer capability
Gunnedah SF | 110 | There were no new ancillary service contracts in Northern NSW in the 12 months prior to, or following, the commissioning of the Gunnedah SF. | The connection of Gunnedah SF has increased the generation capacity in Northern NSW. When Gunnedah SF is generating, it has the potential to increase the utilisation of surrounding Northern NSW 132 kV network lines from Tamworth to Narrabri such as 969, 968, 9U3, 9UH and 9UJ . In the 12 months prior to the connection of Gunnedah SF, the constraint equation for avoiding overloading of line 969 during system normal constrained for approximately 0 hours, and in the 12 months following for approx 183.5 hours. There are many factors that impact line 969 overloading constraint equation: - the relative operation of the existing generating units in Northern NSW - NEM dispatch price in NSW. - network outages (planned and unplanned) significantly impact the power transfer limits. All of the above have a far greater impact on the utilisation of Northern NSW network, compared to a connection of any single SF in Northern NSW. The constraints in the NEM dispatch system, can also not specifically by attributed to any single generator. Connection of Gunnedah SF has had a material impact on network congestion in the 132 kV network between Tamworth and Narrabri. Output of Gunnedah SF has a direct influence on overloading of line 969 and surrounding lines in the 132 kV network. Possible congestion of the 132 kV lines surrounding Gunnedah SF is managed by constraint equation in NEMDE and the following transfer tripping schemes: - Anti-islanding protection addressing trip of 132 kV lines 9UH, 9UJ, 9U3, 968. - Runback/Trip schemes to prevent overloads of line 969 during network contingency. | No project timings have been affected by the inclusion of Gunnedah SF. | Gunnedah SF has positive contribution factor in constraint equation for overloading of line 969, which means it will increase loading on this line. Gunnedah SF is in Northern area of NSW and has a minimal influence on Queensland interconnector power capability.