## Silverton WF
Generator name | Capacity (MW) | (1) Ancillary service requirements | (2) Level and pattern of network congestion | (3) Impact on timing of expenditure on the network | (4) Impact on interconnector power transfer capability
Finley Solar Farm | 135 | There were no new ancillary service contracts in South Western NSW in the 12 months prior to, or following, the commissioning of the Finley SF. | The connection of Finley SF has increased the generation capacity in South Western NSW. When Finley SF is generating, it has the potential to reduce the power transfer from VNI into Wagga (i.e. reduced utilisation of lines 63) and increase the utilisation of South Western NSW 132kV network lines (i.e. the utilisation of 132kV line 99T from Coleambally to Darlington Point and 132 kV lines between Finley and Uranquinty). In the 12 months prior to the connection of Finley SF, the constraint equation for voltage stability limitations at Darlington Point constrained for approximately 2060 hours, and in the 12 months following for approx 536 hours. The constraint equation for avoiding overloading of line 99T constrained for approximately 448 hours in the 12 months prior to the connection of Finley SF, and in the 12 months following for approx 584 hours.. There are many factors that impact the operation of Darlington Point Voltage and 99T overloading constraint equation: - the relative operation of the existing generating units in NSW - NEM dispatch price in NSW and VIC - network outages (planned and unplanned) significantly impact the power transfer limits. All of the above have a far greater impact on the utilisation of VNI and the South Western NSW network compared to a connection of any single SF in South Western NSW. The constraints in the NEM dispatch system can also not specifically by attributed to any single generator. Therefore, it cannot be said that the connection of Finley SF has specifically had a material impact on network congestion in the main 330, 220 kV and 132 kV system network, however it is a contributing factor. Localised historical transmission line flows were investigated surrounding Finley SF in the south western 132kV network, showing congestion may occur due to Finley SF. This is managed by runback and transfer trip schemes in operation and lines were well utilised but did not exceed contingency ratings. | No project timings have been affected by the inclusion of the Finley SF. Timing of upgrades to the VNI to NSW interconnector identified in Section 2.1.2 of TransGrid's 2020 TAPR is not specifically affected by the Finley SF. | Finley SF has negative contribution factor in Darlington Point voltage stability limit equation, which menas it will improve the transfer capability of VNI. The Finley SF has no direct impact on the southerly or northerly power transfer capability between QLD and NSW .