## Goonunmbla SF
Generator name | Capacity (MW) | (1) Ancillary service requirements | (2) Level and pattern of network congestion | (3) Impact on timing of expenditure on the network | (4) Impact on interconnector power transfer capability
Goonunmbla Solar Farm | 70 | There were no new ancillary service contracts in Central West NSW in the 12 months prior to, or following, the commissioning of the Goonunmbla SF. | The connection of Goonunmbla SF has increased the generation capacity in Central West NSW. When Goonunmbla SF is generating, it has the potential to increase the utilisation of some Central West NSW 132kV network lines (i.e. the utilisation of 132kV line 94H from Parkes to Manildra) . During generating, Goonumbla SF also increases loading on 132kV line 94T. In the 12 months prior to the connection of Goonunmbla SF, the constraint equation for avoiding overloading on 94T constrained for approximately 0 hours, and in the 12 months following for approx 130 hours. There are many factors that impact 94T overloading constraint equation: - the relative operation of the existing generating units in Central West NSW - NEM dispatch price in NSW. - network outages (planned and unplanned) significantly impact the power transfer limits. All of the above have a far greater impact on the utilisation of Central West NSW network, compared to a connection of any single SF in Central West NSW. The constraints in the NEM dispatch system, can also not specifically by attributed to any single generator. Connection of Goonumbla SF has not specifically had a material impact on network congestion in the main 330kV and 132 kV system network, however it is a contributing factor to overloading of 132kV line 94T. Localised historical transmission line flows were investigated surrounding Goonumbla SF in the Central West 132kV network, showing congestion may occur due to impact of Goonumbla SF. This is managed by various transfer trips and runback schemes, such as: anti islanding and thermal schemes for managing outage of either transformer at Parkes substation and system strength schemes for managing outages of nearby 132kV lines 94K, 94H, 94P, 94U amd 998. | No project timings have been affected by the inclusion of Goonumbla SF. | Goonumbla SF has positive contribution factor in constraint equation for overloading of line 94T, which means it will increase loading on this line. Goonumbla SF is in Central West area of NSW and does not have direct influence on either Victoria or Queensland interconnector power capability.