## Queanbeyan BESS
Generator name | Capacity (MW) | (1) Ancillary service requirements | (2) Level and pattern of network congestion | (3) Impact on timing of expenditure on the network | (4) Impact on interconnector power transfer capability
Avonlie SF | 190 MW | There were no new ancillary service contracts in Southern NSW in the 12 months prior to, or following, the commissioning of the Avonlie SF. | The connection of Avonlie SF has increased the generation capacity in Southern NSW. When Avonlie SF is generating, it has the potential to increase the utilisation of surrounding Southern NSW 132 kV network lines 99F, 994, 9HR and 9HT. In the 12 months prior to the connection of Avonlie SF, the constraint equation for avoiding overloading of line 99F constrained for approximately 15.3 hours, and in the 12 months following for approx 156.3 hours. There are many factors that impact line 99F overloading constraint equation: - the relative operation of the existing generating units in Southern NSW - NEM dispatch price in NSW. - network outages (planned and unplanned) significantly impact the power transfer limits. Connection of Avonlie SF has had a material impact on network congestion in the 132 kV network around Narrendra. Output of Avonlie SF has a direct influence on overloading of line 99F and surrounding lines in the 132 kV network. Possible congestion of the 132 kV lines surrounding Avonlie SF is managed by constraint equation in NEMDE. | No project timings have been affected by the inclusion of Avonlie SF. | Avonlie SF has positive contribution factor in constraint equation for overloading of line 99F, which means it will increase loading on these line. Avonlie SF is in Southern area of NSW and power transfer capability between Victoria and NSW and vice versa.