## New England SF
Generator name | Capacity (MW) | (1) Ancillary service requirements | (2) Level and pattern of network congestion | (3) Impact on timing of expenditure on the network | (4) Impact on interconnector power transfer capability
Metz SF | 115 MW | There were no new ancillary service contracts in Northern NSW in the 12 months prior to, or following, the commissioning of the Metz SF. | The connection of Metz SF has increased the generation capacity in Northern NSW. When Metz SF is generating, it has the potential to increase the utilisation of surrounding Northern NSW 330 and 132 kV network lines. In the 12 months prior to the connection of Metz SF, the constraint equation for avoiding overloading of line 966/1 constrained for approximately 0 hours, and in the 12 months following for approx 125 hours. Additionally, the constraint equations for avoiding overloading of line 85 (or 86) during the trip of line 86 (or 85) constrained for approximately 38 (71.6) hours, and in the 12 months following for approx 76 (61.9) hours. There are many factors that impact line 966/1 overloading constraint equation: - the relative operation of the existing generating units in Northern NSW - NEM dispatch price in NSW. - network outages (planned and unplanned) significantly impact the power transfer limits. Connection of Metz SF has had a material impact on network congestion in the 330 and 132 kV network around Armidale and Koolkhan. Output of Metz SF has a direct influence on overloading of line 966/1 and surrounding lines in the 330 and 132 kV network. Possible congestion of the 330 kV lines surrounding Metz SF is managed by constraint equation in NEMDE. | No project timings have been affected by the inclusion of Metz SF. | Metz SF has positive contribution factor in constraint equation for overloading of line 966/1 and 85(86), which means it will increase loading on these lines. Metz SF is in Northern area of NSW and has a minimal impact on Queensland interconnector transfer capacity.