## Sunraysia SF
Generator name | Capacity (MW) | (1) Ancillary service requirements | (2) Level and pattern of network congestion | (3) Impact on timing of expenditure on the network | (4) Impact on interconnector power transfer capability
Collector Wind Farm | 227 | There were no new ancillary service contracts in Southern NSW in the 12 months prior to, or following, the commissioning of the Collector WF. | The connection of Collector WF has increased the generation capacity in Southern NSW. On outage of one of 330 kV lines 3L, 4, 5, 6 and 8 Collector WF output may be constrained. Transfer capability between Yass - Canberra and Bannaby-Marulan can be constrained during outages of parallel 330 kV lines in the vicinity. Confirm AEMO constraint equation meaning. There are many factors that impact the operation of Collector Wind Farm constraint equation: - the relative operation of the existing generating units in NSW - NEM dispatch price in NSW and VIC - network outages (planned and unplanned) significantly impact the power transfer limits. All of the above have a far greater impact on the utilisation of Southern NSW network compared to a connection of any single renewable generator in Southern NSW. The constraints in the NEM dispatch system can also not specifically by attributed to any single generator. Therefore, it cannot be said that the connection of Collector WF has specifically had a material impact on network congestion in the main 330 kV system network, however it is a contributing factor. | No project timings have been affected by the inclusion of the Collector WF. | The Collector WF has minimal impact on power transfer capability between Victoria and NSW and vice versa.
Note on D1: Dragana Hele: Compare it with constraint spreadsheet