## Sunraysia SF
Generator name | Capacity (MW) | (1) Ancillary service requirements | (2) Level and pattern of network congestion | (3) Impact on timing of expenditure on the network | (4) Impact on interconnector power transfer capability
Limondale 2 SF | 30 | There were no new ancillary service contracts in South Western NSW in the 12 months prior to, or following, the commissioning of the Limondale No.2 SF. | The connection of Limondale No.2 SF has increased the generation capacity in South Western NSW. When Limondale No.2 SF is generating. A new constraint equation limiting the output of Limondale No.2 SF to manage post contingent voltage oscillations was binding for approximately 94.6 hours in the 12 months following the connection of Limondale No.2 SF. There are many factors that impact the operation of Limondale No.2 SF constraint equation: - the relative operation of the existing generating units in NSW - NEM dispatch price in NSW and VIC - network outages (planned and unplanned) significantly impact the power transfer limits. All of the above have a far greater impact on the utilisation of VNI and the South Western NSW network compared to a connection of any single SF in South Western NSW. The constraints in the NEM dispatch system can also not specifically by attributed to any single generator. Therefore, it cannot be said that the connection of Limondale No.2 SF has specifically had a material impact on network congestion in the main 330, 220 kV and 132 kV system network, however it is a contributing factor. Localised historical transmission line flows were investigated surrounding Limondale No.2 SF in the south western 132kV network, showing congestion may occur due to Limondale No.2 SF. This is managed by runback and transfer trip schemes in operation and lines were well utilised but did not exceed contingency ratings. The system strenght schemes are for outages of lines X3, 63, OX1, X5 and either TX. | No project timings have been affected by the inclusion of the Limondale No.2 SF. | Limondale No.2 SF has minimal influence on the power transfer capability between Victoria and NSW. The Limondale No.2 SF has no direct impact on the southerly or northerly power transfer capability between QLD and NSW .
Note on D2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be discussed with Gang