## Disclaimer
Disclaimer
This modelling assumptions workbook contains data provided by or collected from third parties,
and conclusions, opinions, assumptions or forecasts that are based on that data.
AEMO has made every effort to ensure the quality of the information in this workbook but cannot guarantee
that the information, forecasts and assumptions in it are accurate, complete or appropriate for your
circumstances. This modelling assumptions workbook does not include all of the information that an investor,
participant or potential participant in the electricity or gas market might require, and does not amount to a
recommendation of any investment.
Anyone proposing to use the information in this workbook should independently verify and check its
accuracy, completeness and suitability for purpose, and obtain independent and specific advice from
appropriate experts.
This dataset or the information in it may be subsequently updated or amended. This work does
not constitute legal or business advice, and should not be relied on as a substitute for obtaining detailed
legal advice about the National Electricity Law, the National Electricity Rules, or any other applicable
laws, procedures or policies.
Accordingly, to the maximum extent permitted by law, AEMO and its officers, employees and
consultants involved in the preparation of this document:
• make no representation or warranty, express or implied, as to the currency, accuracy, reliability or
completeness of the information in this workbook; and
• are not liable (whether by reason of negligence or otherwise) for any statements, opinions,
information or other matters contained in or derived from this publication, or any omissions from it,
or in respect of a person’s use of the information in this workbook.

## Assumptions Summary
Modelling Assumptions
This file presents tables of input data for Victoria to New South Wales Interconnector Upgrade RIT-T PADR market modelling studies. It is a compilation of data from a number of sources, listed below.
Version History
Version Number | Date | Description
1 | 2019-08-30 | Relase of market modelling assumptions used in the Victoria to New South Wales Interconnector Upgrade RIT-T (PADR stage)
Worksheet Descriptions
Worksheet | Assumptions Grouping | Description | Source
Scenarios | Scenario and REZ settings | Summary of scenario dimensions and parameters | AEMO
Renewable Energy Zones |  | Renewable Energy Zones | AEMO
Demand, Maximum Demand, Rooftop PV, Electric Vehicles, DSP, Battery Aggregation | Demand Summary | Demand forecasting elements | AEMO - ESOO 2018
Renewable Policy Targets | Renewable Policy Summary | Combined Base LRET parameters Target renewable settings for the Queensland and Victorian Renewable Energy Targets respectively | Clean Energy Regulator, Office of Chief Economist QLD and VIC public policy documents, adjusted to meet ESOO 2018 demand forecasts where appropriate
Interconnector Capability | Interconnector settings | Maximum forward and reverse interconnector flow capability for capacity expansion modelling | 2017 Interconnector capabilities report; adjustments for capacity expansion modelling
Proportioning factors |  | Proportion of interconnector losses applied to regional reference nodes | 2018 Regional Boundaries and Marginal Loss Factors
Maximum capacity | Generator reliability settings | Installed capacity of existing, committed and advanced generators. Existing generators refer to maximal seasonal ratings. | Generator information (2019 January release)
Generation limits |  | Unit commitment constraints for capacity outlook models | GHD, 2018 AEMO costs and technical parameter review, AEMO internal study
Firm capacity |  | Firm capacity of existing, committed and advanced generators and new entrant generator classes | Generator information (2019 January release)
Reserves |  | Minimum reserve levels for reliable regional supply | AEMO internal study
Seasonal ratings |  | Winter and summer ratings for existing, committed, advanced and new entrant generators | Generator information (2019 January release)
Maintenance |  | De-rating applied to generators under maintenance, staged construction or to track age-related degradation | GHD, 2018 AEMO costs and technical parameter review, AEMO internal study
Generator Reliability Settings |  | Defines a generators' forced outage rate, mean time to repair after an outage, and the derating experienced during a partial outage | GHD, 2018 AEMO costs and technical parameter review, AEMO internal study
Maintenance |  | The percentage of time per year that a generator is expected to be out of service for maintenance. | GHD, 2018 AEMO costs and technical parameter review
Build cost | Generator technical and financial settings | Capital Cost projections are given for two scenarios termed "4-degrees" and "2-degrees" which describe the global climate policy goal. | GHD, 2018 AEMO costs and technical parameter review, CSIRO, 2018, GenCost 2018; Updated projections of electricity generation technology costs, Entura, 2018, Pumped hydro cost modelling
Regional Cost Factors |  | Regional cost factors provide an indication of the variation in new entrants generators cost based on the shift in labour, equipment and shipping/delivery cost between regions. Remoteness is also taken into account, leading to three different cost factors (low, medium and high) within each region. | GHD, 2018 AEMO costs and technical parameter review
Generator Regional Build Cost |  | Build cost trajectories calculated for different new generators. These are calculated by applying Regional Cost factors to baseline Melbourne-specific overnight capital costs provided for the 4 degree scenario (including fuel connection costs). | GHD, 2018 AEMO costs and technical parameter review, CSIRO, 2018, GenCost 2018; Updated projections of electricity generation technology costs
Storage Regional Build Cost |  | Storage regional build costs are given for battery storage and pumped hydro plants. For battery storages, build cost trajectories are calculated by applying Regional Cost Factors to baseline Melbourne-specific overnight capital costs provided for the 4 degree scenario (including fuel connection costs). Pumped hydro regional build cost trajectories are based on the Entura report. | GHD, 2018 AEMO costs and technical parameter review, CSIRO, 2018, GenCost 2018; Updated projections of electricity generation technology costs, Entura, 2018, Pumped hydro cost modelling
Connection cost |  | Cost to connect different generation technologies. | AEMO internal study
Build limits |  | Modelled limitations impacting build constraints within the expansion modelling | AEMO internal study
Capacity Factors |  | Capacity factors for renewable generators in the renewable energy zones | DNVGL, AEMO analysis outcomes
Lead times |  | Modelled limitations impacting build timings within the expansion modelling | GHD, 2018 AEMO costs and technical parameter review
Storage properties |  | Battery storage to power ratio, lifetime and round-trip efficiency | GHD, 2018 AEMO costs and technical parameter review
Coal and Biomass price |  | Coal fuel price for each coal generator | Existing generators: 2016 Wood Mackenzie Coal Cost Report New entrants: Resources and Energy Quarterly (June 2018) report, Department of Industry, Innovation and Science (AEMO conversions).
Gas and Liquid fuel price |  | Fuel price for each gas and liquid fuel generator | Core Energy, 2019 wholesale gas price outlook
Refurbishment |  | Cost and timing for refurbishment of ageing generators | Public announcements, AEMO internal study, GHD
Retirement |  | Announced and end-of-technical-life generator retirement | Public announcements, AEMO internal study
Heat rates |  | Efficiency of conversion of fuel to output for thermal generators | GHD, 2018 AEMO costs and technical parameter review
Auxiliary |  | Auxiliary (self) load for each generator or generator class | GHD, 2018 AEMO costs and technical parameter review
Fixed OPEX |  | Fixed operating cost regardless of output for each generator or generator class | GHD, 2018 AEMO costs and technical parameter review
Variable OPEX |  | Variable operating cost per MWh of output for each generator or generator class | GHD, 2018 AEMO costs and technical parameter review
Emissions |  | Emissions production per MWh of output for each generator or generator class | GHD, 2018 AEMO costs and technical parameter review
Marginal Loss Factors |  | Marginal loss factors for each generator | 2018 Regional Boundaries and Marginal Loss Factors
Supporting Materials
For further details on input assumptions and sources visit: | http://aemo.com.au/Electricity/National-Electricity-Market-NEM/Planning-and-forecasting/Inputs-Assumptions-and-Methodologies.
Source | Materials
GHD, 2018 AEMO costs and technical parameter review | AEMO costs and technical parameter review report, available at: https://www.aemo.com.au/-/media/Files/Electricity/NEM/Planning_and_Forecasting/Inputs-Assumptions-Methodologies/2019/9110715-REP-A-Cost-and-Technical-Parameter-Review---Rev-4-Final.pdf AEMO costs and technical parameter review databook, available at: https://www.aemo.com.au/-/media/Files/Electricity/NEM/Planning_and_Forecasting/Inputs-Assumptions-Methodologies/2019/GHD-AEMO-revised---2018-19-Costs_and_Technical_Parameter.xlsb
CSIRO, 2018, GenCost 2018; Updated projections of electricity generation technology costs | https://www.csiro.au/~/media/News-releases/2018/Annual-update-finds-renewables-are-cheapest-new-build-power/GenCost2018.pdf
Wood Mackenzie Coal Cost Report | http://www.aemo.com.au/-/media/Files/Electricity/NEM/Planning_and_Forecasting/NTNDP/2016/Data_Sources/AEMO_Coal-Outputs_20160512_.xlsx
Entura, 2018, Pumped hydro cost modelling | https://projectmarinus.tasnetworks.com.au/assets/Report-Pumped-Hydro-Cost-Modelling.pdf
Core Energy, 2019 wholesale gas price outlook | Wholesale Gas Price Outlook Report, available at: https://www.aemo.com.au/-/media/Files/Electricity/NEM/Planning_and_Forecasting/Inputs-Assumptions-Methodologies/2019/CORE-Delivered-Wholesale-Gas-Price-Outlook_16-January-2019.pdf Wholesale Gas Price Outlook Databook, available at: https://www.aemo.com.au/-/media/Files/Electricity/NEM/Planning_and_Forecasting/Inputs-Assumptions-Methodologies/2019/CORE-Eastern-Australia-Gas-Price-Projections-Databook_16-January-2019.xlsx
Generator information (2019 January release) | http://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Planning-and-forecasting/Generation-information

## Scenarios
Go to Assumptions Summary
Summary of scenario dimensions
Scenario | DER uptake | Large-scale renewable generation uptake | Energy demand
Neutral | Medium | Medium | Medium
Fast change | Low | High | High
Slow change | High | Low | Low
High DER | High | Low | Medium
Summary of scenario parameters
Scenarios
Scenario/sensitivity | Neutral | Slow Change | Fast Change
Demand Settings
Economic growth and population outlook | Neutral | Weaker than Neutral | Stronger than Neutral
Rooftop PV - up to 100 kW | Neutral | Proportionally more household installations than in Neutral | Proportionally fewer household installations than in Neutral
Non-scheduled PV - from 100 kW to 30 MW | Neutral | Proportionally more installations than in Neutral | Proportionally fewer installations than in Neutral
Demand Side Participation (DSP) | Neutral | Less need for DSP | Stronger need for DSP
Electric Vehicle Uptake | Neutral | Weaker than Neutral | Stronger than Neutral
Battery storage installed capacity | Neutral | Proportionally more household installations than in Neutral | Proportionally fewer household installations than in Neutral
Battery storage aggregation by 2050 | Central estimate | Greater adoption of consumer energy management opportunities, leading to greater aggregation | Slower adoption of consumer energy management opportunities, leading to lesser aggregation
Policy Settings (will reflect policies of the day at commencement of modelling)
Emissions trajectory | Coal retirement timings adjusted to give effect to similar trajectories | Coal retirement timings delayed to give effect to a less aggressive trajectory than Neutral | Coal retirement timings accelerated to give effect to a more aggressive trajectory than Neutral
Energy Efficiency Improvement | Neutral | Weak | Strong
Supply Side Settings
Generator cost trajectories | Neutral (CSIRO’s 4-degree scenario) | Neutral (CSIRO’s 4-degree scenario) | Stronger than Neutral (CSIRO’s 2-degree scenario)
Battery cost trajectories (utility and behind the meter) | Neutral | Neutral | Neutral
Gas Market Settings
Gas prices | As forecast by AEMO's independent consultant, consistent to deliver central gas demands | As forecast by AEMO's independent consultant, consistent to deliver lower gas demands | As forecast by AEMO's independent consultant, consistent to deliver stronger gas demands
New gas supplies | As forecast in AEMO's 2019 GSOO | As forecast in AEMO's 2019 GSOO | As forecast in AEMO's 2019 GSOO

## Renewable Energy Zones
Go to Assumptions Summary
Renewable Energy Zones |  |  |  |  | Renewable Energy Zone Map | NEM Regional Cost Zone Map
List of Renewable Energy Zones (REZs) by NEM region and zone
Build cost at each REZ that reflects the NEM regional cost zone map
# | Name | NEM Region | NEM Zone | Regional Cost Zones
1 | Far North Queensland | QLD | NQ | Low
2 | North Queensland Clean Energy Hub | QLD | NQ | Medium
3 | Northern Queensland | QLD | NQ | Low
4 | Isaac | QLD | NQ | Low
5 | Barcaldine | QLD | CQ | Medium
6 | Fitzroy | QLD | CQ | Low
7 | Darling Downs | QLD | SWQ | Low1
8 | North West New South Wales | NSW | NNS | Medium
9 | New England | NSW | NNS | Low
10 | Central West New South Wales | NSW | NCEN | Medium
11 | Southern New South Wales Tablelands | NSW | CAN | Low
12 | Cooma-Monaro | NSW | CAN | Medium
13 | Tumut | NSW | CAN | Medium
14 | South West New South Wales | NSW | SWNSW | High
15 | Broken Hill | NSW | SWNSW | High
16 | Murray River (NSW) | NSW | SWNSW | High
| Murray River (VIC) | VIC | NVIC | High
17 | Western Victoria | VIC | CVIC | Medium2
18 | Moyne | VIC | MEL | Medium2
19 | Ovens Murray | VIC | NVIC | Medium2
20 | Gippsland | VIC | LV | Medium
21 | South East South Australia | SA | SESA | Medium2
22 | Riverland (SA) | SA | NSA | Medium
| Riverland (NSW) | NSW | SWNSW | High
23 | Mid-North South Australia | SA | NSA | Low1
24 | Yorke Peninsula | SA | NSA | Low
25 | Northern South Australia | SA | NSA | Medium
26 | Leigh Creek | SA | NSA | Medium1
27 | Roxby Downs | SA | NSA | Medium1
28 | Eastern Eyre Peninsula | SA | NSA | Medium
29 | Western Eyre Peninsula | SA | NSA | Medium
30 | North West Tasmania | TAS | TAS | Medium2
31 | Tasmania Midlands | TAS | TAS | Medium2
32 | North East Tasmania | TAS | TAS | Medium1
Note:
1 When a REZ zone covers two regional cost zones, the lower cost zone is utilised
2 When a REZ zone covers all three regional cost zones, the medium cost zone is utilised
3 The same cost zone is applied to both sides of a REZ that straddles NEM regions.

## Demand Summary
Go to Assumptions Summary
Demand Summary
NEM Gross State Product growth
| Economic Growth | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
Neutral BAU | Neutral | 100% | 102.8% | 105.7% | 108.8% | 111.6% | 114.3% | 117.3% | 120.4% | 123.6% | 126.9% | 130.2% | 133.4% | 136.7% | 140% | 143.3% | 146.8% | 150.3% | 153.8% | 157.4% | 161.1%
Fast Change | Strong | 100% | 103.2% | 106.6% | 110.2% | 113.7% | 117.1% | 121% | 125.1% | 129.4% | 134% | 138.7% | 143.5% | 148.4% | 153.4% | 158.6% | 164% | 169.5% | 175.3% | 181.2% | 187.2%
Slow Change | Weak | 100% | 102.3% | 104.7% | 106.9% | 108.9% | 110.7% | 112.7% | 114.6% | 116.6% | 118.4% | 120.2% | 121.9% | 123.5% | 125.1% | 126.7% | 128.3% | 129.9% | 131.5% | 133.1% | 134.8%
PV Generation Relative to Underlying Demand
| PV versus Demand | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
Neutral BAU | Neutral PV versus Neutral Demand | 6.053% | 7.147% | 7.709% | 7.988% | 8.339% | 8.661% | 8.887% | 9.317% | 9.803% | 10.23% | 10.62% | 11.04% | 11.39% | 11.85% | 12.28% | 12.79% | 13.46% | 13.97% | 14.17% | 14.41%
Fast Change | Neutral PV versus Strong Demand | 6.03% | 7.107% | 7.661% | 7.936% | 8.209% | 8.533% | 8.693% | 9.035% | 9.319% | 9.653% | 9.938% | 10.26% | 10.53% | 10.91% | 11.25% | 11.67% | 12.21% | 12.61% | 12.71% | 12.85%
Slow Change | Neutral PV versus Weak Demand | 6.069% | 7.224% | 7.809% | 8.219% | 8.681% | 9.211% | 9.511% | 10.09% | 10.66% | 11.21% | 12.4% | 13.29% | 14.25% | 15.14% | 15.82% | 16.52% | 17.39% | 18.09% | 18.36% | 18.69%
Total NEM Summer DSP relative to NEM Operational Max Demand with coincident regional peaks
| DSP versus Demand | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
Neutral BAU | Neutral DSP versus Neutral Demand | 1.134% | 1.272% | 1.391% | 1.526% | 1.644% | 1.75% | 1.867% | 1.995% | 2.133% | 2.278% | 2.385% | 2.481% | 2.583% | 2.652% | 2.757% | 2.865% | 2.947% | 3.056% | 3.19% | 3.247%
Fast Change | Strong DSP versus Strong Demand | 1.13% | 1.352% | 1.543% | 1.762% | 1.954% | 2.149% | 2.343% | 2.536% | 2.699% | 2.911% | 3.065% | 3.176% | 3.348% | 3.474% | 3.607% | 3.778% | 3.869% | 4.065% | 4.221% | 4.346%
Slow Change | Weak DSP versus Weak Demand | 1.141% | 1.147% | 1.134% | 1.162% | 1.158% | 1.162% | 1.166% | 1.169% | 1.182% | 1.202% | 1.251% | 1.266% | 1.288% | 1.285% | 1.274% | 1.282% | 1.268% | 1.271% | 1.272% | 1.24%
Battery Storage Capacity Relative to Operational Max Demand
| Battery uptake versus MD | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
Neutral BAU | Neutral uptake versus Neutral MD | 0.5983% | 1.021% | 1.34% | 1.4% | 1.538% | 1.763% | 2.014% | 2.161% | 2.253% | 2.429% | 2.616% | 2.863% | 3.064% | 3.351% | 3.732% | 4.155% | 4.617% | 4.986% | 5.391% | 5.826%
Fast Change | Neutral uptake versus Strong MD | 0.596% | 1.016% | 1.325% | 1.394% | 1.518% | 1.739% | 1.981% | 2.102% | 2.16% | 2.313% | 2.48% | 2.679% | 2.861% | 3.138% | 3.461% | 3.843% | 4.236% | 4.573% | 4.896% | 5.277%
Slow Change | Neutral uptake versus Weak MD | 0.6017% | 1.027% | 1.347% | 1.435% | 1.584% | 1.844% | 2.123% | 2.293% | 2.402% | 2.605% | 2.936% | 3.296% | 3.631% | 4.055% | 4.514% | 5.058% | 5.624% | 6.105% | 6.605% | 7.129%

## Demand
Go to Assumptions Summary
Energy Consumption (GWh)
Amount of energy consumed by customers in each region in each financial year.
Operational demand
Energy consumption which is net of rooftop PV generation
Neutral
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 66704.9018 | 66440.9869 | 66505.4363 | 66661.6944 | 66266.9216 | 66557.0613 | 67237.6917 | 68009.9132 | 68803.1991 | 69645.4056 | 70594.4119 | 71737.6423 | 72946.9696 | 73951.6023 | 74826.2587 | 75824.334 | 76636.5525 | 77534.2204 | 78685.7487 | 79796.4064
QLD | 49422.1699 | 49362.6007 | 49334.2701 | 49622.2964 | 49911.597 | 50201.764 | 50407.4488 | 50388.0707 | 50303.7437 | 50415.3146 | 50542.0158 | 50737.8773 | 50934.5843 | 51030.3799 | 51072.1158 | 51084.5541 | 51039.2758 | 51155.8788 | 51339.8844 | 51514.4414
SA | 12053.4467 | 11833.519 | 11825.7928 | 12209.9976 | 12167.2823 | 12184.3949 | 12247.7031 | 12032.192 | 11839.3576 | 11856.1742 | 11860.1843 | 11895.0327 | 11990.4503 | 12001.3795 | 12055.308 | 11959.9907 | 11966.6541 | 11992.5212 | 12078.3147 | 12167.4041
TAS | 10387.7737 | 10412.2168 | 10474.4711 | 10546.3409 | 10429.1041 | 10460.2223 | 10509.8787 | 10416.959 | 10343.2021 | 10387.6801 | 10400.6502 | 10367.9561 | 10383.4971 | 10439.0727 | 10497.7587 | 10549.7676 | 10594.0095 | 10643.2129 | 10711.8593 | 10783.8298
VIC | 43302.8147 | 43183.6279 | 43467.5205 | 43994.8849 | 44145.4446 | 44551.8535 | 45293.79 | 45263.7143 | 45297.8985 | 46051.2112 | 46737.6044 | 47474.0341 | 48299.2277 | 49150.3418 | 50038.4877 | 50845.8687 | 51515.4521 | 52265.499 | 53138.6624 | 53957.5681
Fast
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 66633.9601 | 66412.7981 | 66371.3469 | 66352.4373 | 66872.696 | 67222.1285 | 68330.1072 | 69603.5599 | 70990.4121 | 72557.4778 | 74126.5649 | 75841.743 | 77601.9611 | 78953.1634 | 80635.4514 | 82246.5078 | 83686.4738 | 85279.2666 | 87159.2172 | 89008.0574
QLD | 49840.56 | 49904.2286 | 49950.5959 | 50190.2752 | 50456.7341 | 50615.4235 | 51381.9744 | 51665.6311 | 53582.5475 | 54012.5886 | 54458.7809 | 54909.9225 | 55236.1338 | 55615.3556 | 55532.1608 | 55776.7516 | 55995.6544 | 56426.6464 | 56975.4296 | 57533.1063
SA | 12091.2879 | 11894.5414 | 11913.3793 | 12371.5335 | 12451.1601 | 12432.8109 | 12588.3325 | 12633.7665 | 12782.3255 | 12944.6794 | 13141.8004 | 13319.1323 | 13508.2581 | 13649.7395 | 13824.8777 | 13863.1722 | 13995.4591 | 14139.9902 | 14369.3993 | 14606.145
TAS | 10401.7698 | 10448.6712 | 10538.367 | 10647.977 | 10717.3356 | 10756.1824 | 10836.2436 | 10825.4791 | 10943.4322 | 11066.5678 | 11170.8625 | 11222.2751 | 11335.089 | 11468.1797 | 11606.2371 | 11742.6739 | 11862.091 | 12003.2163 | 12168.1931 | 12339.3836
VIC | 43648.0135 | 43665.7919 | 44090.705 | 44773.4425 | 45569.6378 | 45946.4655 | 47092.1947 | 47793.7127 | 49024.5667 | 50410.9925 | 51874.8868 | 53353.6477 | 54801.815 | 56079.6596 | 57480.7028 | 58823.8689 | 60036.5781 | 61387.8178 | 62881.6252 | 64341.2525
Slow
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 66505.6218 | 65877.4909 | 66090.9395 | 66080.8889 | 66270.0822 | 65080.4352 | 65457.6963 | 65860.6201 | 66212.43 | 66509.6986 | 63882.8106 | 60895.5722 | 57912.6428 | 56792.1283 | 56708.9366 | 57158.9198 | 57542.1805 | 57978.9929 | 58655.3902 | 59294.5302
QLD | 49242.9003 | 48546.4745 | 48011.8049 | 47811.6703 | 47840.3206 | 47287.0278 | 46819.8426 | 45907.7016 | 45401.5192 | 44886.8946 | 36794.5526 | 36319.1116 | 35325.2341 | 35285.72 | 34890.4458 | 34817.9824 | 34762.343 | 34722.9007 | 34839.8898 | 34920.8729
SA | 11780.7765 | 11509.2751 | 11481.3055 | 11845.9799 | 11665.0669 | 11366.7755 | 11369.293 | 11089.231 | 10895.1514 | 10819.7984 | 10761.247 | 10576.3978 | 10286.713 | 9850.9267 | 9770.1813 | 9579.6048 | 9521.2449 | 9459.7809 | 9474.0669 | 9491.6027
TAS | 10374.3775 | 9966.7339 | 9995.0923 | 10025.735 | 9910.8215 | 9736.3794 | 9728.7917 | 8950.4365 | 8940.5184 | 8925.3943 | 8907.1509 | 8741.0106 | 8456.9 | 8159.9413 | 8059.1647 | 8044.8643 | 7904.5256 | 7879.5623 | 7885.4699 | 7893.1555
VIC | 43443.7549 | 43250.1816 | 43513.448 | 41686.217 | 39369.7088 | 38461.809 | 38949.6598 | 38549.9776 | 38506.472 | 38876.9486 | 39229.2772 | 39135.2243 | 38456.5652 | 37922.016 | 38404.5345 | 38875.2973 | 39298.3218 | 39716.5191 | 40326.7832 | 40883.6211
Underlying demand
Energy consumption that is equivalent to the 'power point' - gross of rooftop PV generation and other small non-scheduled systems
Neutral
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 70160.9908 | 70787.2381 | 71318.3461 | 71714.0508 | 71555.6502 | 72101.7909 | 72996.3163 | 74088.1771 | 75234.279 | 76428.2292 | 77685.3601 | 79169.9457 | 80661.4324 | 81991.9219 | 83168.1358 | 84552.2193 | 85914.8379 | 87273.5975 | 88627.9027 | 89976.3445
QLD | 53380.8289 | 53787.2657 | 54175.5668 | 54782.3028 | 55379.8724 | 55990.1937 | 56474.0204 | 56836.0214 | 57193.8289 | 57762.0238 | 58321.0709 | 58993.4793 | 59687.9971 | 60356.5032 | 60960.8808 | 61602.8842 | 62283.4393 | 63053.6197 | 63672.2084 | 64326.0027
SA | 13717.9942 | 13717.6141 | 13795.4853 | 14262.3309 | 14296.8765 | 14396.3925 | 14524.9733 | 14416.9467 | 14350.0418 | 14501.1209 | 14624.0288 | 14790.5637 | 14984.1674 | 15137.5045 | 15323.4995 | 15378.4872 | 15554.8037 | 15721.445 | 15880.9897 | 16058.1997
TAS | 10602.5794 | 10673.5994 | 10751.8084 | 10828.6053 | 10739.7418 | 10799.3495 | 10873.9844 | 10809.0118 | 10765.7457 | 10846.4012 | 10895.9931 | 10903.8218 | 10931.2612 | 11004.9966 | 11079.6093 | 11150.7737 | 11220.6953 | 11288.5475 | 11360.3664 | 11438.6124
VIC | 45726.4531 | 46216.2913 | 46736.8235 | 47338.9013 | 47588.9837 | 48110.9506 | 48938.8215 | 49082.8399 | 49322.3883 | 50291.848 | 51205.1532 | 52203.4585 | 53296.0737 | 54496.7336 | 55736.6632 | 56959.9567 | 58157.2065 | 59327.0723 | 60411.8921 | 61478.2936
Fast
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 70090.0491 | 70759.0493 | 71184.2568 | 71404.7938 | 72161.4246 | 72766.858 | 74088.7318 | 75681.8238 | 77421.492 | 79340.3014 | 81217.5131 | 83274.0464 | 85316.4239 | 86993.483 | 88977.3285 | 90974.3931 | 92964.7592 | 95018.6438 | 97101.3713 | 99187.9956
QLD | 53799.219 | 54328.8937 | 54791.8927 | 55350.2815 | 55925.0095 | 56403.8532 | 57448.546 | 58113.5819 | 60472.6326 | 61359.2978 | 62237.836 | 63165.5246 | 63989.5467 | 64941.4789 | 65420.9258 | 66295.0817 | 67239.8179 | 68324.3873 | 69307.7536 | 70344.6676
SA | 13755.8355 | 13778.6366 | 13883.0718 | 14423.8668 | 14580.7542 | 14644.8084 | 14865.6027 | 15018.5211 | 15293.0096 | 15589.6261 | 15905.645 | 16214.6633 | 16501.9752 | 16785.8646 | 17093.0693 | 17281.6687 | 17583.6086 | 17868.914 | 18172.0744 | 18496.9406
TAS | 10616.5755 | 10710.0539 | 10815.7043 | 10930.2414 | 11027.9733 | 11095.3096 | 11200.3493 | 11217.5319 | 11365.9758 | 11525.2889 | 11666.2055 | 11758.1407 | 11882.853 | 12034.1037 | 12188.0877 | 12343.68 | 12488.7768 | 12648.5509 | 12816.7002 | 12994.1662
VIC | 46071.6519 | 46698.4553 | 47360.008 | 48117.4589 | 49013.1769 | 49505.5625 | 50737.2263 | 51612.8383 | 53049.0564 | 54651.6293 | 56342.4355 | 58083.0721 | 59798.6611 | 61426.0514 | 63178.8783 | 64937.9568 | 66678.3325 | 68449.3911 | 70154.8549 | 71861.978
Slow
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 69961.7108 | 70223.742 | 70903.8493 | 71133.2454 | 71558.8109 | 70625.1648 | 71216.3209 | 71938.884 | 72643.5098 | 73292.5222 | 70973.7588 | 68327.8755 | 65627.1056 | 64832.4479 | 65050.8137 | 65886.8051 | 66820.4659 | 67718.37 | 68597.5443 | 69474.4684
QLD | 53201.5593 | 52971.1395 | 52853.1016 | 52971.6767 | 53308.596 | 53075.4575 | 52886.4142 | 52355.6523 | 52291.6043 | 52233.6038 | 44573.6077 | 44574.7136 | 44078.6469 | 44611.8433 | 44779.2107 | 45336.3125 | 46006.5065 | 46620.6415 | 47172.2138 | 47732.4342
SA | 13445.3241 | 13393.3703 | 13450.998 | 13898.3132 | 13794.6611 | 13578.773 | 13646.5632 | 13473.9856 | 13405.8356 | 13464.7451 | 13525.0915 | 13471.9288 | 13280.4301 | 12987.0518 | 13038.3729 | 12998.1013 | 13109.3944 | 13188.7047 | 13276.7419 | 13382.3983
TAS | 10589.1832 | 10228.1166 | 10272.4296 | 10307.9994 | 10221.4591 | 10075.5066 | 10092.8974 | 9342.4893 | 9363.0619 | 9384.1154 | 9402.4938 | 9276.8763 | 9004.6641 | 8725.8652 | 8641.0153 | 8645.8704 | 8531.2113 | 8524.8969 | 8533.9769 | 8547.938
VIC | 45867.3934 | 46282.845 | 46782.751 | 45030.2334 | 42813.2479 | 42020.906 | 42594.6914 | 42369.1033 | 42530.9618 | 43117.5854 | 43696.826 | 43864.6487 | 43453.4113 | 43268.4078 | 44102.71 | 44989.3852 | 45940.0763 | 46778.0924 | 47600.0129 | 48404.3466

## Maximum Demand
Go to Assumptions Summary
Maximum Demand (Power, MW)
Amount of power that must be generated at times of peak operational demand. Peak operational demand occurs in Summer months in all NEM regions except Tasmania.
10% Probability of exceedance
Neutral
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 14024.1258 | 13975.338 | 13993.7289 | 14202.2972 | 14260.3673 | 14454.0099 | 14579.3478 | 14644.0115 | 14937.5329 | 15062.2956 | 15356.5502 | 15500.4016 | 15693.2674 | 15971.8555 | 16146.9696 | 16290.8441 | 16536.3488 | 16656.3607 | 16803.8425 | 16965.344
QLD | 9066.948 | 9076.2347 | 9005.639 | 9080.2644 | 9090.8949 | 9102.6825 | 9245.73 | 9161.0037 | 9249.0306 | 9286.7936 | 9323.3846 | 9437.7875 | 9572.1326 | 9691.5733 | 9767.4284 | 9873.9117 | 9961.7086 | 10108.8736 | 10182.5584 | 10257.9892
SA | 3175.6954 | 3170.3834 | 3184.8893 | 3258.8581 | 3227.9445 | 3264.9406 | 3291.6766 | 3289.1249 | 3272.0949 | 3309.0676 | 3326.2555 | 3352.415 | 3406.1651 | 3469.8302 | 3490.1925 | 3481.7706 | 3492.4127 | 3523.5836 | 3592.8682 | 3638.689
TAS | 1717.7084 | 1722.7531 | 1733.9548 | 1746.6778 | 1728.9804 | 1737.2007 | 1749.4716 | 1736.991 | 1729.627 | 1741.9251 | 1745.5961 | 1749.6578 | 1752.4698 | 1767.0506 | 1775.9469 | 1783.824 | 1794.4836 | 1808.298 | 1816.3305 | 1859.458
VIC | 9764.4807 | 9721.0821 | 9791.2823 | 9965.383 | 9958.7292 | 10083.7384 | 10277.7344 | 10318.044 | 10276.8849 | 10455.1753 | 10566.5571 | 10764.1503 | 10961.6754 | 11234.4049 | 11293.2727 | 11554.4606 | 11752.2579 | 12002.1647 | 12105.6248 | 12125.5675
Fast
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 14086.3394 | 13979.703 | 14078.2184 | 14172.4835 | 14365.2726 | 14551.4263 | 14676.011 | 14952.4862 | 15216.9942 | 15603.821 | 15864.8781 | 16278.2844 | 16498.7302 | 16719.7112 | 17065.81 | 17295.092 | 17633.8109 | 17885.1673 | 18183.2355 | 18300.624
QLD | 9084.9521 | 9116.849 | 9161.4971 | 9131.8855 | 9188.8375 | 9245.5323 | 9364.7188 | 9398.8348 | 9676.4588 | 9764.8245 | 9897.9845 | 10089.9163 | 10217.8244 | 10359.9079 | 10476.4815 | 10581.7305 | 10794.7776 | 10923.68 | 11109.5976 | 11230.5798
SA | 3172.9478 | 3200.34 | 3216.2082 | 3273.1758 | 3295.5214 | 3303.064 | 3361.6363 | 3350.7008 | 3460.0487 | 3508.5655 | 3512.5504 | 3597.3504 | 3713.8259 | 3740.6703 | 3778.0243 | 3799.9563 | 3821.8656 | 3881.9142 | 3961.1652 | 4040.2196
TAS | 1715.6867 | 1732.1142 | 1746.3646 | 1758.3603 | 1772.3682 | 1785.6354 | 1798.642 | 1800.3073 | 1819.3211 | 1843.6889 | 1865.8407 | 1879.8303 | 1897.8548 | 1922.0599 | 1939.6622 | 1964.6789 | 1986.6033 | 2010.5137 | 2032.9351 | 2093.4131
VIC | 9834.0384 | 9830.0324 | 9937.9242 | 10092.3203 | 10169.2219 | 10302.3285 | 10600.8623 | 10753.0418 | 10990.4611 | 11137.1118 | 11391.9718 | 11764.1714 | 11989.433 | 12252.6814 | 12536.9319 | 12830.0798 | 13213.608 | 13373.2725 | 13711.9146 | 13850.8698
Slow
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 13921.406 | 13976.159 | 14048.4198 | 14123.6331 | 14200.5157 | 14206.3991 | 14227.5441 | 14212.1835 | 14468.7755 | 14589.8438 | 14394.4371 | 13811.593 | 13466.1897 | 13342.2188 | 13533.6498 | 13671.0106 | 13792.3426 | 13777.266 | 13888.7002 | 14028.2597
QLD | 9035.5826 | 8944.2778 | 8887.6447 | 8855.0074 | 8873.5398 | 8765.2902 | 8751.802 | 8655.5723 | 8631.9222 | 8601.9953 | 7441.2722 | 7412.5173 | 7387.2745 | 7439.5178 | 7441.4203 | 7518.0063 | 7556.0696 | 7681.906 | 7778.3508 | 7839.781
SA | 3131.5633 | 3118.1812 | 3159.6338 | 3181.9498 | 3182.6509 | 3132.5834 | 3179.3083 | 3127.6596 | 3116.5345 | 3121.3328 | 3117.4428 | 3152.5761 | 3127.6482 | 3115.4405 | 3113.5379 | 3065.6647 | 3105.2702 | 3136.4895 | 3164.0348 | 3209.0982
TAS | 1707.956 | 1660.1268 | 1663.0693 | 1667.6678 | 1651.0622 | 1627.9617 | 1629.4115 | 1515.6034 | 1519.5798 | 1523.5636 | 1523.242 | 1505.3803 | 1467.543 | 1423.9432 | 1406.4413 | 1410.2233 | 1393.3629 | 1391.8188 | 1392.3412 | 1430.6638
VIC | 9740.872 | 9733.5592 | 9766.3238 | 9485.1296 | 9254.6886 | 9207.6458 | 9355.1116 | 9389.848 | 9286.3701 | 9330.1455 | 9444.0369 | 9560.0307 | 9473.3603 | 9495.6418 | 9625.1309 | 9646.7324 | 9896.9977 | 10024.4801 | 10099.5991 | 10145.1584
50% Probability of exceedance
Neutral
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 12366.4358 | 12322.4126 | 12346.2209 | 12400.3173 | 12442.3526 | 12545.913 | 12733.1937 | 12770.1529 | 12986.9279 | 13172.0349 | 13297.9351 | 13502.0129 | 13692.1622 | 13986.8005 | 14083.4345 | 14265.1088 | 14423.1408 | 14587.8468 | 14739.0852 | 14869.5284
QLD | 8532.8778 | 8531.4022 | 8513.2798 | 8554.4689 | 8625.7512 | 8663.4781 | 8710.4964 | 8741.8973 | 8788.0454 | 8857.1307 | 8942.7474 | 9037.0174 | 9145.0046 | 9257.2005 | 9346.8175 | 9453.818 | 9561.0356 | 9661.7766 | 9762.2709 | 9835.1277
SA | 2900.74 | 2892.534 | 2895.3653 | 2953.9446 | 2950.8046 | 2977.5766 | 2997.1977 | 2985.1635 | 2968.0251 | 3004.0147 | 3044.0749 | 3045.8284 | 3096.4437 | 3116.67 | 3155.2167 | 3173.6954 | 3200.2613 | 3249.5966 | 3248.5958 | 3304.9471
TAS | 1675.1962 | 1687.4399 | 1696.7234 | 1706.5127 | 1692.0138 | 1700.3165 | 1709.853 | 1698.8051 | 1691.1137 | 1703.4758 | 1709.8985 | 1712.394 | 1716.6848 | 1728.9529 | 1736.3734 | 1747.3827 | 1756.7826 | 1767.5792 | 1779.8697 | 1825.164
VIC | 8983.41 | 8996.9877 | 9008.5601 | 9221.2005 | 9248.5261 | 9330.2273 | 9518.551 | 9480.4955 | 9499.3301 | 9679.2054 | 9855.7587 | 10009.2161 | 10163.6805 | 10412.7258 | 10522.3645 | 10769.9835 | 10976.6353 | 11143.7133 | 11289.9549 | 11370.8
Fast
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 12431.8122 | 12319.6161 | 12398.8227 | 12451.4755 | 12529.1549 | 12631.3633 | 12875.9659 | 13170.6784 | 13444.4055 | 13656.9914 | 13819.6111 | 14213.5426 | 14452.6397 | 14723.5281 | 15052.8347 | 15212.3026 | 15505.6661 | 15747.0562 | 16012.2718 | 16232.0876
QLD | 8589.9453 | 8622.0433 | 8623.3797 | 8661.8914 | 8717.6065 | 8756.6485 | 8885.8776 | 8939.3872 | 9222.5795 | 9340.1032 | 9501.4733 | 9668.0037 | 9792.9276 | 9962.8137 | 10045.0833 | 10190.7899 | 10345.5944 | 10484.522 | 10661.8772 | 10773.4862
SA | 2913.6466 | 2891.4265 | 2924.3371 | 2970.3346 | 3012.3946 | 3028.1565 | 3080.4521 | 3083.9834 | 3142.769 | 3174.2498 | 3255.8622 | 3303.277 | 3357.531 | 3406.5798 | 3455.3253 | 3495.1234 | 3542.3917 | 3581.3684 | 3641.4881 | 3700.1331
TAS | 1677.2908 | 1694.9344 | 1708.8001 | 1724.1524 | 1733.7559 | 1744.5201 | 1760.7051 | 1762.3564 | 1781.9617 | 1804.9952 | 1824.5293 | 1840.4174 | 1860.0163 | 1879.3282 | 1901.5798 | 1924.5632 | 1947.2853 | 1970.6839 | 1993.7426 | 2054.3748
VIC | 9090.3249 | 9107.0799 | 9198.28 | 9277.7344 | 9482.5057 | 9608.8991 | 9849.3404 | 9971.059 | 10177.9616 | 10418.6132 | 10675.7142 | 11016.066 | 11274.1277 | 11450.1949 | 11769.3718 | 12093.6827 | 12387.5591 | 12587.1648 | 12868.2893 | 13031.5238
Slow
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 12345.0466 | 12258.9462 | 12304.6446 | 12418.0659 | 12489.1387 | 12298.6886 | 12364.3224 | 12474.8309 | 12567.9968 | 12694.3251 | 12291.8319 | 11960.7895 | 11540.4026 | 11466.7883 | 11511.7789 | 11592.8187 | 11656.3361 | 11705.9245 | 11884.1913 | 12061.2263
QLD | 8509.6143 | 8443.7944 | 8372.9144 | 8332.9968 | 8402.7582 | 8341.6205 | 8321.2767 | 8213.2773 | 8200.7301 | 8188.6642 | 7050.0231 | 7044.9756 | 6966.0152 | 7001.9329 | 7031.0458 | 7104.6288 | 7175.1968 | 7265.1845 | 7349.3507 | 7407.5657
SA | 2848.1578 | 2846.4235 | 2837.0357 | 2882.8729 | 2879.0854 | 2856.7659 | 2881.8015 | 2834.4278 | 2813.47 | 2839.0141 | 2849.5104 | 2841.3427 | 2832.874 | 2787.828 | 2799.5076 | 2804.134 | 2830.2817 | 2833.3644 | 2873.738 | 2905.3378
TAS | 1671.0938 | 1619.9264 | 1624.6903 | 1628.75 | 1612.8177 | 1591.3981 | 1593.9502 | 1480.434 | 1480.9149 | 1484.8112 | 1486.5704 | 1469.0139 | 1429.6134 | 1388.173 | 1372.846 | 1372.1017 | 1355.4776 | 1355.0181 | 1355.6126 | 1392.8513
VIC | 9046.9202 | 9027.2458 | 9033.7706 | 8789.9569 | 8583.3618 | 8506.0192 | 8588.5725 | 8522.1823 | 8557.2976 | 8600.0367 | 8737.4675 | 8757.0693 | 8663.7095 | 8694.4392 | 8808.673 | 8924.3757 | 9121.794 | 9228.9679 | 9314.5036 | 9382.2911
90% Probability of exceedance
Neutral
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 11261.527 | 11192.7082 | 11302.4808 | 11261.1134 | 11350.405 | 11397.3295 | 11522.9138 | 11636.2128 | 11842.8423 | 11968.2077 | 12132.2274 | 12329.9165 | 12641.4601 | 12817.9684 | 12872.5668 | 12998.6414 | 13244.2308 | 13359.876 | 13521.5422 | 13697.6443
QLD | 8251.7426 | 8255.0603 | 8262.6543 | 8291.5429 | 8360.8376 | 8406.3734 | 8448.1549 | 8495.6654 | 8548.7826 | 8607.2705 | 8708.1775 | 8819.6532 | 8917.4242 | 9010.3924 | 9099.7337 | 9212.1756 | 9318.8577 | 9428.6959 | 9493.4754 | 9558.3656
SA | 2613.7805 | 2658.8046 | 2641.4738 | 2703.3934 | 2705.7087 | 2729.656 | 2745.3523 | 2729.7863 | 2698.8789 | 2738.9205 | 2749.338 | 2796.6172 | 2841.3191 | 2851.5802 | 2905.0944 | 2888.9223 | 2931.18 | 2960.0606 | 2981.9579 | 3035.7905
TAS | 1642.7067 | 1655.5983 | 1665.3101 | 1675.1144 | 1657.6293 | 1668.3909 | 1678.6951 | 1667.7204 | 1658.2832 | 1671.3998 | 1678.466 | 1677.8848 | 1683.3748 | 1694.1975 | 1703.4174 | 1715.891 | 1724.9335 | 1735.8542 | 1749.218 | 1794.7469
VIC | 8366.4821 | 8373.3205 | 8411.1154 | 8543.2621 | 8567.6416 | 8685.5683 | 8804.127 | 8857.1885 | 8876.3506 | 9032.4168 | 9184.4188 | 9323.3795 | 9498.8597 | 9749.1509 | 9835.1188 | 10076.148 | 10277.0631 | 10407.5013 | 10612.2877 | 10651.4136
Fast
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 11309.9313 | 11251.3131 | 11169.8212 | 11231.6063 | 11361.1543 | 11425.1401 | 11710.3993 | 11939.9748 | 12196.3002 | 12459.426 | 12606.3146 | 12976.8308 | 13236.9976 | 13553.8572 | 13767.6006 | 14022.9514 | 14285.377 | 14624.6021 | 14856.5918 | 15038.6276
QLD | 8318.3964 | 8335.1404 | 8352.7497 | 8382.092 | 8466.5533 | 8503.9915 | 8610.1131 | 8675.4626 | 8981.4874 | 9095.2689 | 9262.8708 | 9416.5998 | 9558.85 | 9702.4327 | 9801.6917 | 9933.2935 | 10078.2787 | 10244.3882 | 10381.1201 | 10491.5552
SA | 2649.4054 | 2633.4258 | 2663.7946 | 2731.871 | 2745.5707 | 2767.6012 | 2816.4204 | 2831.5985 | 2869.1808 | 2933.4117 | 3002.5822 | 3059.185 | 3095.6686 | 3137.3468 | 3180.4647 | 3233.7081 | 3253.7019 | 3316.6427 | 3366.975 | 3416.4668
TAS | 1644.2126 | 1660.7655 | 1676.003 | 1689.1345 | 1702.8613 | 1712.2741 | 1727.6992 | 1727.3417 | 1750.575 | 1771.2356 | 1791.608 | 1805.3467 | 1826.4484 | 1846.4507 | 1869.8592 | 1888.16 | 1911.0275 | 1933.5358 | 1963.1538 | 2019.8914
VIC | 8411.6838 | 8477.6491 | 8544.7003 | 8677.9498 | 8799.6353 | 8916.717 | 9128.9126 | 9294.3364 | 9494.1934 | 9700.7823 | 10036.9451 | 10323.7354 | 10569.7691 | 10808.4887 | 11090.9041 | 11336.7862 | 11609.8972 | 11880.2483 | 12122.3365 | 12275.0605
Slow
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 11173.2208 | 11170.662 | 11169.8491 | 11289.1115 | 11265.7063 | 11139.485 | 11212.7073 | 11340.367 | 11432.8247 | 11530.116 | 11083.8365 | 10843.1428 | 10357.3646 | 10263.6694 | 10235.9772 | 10409.6917 | 10517.0206 | 10586.7982 | 10779.1614 | 10894.6173
QLD | 8234.9137 | 8160.8438 | 8102.5188 | 8095.056 | 8131.8266 | 8075.6461 | 8050.6866 | 7967.4367 | 7946.1546 | 7955.0662 | 6830.1993 | 6808.8033 | 6737.4962 | 6788.5137 | 6780.2096 | 6856.9806 | 6936.7386 | 7014.7496 | 7092.0693 | 7151.8269
SA | 2586.9449 | 2592.3791 | 2593.4851 | 2629.2571 | 2636.342 | 2613.8047 | 2634.3155 | 2583.8935 | 2572.2793 | 2587.1875 | 2594.2854 | 2594.4695 | 2581.6223 | 2528.3668 | 2530.1549 | 2538.3833 | 2591.0332 | 2572.9804 | 2612.7863 | 2645.5257
TAS | 1641.5161 | 1586.8214 | 1591.3743 | 1597.3464 | 1581.189 | 1561.0471 | 1560.5105 | 1450.9171 | 1451.4325 | 1452.7823 | 1455.3988 | 1437.5887 | 1399.0609 | 1355.7901 | 1341.0709 | 1341.3425 | 1324.4913 | 1322.3437 | 1325.4838 | 1359.8569
VIC | 8422.8921 | 8391.7929 | 8410.8345 | 8191.1761 | 7947.6819 | 7859.4365 | 7857.1926 | 7842.891 | 7896.8308 | 7926.4087 | 8092.1281 | 8079.9462 | 8026.2633 | 8045.9938 | 8135.7342 | 8221.7696 | 8420.6284 | 8537.5499 | 8610.6801 | 8735.1432

## Rooftop PV
Go to Assumptions Summary
Rooftop PV (Energy, GWh)
Amount of energy generated by behind-the-meter rooftop PV and small-scale non-scheduled generating systems
Neutral Rooftop PV uptake
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 3456.089 | 4346.2511 | 4812.9098 | 5052.3565 | 5288.7287 | 5544.7296 | 5758.6246 | 6078.2639 | 6431.0799 | 6782.8236 | 7090.9482 | 7432.3034 | 7714.4628 | 8040.3196 | 8341.8771 | 8727.8853 | 9278.2854 | 9739.3772 | 9942.1541 | 10179.9382
QLD | 3958.659 | 4424.6651 | 4841.2968 | 5160.0063 | 5468.2754 | 5788.4297 | 6066.5716 | 6447.9508 | 6890.0852 | 7346.7092 | 7779.0551 | 8255.602 | 8753.4129 | 9326.1233 | 9888.765 | 10518.3301 | 11244.1635 | 11897.7409 | 12332.324 | 12811.5613
SA | 1664.5476 | 1884.0952 | 1969.6925 | 2052.3333 | 2129.5942 | 2211.9976 | 2277.2702 | 2384.7546 | 2510.6842 | 2644.9467 | 2763.8445 | 2895.5309 | 2993.7171 | 3136.125 | 3268.1915 | 3418.4965 | 3588.1496 | 3728.9238 | 3802.675 | 3890.7956
TAS | 214.8057 | 261.3827 | 277.3373 | 282.2644 | 310.6377 | 339.1272 | 364.1057 | 392.0528 | 422.5436 | 458.7211 | 495.343 | 535.8657 | 547.764 | 565.924 | 581.8506 | 601.0061 | 626.6857 | 645.3346 | 648.5071 | 654.7825
VIC | 2423.6385 | 3032.6634 | 3269.303 | 3344.0164 | 3443.5391 | 3559.0971 | 3645.0315 | 3819.1256 | 4024.4898 | 4240.6369 | 4467.5487 | 4729.4244 | 4996.8461 | 5346.3918 | 5698.1755 | 6114.088 | 6641.7544 | 7061.5733 | 7273.2298 | 7520.7255
Strong Rooftop PV uptake
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 2265.6026 | 2483.458 | 2867.7836 | 3233.0081 | 3609.5756 | 3993.5381 | 4414.3791 | 4831.9915 | 5304.0646 | 5839.9025 | 6492.899 | 7218.7981 | 8102.3962 | 9098.2409 | 10182.4899 | 11144.668 | 12008.5108 | 12699.5404 | 13275.3057 | 13658.0467
QLD | 2975.4319 | 2975.4319 | 3222.4665 | 3460.5679 | 3719.6398 | 3992.6224 | 4303.1288 | 4621.7227 | 5020.5331 | 5522.7667 | 6188.4806 | 6971.8627 | 7922.0241 | 8926.7771 | 9888.43 | 10610.2344 | 11174.7343 | 11620.0702 | 12031.8179 | 12285.6893
SA | 861.7137 | 1341.0071 | 1468.2303 | 1582.8273 | 1705.2641 | 1836.5549 | 1988.9314 | 2138.7836 | 2294.4541 | 2429.39 | 2545.0817 | 2619.0374 | 2688.4837 | 2748.7199 | 2814.0656 | 2856.5319 | 2908.3221 | 2957.7157 | 3016.1835 | 3050.1178
TAS | 153.6459 | 181.6886 | 211.2507 | 240.168 | 271.3424 | 303.0057 | 336.7238 | 368.5184 | 403.196 | 438.7227 | 477.8089 | 514.522 | 556.8064 | 603.9711 | 660.8094 | 719.2707 | 788.5829 | 863.4629 | 944.6385 | 1013.2334
VIC | 1668.9733 | 1932.9441 | 2273.1277 | 2609.1686 | 2972.1789 | 3354.9143 | 3786.0085 | 4223.4713 | 4724.6657 | 5299.4489 | 6009.5841 | 6820.6804 | 7855.8662 | 9106.5991 | 10578.2109 | 12030.7535 | 13456.2595 | 14670.1896 | 15682.8978 | 16312.4407
Rooftop PV generation relative to demand
Percentage of generation that is sourced from rooftop PV and small-scale non-scheduled generating systems relative to underlying demand
Neutral
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 4.926% | 6.14% | 6.748% | 7.045% | 7.391% | 7.69% | 7.889% | 8.204% | 8.548% | 8.875% | 9.128% | 9.388% | 9.564% | 9.806% | 10.03% | 10.32% | 10.8% | 11.16% | 11.22% | 11.31%
QLD | 7.416% | 8.226% | 8.936% | 9.419% | 9.874% | 10.34% | 10.74% | 11.34% | 12.05% | 12.72% | 13.34% | 13.99% | 14.67% | 15.45% | 16.22% | 17.07% | 18.05% | 18.87% | 19.37% | 19.92%
SA | 12.13% | 13.73% | 14.28% | 14.39% | 14.9% | 15.36% | 15.68% | 16.54% | 17.5% | 18.24% | 18.9% | 19.58% | 19.98% | 20.72% | 21.33% | 22.23% | 23.07% | 23.72% | 23.94% | 24.23%
TAS | 2.026% | 2.449% | 2.579% | 2.607% | 2.892% | 3.14% | 3.348% | 3.627% | 3.925% | 4.229% | 4.546% | 4.914% | 5.011% | 5.142% | 5.252% | 5.39% | 5.585% | 5.717% | 5.709% | 5.724%
VIC | 5.3% | 6.562% | 6.995% | 7.064% | 7.236% | 7.398% | 7.448% | 7.781% | 8.16% | 8.432% | 8.725% | 9.06% | 9.376% | 9.81% | 10.22% | 10.73% | 11.42% | 11.9% | 12.04% | 12.23%
Strong Rooftop PV uptake
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 3.229% | 3.508% | 4.021% | 4.508% | 5.044% | 5.539% | 6.047% | 6.522% | 7.05% | 7.641% | 8.358% | 9.118% | 10.04% | 11.1% | 12.24% | 13.18% | 13.98% | 14.55% | 14.98% | 15.18%
QLD | 5.574% | 5.532% | 5.948% | 6.317% | 6.717% | 7.131% | 7.62% | 8.132% | 8.778% | 9.561% | 10.61% | 11.82% | 13.27% | 14.79% | 16.22% | 17.22% | 17.94% | 18.43% | 18.9% | 19.1%
SA | 6.282% | 9.776% | 10.64% | 11.1% | 11.93% | 12.76% | 13.69% | 14.84% | 15.99% | 16.75% | 17.4% | 17.71% | 17.94% | 18.16% | 18.36% | 18.57% | 18.7% | 18.81% | 18.99% | 18.99%
TAS | 1.449% | 1.702% | 1.965% | 2.218% | 2.527% | 2.806% | 3.097% | 3.409% | 3.745% | 4.045% | 4.385% | 4.719% | 5.094% | 5.488% | 5.964% | 6.45% | 7.028% | 7.649% | 8.315% | 8.858%
VIC | 3.65% | 4.182% | 4.864% | 5.512% | 6.246% | 6.973% | 7.736% | 8.605% | 9.579% | 10.54% | 11.74% | 13.07% | 14.74% | 16.71% | 18.98% | 21.12% | 23.14% | 24.73% | 25.96% | 26.53%

## Electric Vehicles
Go to Assumptions Summary
Electric Vehicles (Energy, MWh)
Amount of energy consumed by electric vehicles
Neutral
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 15213.5963 | 19524.7019 | 31688.7321 | 52642.6696 | 88036.7352 | 146613.3686 | 234717.3019 | 370686.5676 | 574627.6663 | 873302.4788 | 1305169.9269 | 1901657.3942 | 2507879.9577 | 3105038.8817 | 3698444.999 | 4289780.1066 | 4850695.4673 | 5460952.0156 | 6072750.2884 | 6681253.0596
Qld | 3881.1547 | 6158.2846 | 13498.513 | 26284.5485 | 47568.8734 | 82357.5256 | 134952.024 | 216432.4183 | 339794.0514 | 520546.132 | 778218.4498 | 1128218.7047 | 1484002.9312 | 1841912.1758 | 2204944.033 | 2577170.0949 | 2940929.0051 | 3341743.4493 | 3750261.1872 | 4162643.2926
SA | 1849.2296 | 2559.9745 | 4681.9684 | 8574.7464 | 15241.0983 | 26147.5277 | 42247.1288 | 66766.8591 | 102934.7939 | 154929.0235 | 228643.7215 | 325584.3835 | 421656.4103 | 516315.0111 | 610889.634 | 706703.9638 | 798340.6342 | 899221.419 | 1002192.4342 | 1104729.5984
Tas | 950.733 | 939.4928 | 1356.221 | 2328.5421 | 4047.1299 | 6781.3644 | 10598.4744 | 16430.8939 | 24709.83 | 35816.2114 | 49756.9204 | 66813.7027 | 83154.44 | 98992.1824 | 115377.7061 | 133108.0446 | 150775.1394 | 171131.1789 | 192610.7117 | 214565.6088
Vic | 16577.159 | 20971.7571 | 33108.4741 | 53710.6764 | 88707.7107 | 146462.5167 | 231395.8252 | 360448.7343 | 552090.8799 | 831797.8515 | 1230190.6508 | 1764358.1258 | 2308547.4358 | 2850406.0374 | 3391928.327 | 3933604.7875 | 4447316.5175 | 5002245.2577 | 5553394.6046 | 6095768.325
Fast
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 17569.9751 | 28117.2353 | 57949.1452 | 111017.5223 | 205877.92 | 369946.2709 | 646362.9561 | 1015220.7855 | 1526282.4989 | 2236948.5527 | 3082265.6943 | 3907387.2206 | 4718250.9519 | 5512773.4898 | 6306117.1338 | 7106290.329 | 7876623.1245 | 8744606.5716 | 9628515.4875 | 10515238.051
Qld | 5111.1746 | 10601.581 | 27343.0531 | 58709.3214 | 116603.9148 | 217541.7583 | 389729.6972 | 619316.8343 | 940931.9313 | 1394642.3736 | 1908144.0505 | 2419247.6093 | 2933156.8484 | 3449362.17 | 3981657.8599 | 4536354.2863 | 5091201.8972 | 5726991.468 | 6390184.3482 | 7072135.6338
SA | 2243.5088 | 4018.4008 | 9550.2779 | 19992.4577 | 39128.7549 | 71956.2278 | 125416.7287 | 195898.9461 | 291816.2926 | 422113.1325 | 567519.2727 | 709164.7816 | 848045.1313 | 982392.1755 | 1117731.587 | 1254587.124 | 1388043.7703 | 1540026.9886 | 1697384.902 | 1858302.997
Tas | 1034.9878 | 1353.1113 | 2910.8188 | 5967.7002 | 11274.933 | 20081.4352 | 34267.5397 | 53012.6455 | 77680.568 | 110075.3389 | 141501.2075 | 170889.6365 | 199161.674 | 226055.1021 | 253646.8499 | 282986.7255 | 312800.8247 | 346979.901 | 383866.482 | 422414.1461
Vic | 20390.234 | 33489.6662 | 65800.9641 | 124022.2857 | 226174.2702 | 393916.6243 | 659639.5956 | 1007580.0702 | 1480911.2744 | 2126628.8128 | 2878185.7398 | 3625006.8306 | 4369232.3707 | 5104029.7272 | 5843803.9367 | 6592728.9986 | 7315932.844 | 8124134.0674 | 8943785.1724 | 9767310.3896
Slow
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 11228.0499 | 11499.8709 | 14589.0086 | 20362.065 | 30992.0967 | 48704.6903 | 71996.5743 | 107223.4142 | 156835.4998 | 228057.5291 | 328571.8932 | 467663.2415 | 690577.606 | 970924.9808 | 1325046.4128 | 1763529.8497 | 2289067.3316 | 2839415.9793 | 3395244.0067 | 3954886.8561
Qld | 2422.7336 | 2512.4558 | 3823.9117 | 7208.1879 | 14001.0237 | 25597.5736 | 41252.8136 | 64442.0939 | 97435.4888 | 144411.9098 | 209943.4756 | 299232.4581 | 428432.4296 | 591388.2952 | 799352.5803 | 1063222.0864 | 1386188.2575 | 1728832.6666 | 2079994.7587 | 2435825.7541
SA | 1276.9298 | 1273.8027 | 1838.6827 | 2909.4964 | 5094.8777 | 9183.117 | 14692.7252 | 22787.8905 | 34520.4898 | 50804.8331 | 73172.1616 | 102838.8831 | 147904.0109 | 200389.03 | 262725.4007 | 338392.9161 | 428424.6667 | 524113.7202 | 621002.8376 | 716767.3728
Tas | 938.7039 | 873.975 | 887.7767 | 992.6363 | 1366.6911 | 2269.8617 | 3406.0828 | 5226.7858 | 7588.5261 | 10794.195 | 14948.6876 | 20190.9229 | 26844.9699 | 34637.2397 | 44358.1154 | 56906.7575 | 72544.7712 | 89565.2372 | 107237.1157 | 125225.4599
Vic | 11724.806 | 12191.5233 | 15540.6004 | 21307.2055 | 32124.6144 | 50360.7711 | 75000.4686 | 111341.1365 | 162221.9991 | 234009.0262 | 333885.1448 | 471172.6031 | 715255.0729 | 1007453.8209 | 1356355.0569 | 1768006.7446 | 2239478.6353 | 2731062.5175 | 3223675.5113 | 3713449.3584
Electric vehicle consumption share of operational demand
Neutral
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 0.02281% | 0.02939% | 0.04765% | 0.07897% | 0.1329% | 0.2203% | 0.3491% | 0.545% | 0.8352% | 1.254% | 1.849% | 2.651% | 3.438% | 4.199% | 4.943% | 5.658% | 6.329% | 7.043% | 7.718% | 8.373%
Qld | 0.007853% | 0.01248% | 0.02736% | 0.05297% | 0.09531% | 0.1641% | 0.2677% | 0.4295% | 0.6755% | 1.033% | 1.54% | 2.224% | 2.914% | 3.609% | 4.317% | 5.045% | 5.762% | 6.532% | 7.305% | 8.081%
SA | 0.01534% | 0.02163% | 0.03959% | 0.07023% | 0.1253% | 0.2146% | 0.3449% | 0.5549% | 0.8694% | 1.307% | 1.928% | 2.737% | 3.517% | 4.302% | 5.067% | 5.909% | 6.671% | 7.498% | 8.297% | 9.079%
Tas | 0.009152% | 0.009023% | 0.01295% | 0.02208% | 0.03881% | 0.06483% | 0.1008% | 0.1577% | 0.2389% | 0.3448% | 0.4784% | 0.6444% | 0.8008% | 0.9483% | 1.099% | 1.262% | 1.423% | 1.608% | 1.798% | 1.99%
Vic | 0.03828% | 0.04856% | 0.07617% | 0.1221% | 0.2009% | 0.3287% | 0.5109% | 0.7963% | 1.219% | 1.806% | 2.632% | 3.716% | 4.78% | 5.799% | 6.779% | 7.736% | 8.633% | 9.571% | 10.45% | 11.3%
Fast
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 0.02637% | 0.04234% | 0.08731% | 0.1673% | 0.3079% | 0.5503% | 0.9459% | 1.459% | 2.15% | 3.083% | 4.158% | 5.152% | 6.08% | 6.982% | 7.821% | 8.64% | 9.412% | 10.25% | 11.05% | 11.81%
Qld | 0.01026% | 0.02124% | 0.05474% | 0.117% | 0.2311% | 0.4298% | 0.7585% | 1.199% | 1.756% | 2.582% | 3.504% | 4.406% | 5.31% | 6.202% | 7.17% | 8.133% | 9.092% | 10.15% | 11.22% | 12.29%
SA | 0.01855% | 0.03378% | 0.08016% | 0.1616% | 0.3143% | 0.5788% | 0.9963% | 1.551% | 2.283% | 3.261% | 4.318% | 5.324% | 6.278% | 7.197% | 8.085% | 9.05% | 9.918% | 10.89% | 11.81% | 12.72%
Tas | 0.00995% | 0.01295% | 0.02762% | 0.05605% | 0.1052% | 0.1867% | 0.3162% | 0.4897% | 0.7098% | 0.9947% | 1.267% | 1.523% | 1.757% | 1.971% | 2.185% | 2.41% | 2.637% | 2.891% | 3.155% | 3.423%
Vic | 0.04672% | 0.0767% | 0.1492% | 0.277% | 0.4963% | 0.8573% | 1.401% | 2.108% | 3.021% | 4.219% | 5.548% | 6.794% | 7.973% | 9.101% | 10.17% | 11.21% | 12.19% | 13.23% | 14.22% | 15.18%
Slow
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 0.01688% | 0.01746% | 0.02207% | 0.03081% | 0.04677% | 0.07484% | 0.11% | 0.1628% | 0.2369% | 0.3429% | 0.5143% | 0.768% | 1.192% | 1.71% | 2.337% | 3.085% | 3.978% | 4.897% | 5.788% | 6.67%
Qld | 0.00492% | 0.005175% | 0.007965% | 0.01508% | 0.02927% | 0.05413% | 0.08811% | 0.1404% | 0.2146% | 0.3217% | 0.5706% | 0.8239% | 1.213% | 1.676% | 2.291% | 3.054% | 3.988% | 4.979% | 5.97% | 6.975%
SA | 0.01084% | 0.01107% | 0.01601% | 0.02456% | 0.04368% | 0.08079% | 0.1292% | 0.2055% | 0.3168% | 0.4696% | 0.68% | 0.9723% | 1.438% | 2.034% | 2.689% | 3.532% | 4.5% | 5.54% | 6.555% | 7.552%
Tas | 0.009048% | 0.008769% | 0.008882% | 0.009901% | 0.01379% | 0.02331% | 0.03501% | 0.0584% | 0.08488% | 0.1209% | 0.1678% | 0.231% | 0.3174% | 0.4245% | 0.5504% | 0.7074% | 0.9178% | 1.137% | 1.36% | 1.587%
Vic | 0.02699% | 0.02819% | 0.03571% | 0.05111% | 0.0816% | 0.1309% | 0.1926% | 0.2888% | 0.4213% | 0.6019% | 0.8511% | 1.204% | 1.86% | 2.657% | 3.532% | 4.548% | 5.699% | 6.876% | 7.994% | 9.083%
Electric Vehicles (Charge Type, % of fleet)
Split between time of day electric vehicles are charged
Slow
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
Evening/Convenience | 83.7% | 75.55% | 70.66% | 65.77% | 60.88% | 55.99% | 51.1% | 47.84% | 44.58% | 41.32% | 38.06% | 34.8% | 33.17% | 31.54% | 29.91% | 28.28% | 26.65% | 25.02% | 23.39% | 21.76%
Overnight | 8.15% | 12.22% | 14.67% | 17.12% | 19.56% | 22% | 24.45% | 26.08% | 27.71% | 29.34% | 30.97% | 32.6% | 33.41% | 34.23% | 35.05% | 35.86% | 36.68% | 37.49% | 38.3% | 39.12%
Daytime | 8.15% | 12.22% | 14.67% | 17.12% | 19.56% | 22% | 24.45% | 26.08% | 27.71% | 29.34% | 30.97% | 32.6% | 33.41% | 34.23% | 35.05% | 35.86% | 36.68% | 37.49% | 38.3% | 39.12%
Neutral
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
Evening/Convenience | 87.32% | 80.98% | 77.18% | 73.38% | 69.57% | 65.77% | 61.97% | 59.43% | 56.9% | 54.36% | 51.82% | 49.29% | 48.02% | 46.75% | 45.49% | 44.22% | 42.95% | 41.68% | 40.41% | 39.15%
Overnight | 6.339% | 9.508% | 11.41% | 13.31% | 15.21% | 17.12% | 19.02% | 20.28% | 21.55% | 22.82% | 24.09% | 25.36% | 25.99% | 26.62% | 27.26% | 27.89% | 28.52% | 29.16% | 29.79% | 30.43%
Daytime | 6.339% | 9.508% | 11.41% | 13.31% | 15.21% | 17.12% | 19.02% | 20.28% | 21.55% | 22.82% | 24.09% | 25.36% | 25.99% | 26.62% | 27.26% | 27.89% | 28.52% | 29.16% | 29.79% | 30.43%
Fast
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
Evening/Convenience | 98.19% | 97.28% | 96.74% | 96.2% | 95.65% | 95.11% | 94.57% | 94.2% | 93.84% | 93.48% | 93.12% | 92.76% | 92.57% | 92.39% | 92.21% | 92.03% | 91.85% | 91.67% | 91.49% | 91.31%
Overnight | 0.9056% | 1.358% | 1.63% | 1.902% | 2.173% | 2.445% | 2.717% | 2.898% | 3.079% | 3.26% | 3.441% | 3.622% | 3.713% | 3.803% | 3.894% | 3.984% | 4.075% | 4.166% | 4.256% | 4.347%
Daytime | 0.9056% | 1.358% | 1.63% | 1.902% | 2.173% | 2.445% | 2.717% | 2.898% | 3.079% | 3.26% | 3.441% | 3.622% | 3.713% | 3.803% | 3.894% | 3.984% | 4.075% | 4.166% | 4.256% | 4.347%
Electric Vehicle Charge Profile (kW/car)
NEM Time | 0:30 | 1:00 | 1:30 | 2:00 | 2:30 | 3:00 | 3:30 | 4:00 | 4:30 | 5:00 | 5:30 | 6:00 | 6:30 | 7:00 | 7:30 | 8:00 | 8:30 | 9:00 | 9:30 | 10:00 | 12:00 | 12:30 | 13:00 | 13:30 | 14:00 | 14:30 | 15:00 | 15:30 | 16:00 | 16:30 | 17:00 | 17:30 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 20:30 | 21:00 | 21:30 | 22:00 | 22:30 | 23:00 | 23:30 | 24:00
Evening/Convenience (kW/car) | 0.11302 | 0.081756 | 0.06252 | 0.043283 | 0.04689 | 0.050497 | 0.049294 | 0.048092 | 0.052901 | 0.05771 | 0.054825 | 0.051939 | 0.064443 | 0.076947 | 0.098589 | 0.12023 | 0.18996 | 0.2597 | 0.31164 | 0.36358 | 0.36358 | 0.35011 | 0.33664 | 0.38474 | 0.43283 | 0.41119 | 0.38955 | 0.41119 | 0.43283 | 0.4689 | 0.50497 | 0.61317 | 0.72138 | 0.8897 | 1.058 | 1.1226 | 1.1872 | 1.1467 | 1.1061 | 0.86566 | 0.6252 | 0.43283 | 0.24046 | 0.19237 | 0.17334
Overnight (kW/car) | 0.5973 | 0.71369 | 0.71369 | 0.71369 | 0.71369 | 0.71369 | 0.71369 | 0.71369 | 0.71369 | 0.71369 | 0.5973 | 0.48092 | 0.40878 | 0.33664 | 0.28855 | 0.24046 | 0.25008 | 0.2597 | 0.31164 | 0.36358 | 0.36358 | 0.35011 | 0.33664 | 0.38474 | 0.43283 | 0.41119 | 0.38955 | 0.29096 | 0.19237 | 0.16832 | 0.14428 | 0.14428 | 0.14428 | 0.14428 | 0.14428 | 0.14428 | 0.14428 | 0.14428 | 0.14428 | 0.1688 | 0.19333 | 0.26499 | 0.33664 | 0.40878 | 0.57778
Daytime (kW/car) | 0.26835 | 0.19237 | 0.18034 | 0.16832 | 0.16832 | 0.16832 | 0.16832 | 0.16832 | 0.16832 | 0.16832 | 0.16832 | 0.16832 | 0.1563 | 0.14428 | 0.16832 | 0.19237 | 0.3126 | 0.43283 | 0.64924 | 0.86566 | 1.2023 | 1.1542 | 1.1061 | 0.98589 | 0.86566 | 0.64924 | 0.43283 | 0.3126 | 0.19237 | 0.16832 | 0.14428 | 0.14428 | 0.14428 | 0.14428 | 0.14428 | 0.14428 | 0.14428 | 0.14428 | 0.14428 | 0.1688 | 0.19333 | 0.21689 | 0.24046 | 0.2924 | 0.41369
Electric Vehicle Charge Profile (kW/car)

## DSP
Go to Assumptions Summary
Demand-side Participation (MW)
Expected voluntary consumer demand management resulting in reductions of demand at various price levels. This demand response is considered an alternative source of supply - that is, the Maximum Demands are 'gross' of this demand response.
Neutral
Queensland
Summer
Price band | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
$300 - $500 | 32.46 | 34.0523 | 35.0223 | 37.4238 | 38.8108 | 40.3889 | 42.3314 | 43.1421 | 45.3484 | 48.2758 | 50.3232 | 51.5702 | 53.0035 | 53.8757 | 55.23 | 57.875 | 59.6883 | 61.6696 | 63.3588 | 63.0905
$500 - $1,000 | 0.36 | 0.37766 | 0.38842 | 0.41505 | 0.43043 | 0.44794 | 0.46948 | 0.47847 | 0.50294 | 0.53541 | 0.55811 | 0.57194 | 0.58784 | 0.59751 | 0.61253 | 0.64187 | 0.66198 | 0.68395 | 0.70269 | 0.69971
$1,000 - $7,500 | 1.09 | 1.1435 | 1.176 | 1.2567 | 1.3033 | 1.3563 | 1.4215 | 1.4487 | 1.5228 | 1.6211 | 1.6898 | 1.7317 | 1.7798 | 1.8091 | 1.8546 | 1.9434 | 2.0043 | 2.0709 | 2.1276 | 2.1186
$7,500 - MPC | 6.39 | 6.7034 | 6.8944 | 7.3672 | 7.6402 | 7.9509 | 8.3333 | 8.4929 | 8.9272 | 9.5035 | 9.9065 | 10.152 | 10.4342 | 10.6059 | 10.8724 | 11.3931 | 11.7501 | 12.1401 | 12.4727 | 12.4198
MPC | 176.07 | 184.7068 | 189.9683 | 202.9947 | 210.5183 | 219.0782 | 229.6145 | 234.0121 | 245.9797 | 261.858 | 272.9639 | 279.728 | 287.5026 | 292.2335 | 299.5793 | 313.9262 | 323.7621 | 334.5094 | 343.6718 | 342.2164
Winter
Price band | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037
$300 - $500 | 32.46 | 34.1414 | 35.6642 | 37.5711 | 39.4311 | 41.0965 | 42.5687 | 44.3402 | 47.1498 | 49.1788 | 50.8992 | 52.2082 | 54.2172 | 56.2999 | 58.3806 | 60.1988 | 61.6958 | 63.0391 | 65.8321 | 67.0766
$500 - $1,000 | 0.36 | 0.37865 | 0.39554 | 0.41669 | 0.43731 | 0.45578 | 0.47211 | 0.49176 | 0.52292 | 0.54542 | 0.5645 | 0.57902 | 0.6013 | 0.6244 | 0.64747 | 0.66764 | 0.68424 | 0.69914 | 0.73012 | 0.74392
$1,000 - $7,500 | 1.09 | 1.1465 | 1.1976 | 1.2616 | 1.3241 | 1.38 | 1.4294 | 1.4889 | 1.5833 | 1.6514 | 1.7092 | 1.7531 | 1.8206 | 1.8905 | 1.9604 | 2.0215 | 2.0717 | 2.1168 | 2.2106 | 2.2524
$7,500 - MPC | 6.39 | 6.721 | 7.0208 | 7.3962 | 7.7623 | 8.0902 | 8.38 | 8.7287 | 9.2818 | 9.6812 | 10.0199 | 10.2776 | 10.6731 | 11.0831 | 11.4927 | 11.8506 | 12.1453 | 12.4097 | 12.9596 | 13.2045
MPC | 156.07 | 164.1542 | 171.4761 | 180.6447 | 189.5878 | 197.5948 | 204.6733 | 213.1909 | 226.6995 | 236.455 | 244.727 | 251.0206 | 260.6801 | 270.6941 | 280.6981 | 289.4399 | 296.638 | 303.0966 | 316.5254 | 322.5089
New South Wales
Summer
Price band | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
$300 - $500 | 77.73 | 92.8563 | 108.0428 | 124.3374 | 139.6579 | 155.3028 | 170.6709 | 189.0836 | 208.1586 | 227.304 | 242.2635 | 257.6907 | 278.0438 | 292.7794 | 309.5983 | 328.5481 | 345.6494 | 363.7884 | 389.4479 | 404.0981
$500 - $1,000 | 0.27 | 0.32254 | 0.37529 | 0.43189 | 0.48511 | 0.53945 | 0.59284 | 0.65679 | 0.72305 | 0.78955 | 0.84152 | 0.8951 | 0.9658 | 1.017 | 1.0754 | 1.1412 | 1.2006 | 1.2636 | 1.3528 | 1.4037
$1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$7,500 - MPC | 27.01 | 32.2662 | 37.5432 | 43.2054 | 48.529 | 53.9654 | 59.3056 | 65.7037 | 72.332 | 78.9847 | 84.1829 | 89.5436 | 96.616 | 101.7364 | 107.5807 | 114.1655 | 120.1079 | 126.411 | 135.3273 | 140.418
MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Winter
Price band | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037
$300 - $500 | 77.73 | 91.1095 | 106.5544 | 121.6801 | 137.0607 | 153.3086 | 167.8506 | 185.994 | 204.6604 | 222.6753 | 240.9582 | 255.9211 | 273.4598 | 293.9347 | 312.0123 | 332.788 | 355.1466 | 371.3282 | 397.058 | 414.3212
$500 - $1,000 | 0.27 | 0.31647 | 0.37012 | 0.42266 | 0.47609 | 0.53253 | 0.58304 | 0.64606 | 0.7109 | 0.77348 | 0.83698 | 0.88896 | 0.94988 | 1.021 | 1.0838 | 1.156 | 1.2336 | 1.2898 | 1.3792 | 1.4392
$1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$7,500 - MPC | 27.01 | 31.6592 | 37.0261 | 42.282 | 47.6265 | 53.2724 | 58.3256 | 64.6301 | 71.1164 | 77.3763 | 83.7293 | 88.9287 | 95.0231 | 102.1379 | 108.4195 | 115.6388 | 123.4081 | 129.031 | 137.9716 | 143.9703
MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Victoria
Summer
Price band | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
$300 - $500 | 28.3775 | 33.5 | 38.1748 | 43.9435 | 47.927 | 51.5418 | 57.3114 | 62.2751 | 67.5559 | 73.2614 | 78.4449 | 84.3275 | 89.0691 | 95.2638 | 101.2641 | 105.7532 | 109.7958 | 117.4408 | 124.6182 | 128.8018
$500 - $1,000 | 3.04 | 3.5888 | 4.0896 | 4.7075 | 5.1343 | 5.5215 | 6.1396 | 6.6714 | 7.2371 | 7.8483 | 8.4036 | 9.0338 | 9.5417 | 10.2053 | 10.8481 | 11.329 | 11.7621 | 12.5811 | 13.35 | 13.7982
$1,000 - $7,500 | 1.6 | 1.8888 | 2.1524 | 2.4777 | 2.7023 | 2.9061 | 3.2314 | 3.5112 | 3.809 | 4.1307 | 4.4229 | 4.7546 | 5.022 | 5.3712 | 5.7095 | 5.9627 | 6.1906 | 6.6216 | 7.0263 | 7.2622
$7,500 - MPC | 0.66 | 0.77914 | 0.88787 | 1.022 | 1.1147 | 1.1988 | 1.3329 | 1.4484 | 1.5712 | 1.7039 | 1.8245 | 1.9613 | 2.0716 | 2.2156 | 2.3552 | 2.4596 | 2.5536 | 2.7314 | 2.8984 | 2.9957
MPC | 43.5 | 51.3524 | 58.5184 | 67.3612 | 73.4676 | 79.0087 | 87.8531 | 95.4619 | 103.5568 | 112.3029 | 120.2486 | 129.2661 | 136.5345 | 146.0304 | 155.2283 | 162.1097 | 168.3067 | 180.0256 | 191.028 | 197.4411
Winter
Price band | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037
$300 - $500 | 28.3775 | 37.231 | 46.2061 | 55.1565 | 63.3412 | 71.9342 | 80.2684 | 88.2698 | 99.0359 | 108.6035 | 119.0805 | 128.508 | 137.1636 | 149.2975 | 159.8409 | 169.5051 | 180.5924 | 191.5764 | 203.6471 | 216.1936
$500 - $1,000 | 3.04 | 3.9885 | 4.9499 | 5.9088 | 6.7856 | 7.7061 | 8.5989 | 9.4561 | 10.6094 | 11.6344 | 12.7568 | 13.7667 | 14.694 | 15.9938 | 17.1233 | 18.1586 | 19.3464 | 20.523 | 21.8161 | 23.1602
$1,000 - $7,500 | 1.6 | 2.0992 | 2.6052 | 3.1099 | 3.5714 | 4.0558 | 4.5258 | 4.9769 | 5.5839 | 6.1234 | 6.7141 | 7.2456 | 7.7337 | 8.4178 | 9.0123 | 9.5572 | 10.1823 | 10.8016 | 11.4822 | 12.1896
$7,500 - MPC | 0.66 | 0.86591 | 1.0747 | 1.2828 | 1.4732 | 1.673 | 1.8669 | 2.053 | 2.3034 | 2.5259 | 2.7696 | 2.9888 | 3.1901 | 3.4723 | 3.7176 | 3.9423 | 4.2002 | 4.4557 | 4.7364 | 5.0282
MPC | 6.5 | 8.5279 | 10.5837 | 12.6339 | 14.5086 | 16.4769 | 18.3859 | 20.2186 | 22.6846 | 24.8762 | 27.276 | 29.4354 | 31.418 | 34.1973 | 36.6123 | 38.826 | 41.3656 | 43.8815 | 46.6464 | 49.5202
South Australia
Summer
Price band | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
$300 - $500 | 1.2201 | 2.1927 | 3.1942 | 4.1003 | 5.0211 | 6.0119 | 6.8831 | 7.9672 | 8.9668 | 9.8215 | 10.7647 | 11.6576 | 12.7598 | 13.8323 | 14.7823 | 15.6548 | 16.5292 | 17.477 | 18.6323 | 19.7909
$500 - $1,000 | 0.86 | 1.5455 | 2.2515 | 2.8902 | 3.5392 | 4.2376 | 4.8516 | 5.6158 | 6.3204 | 6.9228 | 7.5876 | 8.217 | 8.9939 | 9.7499 | 10.4195 | 11.0345 | 11.6508 | 12.3189 | 13.1332 | 13.9498
$1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$7,500 - MPC | 4.35 | 7.8176 | 11.3882 | 14.6189 | 17.9017 | 21.4343 | 24.5402 | 28.4056 | 31.9693 | 35.0164 | 38.3791 | 41.5628 | 45.4923 | 49.3163 | 52.7033 | 55.8141 | 58.9315 | 62.3105 | 66.4296 | 70.5602
MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Winter
Price band | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037
$300 - $500 | 1.2201 | 2.038 | 2.93 | 3.762 | 4.6431 | 5.5506 | 6.4077 | 7.312 | 8.2695 | 9.2163 | 10.1806 | 11.0565 | 11.9581 | 13.0218 | 14.0519 | 15.0213 | 16.0601 | 17.1054 | 18.0892 | 19.1628
$500 - $1,000 | 0.86 | 1.4365 | 2.0653 | 2.6517 | 3.2728 | 3.9124 | 4.5165 | 5.1539 | 5.8289 | 6.4962 | 7.1759 | 7.7933 | 8.4288 | 9.1786 | 9.9047 | 10.5879 | 11.3202 | 12.0569 | 12.7504 | 13.5072
$1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$7,500 - MPC | 4.35 | 7.2661 | 10.4464 | 13.4125 | 16.5541 | 19.7896 | 22.8452 | 26.0693 | 29.4832 | 32.8587 | 36.2967 | 39.4198 | 42.6342 | 46.4266 | 50.0991 | 53.5552 | 57.2589 | 60.9856 | 64.4932 | 68.3212
MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tasmania
Summer
Price band | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
$300 - $500 | 5.55 | 5.726 | 5.8484 | 6.0165 | 5.9282 | 6.0508 | 6.2067 | 6.3571 | 6.5266 | 6.6833 | 6.8983 | 7.0787 | 7.2692 | 7.3901 | 7.4919 | 7.6263 | 7.82 | 8.0395 | 8.1791 | 8.3766
$500 - $1,000 | 13.2 | 13.6185 | 13.9097 | 14.3095 | 14.0995 | 14.3912 | 14.7618 | 15.1196 | 15.5228 | 15.8953 | 16.4067 | 16.8358 | 17.2888 | 17.5765 | 17.8185 | 18.1383 | 18.599 | 19.121 | 19.4531 | 19.9228
$1,000 - $7,500 | 0.5 | 0.51585 | 0.52688 | 0.54203 | 0.53407 | 0.54512 | 0.55916 | 0.57271 | 0.58799 | 0.6021 | 0.62147 | 0.63772 | 0.65488 | 0.66578 | 0.67494 | 0.68706 | 0.70451 | 0.72428 | 0.73686 | 0.75465
$7,500 - MPC | 2.29 | 2.3626 | 2.4131 | 2.4825 | 2.446 | 2.4966 | 2.561 | 2.623 | 2.693 | 2.7576 | 2.8463 | 2.9208 | 2.9994 | 3.0493 | 3.0912 | 3.1467 | 3.2267 | 3.3172 | 3.3748 | 3.4563
MPC | 1.667 | 1.7198 | 1.7566 | 1.8071 | 1.7805 | 1.8174 | 1.8642 | 1.9094 | 1.9603 | 2.0073 | 2.0719 | 2.1261 | 2.1833 | 2.2196 | 2.2502 | 2.2906 | 2.3488 | 2.4147 | 2.4566 | 2.5159
Winter
Price band | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037
$300 - $500 | 5.55 | 5.8179 | 6.0326 | 6.2787 | 6.3105 | 6.5137 | 6.7633 | 6.9532 | 7.2233 | 7.5291 | 7.7943 | 8.086 | 8.3041 | 8.5499 | 8.7832 | 8.9899 | 9.2229 | 9.5133 | 9.7964 | 10.0695
$500 - $1,000 | 13.2 | 13.8372 | 14.3478 | 14.933 | 15.0088 | 15.492 | 16.0856 | 16.5373 | 17.1798 | 17.907 | 18.5378 | 19.2315 | 19.7504 | 20.3348 | 20.8897 | 21.3814 | 21.9355 | 22.6263 | 23.2995 | 23.9492
$1,000 - $7,500 | 0.5 | 0.52413 | 0.54348 | 0.56565 | 0.56851 | 0.58682 | 0.6093 | 0.62641 | 0.65075 | 0.67829 | 0.70219 | 0.72847 | 0.74812 | 0.77026 | 0.79128 | 0.8099 | 0.83089 | 0.85705 | 0.88256 | 0.90717
$7,500 - MPC | 2.29 | 2.4005 | 2.4891 | 2.5907 | 2.6038 | 2.6876 | 2.7906 | 2.869 | 2.9804 | 3.1066 | 3.216 | 3.3364 | 3.4264 | 3.5278 | 3.6241 | 3.7094 | 3.8055 | 3.9253 | 4.0421 | 4.1548
MPC | 1.667 | 1.7474 | 1.8119 | 1.8858 | 1.8954 | 1.9564 | 2.0314 | 2.0884 | 2.1695 | 2.2614 | 2.341 | 2.4286 | 2.4942 | 2.568 | 2.638 | 2.7001 | 2.7701 | 2.8573 | 2.9424 | 3.0244
Strong
Queensland
Summer
Price band | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
$300 - $500 | 32.46 | 35.2097 | 37.1698 | 40.7993 | 43.4656 | 46.9013 | 49.7357 | 52.0509 | 55.5269 | 60.1367 | 63.3705 | 65.9977 | 69.376 | 71.4842 | 74.2128 | 79.2005 | 82.8291 | 86.2015 | 90.0765 | 90.8142
$500 - $1,000 | 0.36 | 0.3905 | 0.41223 | 0.45249 | 0.48206 | 0.52016 | 0.5516 | 0.57727 | 0.61582 | 0.66695 | 0.70281 | 0.73195 | 0.76942 | 0.7928 | 0.82306 | 0.87838 | 0.91862 | 0.95602 | 0.999 | 1.0072
$1,000 - $7,500 | 1.09 | 1.1823 | 1.2482 | 1.37 | 1.4596 | 1.5749 | 1.6701 | 1.7479 | 1.8646 | 2.0194 | 2.128 | 2.2162 | 2.3296 | 2.4004 | 2.4921 | 2.6595 | 2.7814 | 2.8946 | 3.0248 | 3.0495
$7,500 - MPC | 6.39 | 6.9313 | 7.3172 | 8.0316 | 8.5565 | 9.2329 | 9.7909 | 10.2466 | 10.9309 | 11.8384 | 12.475 | 12.9921 | 13.6572 | 14.0722 | 14.6094 | 15.5912 | 16.3056 | 16.9694 | 17.7323 | 17.8775
MPC | 176.07 | 190.985 | 201.617 | 221.3039 | 235.7667 | 254.4029 | 269.7773 | 282.3354 | 301.1896 | 326.1944 | 343.7351 | 357.9855 | 376.3101 | 387.7459 | 402.5462 | 429.6007 | 449.283 | 467.5756 | 488.5944 | 492.5957
Winter
Price band | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037
$300 - $500 | 32.46 | 35.0274 | 38.0183 | 41.1759 | 44.1916 | 47.0181 | 49.6679 | 52.621 | 56.9188 | 60.0547 | 62.9765 | 65.5708 | 68.4285 | 71.8373 | 75.2761 | 78.2355 | 81.1959 | 83.8149 | 87.3673 | 90.8072
$500 - $1,000 | 0.36 | 0.38847 | 0.42164 | 0.45666 | 0.49011 | 0.52146 | 0.55085 | 0.5836 | 0.63126 | 0.66604 | 0.69844 | 0.72722 | 0.75891 | 0.79672 | 0.83486 | 0.86768 | 0.90051 | 0.92956 | 0.96895 | 1.0071
$1,000 - $7,500 | 1.09 | 1.1762 | 1.2766 | 1.3827 | 1.4839 | 1.5789 | 1.6678 | 1.767 | 1.9113 | 2.0166 | 2.1147 | 2.2019 | 2.2978 | 2.4123 | 2.5278 | 2.6271 | 2.7265 | 2.8145 | 2.9338 | 3.0493
$7,500 - MPC | 6.39 | 6.8954 | 7.4842 | 8.1058 | 8.6995 | 9.2559 | 9.7775 | 10.3589 | 11.2049 | 11.8222 | 12.3974 | 12.9081 | 13.4707 | 14.1417 | 14.8187 | 15.4013 | 15.984 | 16.4996 | 17.1989 | 17.8761
MPC | 156.07 | 168.4143 | 182.7945 | 197.9768 | 212.4763 | 226.0664 | 238.807 | 253.0057 | 273.6697 | 288.7471 | 302.7953 | 315.269 | 329.0093 | 345.3991 | 361.9329 | 376.1618 | 390.3955 | 402.9881 | 420.0684 | 436.6076
New South Wales
Summer
Price band | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
$300 - $500 | 77.73 | 103.0066 | 126.8519 | 151.8192 | 176.5757 | 199.9942 | 225.9737 | 253.9989 | 278.5219 | 309.1274 | 333.1624 | 358.1545 | 387.5127 | 412.5448 | 439.2906 | 469.7517 | 492.0782 | 523.2652 | 559.3418 | 590.8385
$500 - $1,000 | 0.27 | 0.3578 | 0.44063 | 0.52735 | 0.61335 | 0.69469 | 0.78493 | 0.88228 | 0.96746 | 1.0738 | 1.1573 | 1.2441 | 1.346 | 1.433 | 1.5259 | 1.6317 | 1.7093 | 1.8176 | 1.9429 | 2.0523
$1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$7,500 - MPC | 27.01 | 35.7932 | 44.0791 | 52.7549 | 61.3574 | 69.495 | 78.5225 | 88.2608 | 96.7821 | 107.4171 | 115.7689 | 124.4533 | 134.6548 | 143.3531 | 152.6468 | 163.2316 | 170.9897 | 181.8267 | 194.3628 | 205.3074
MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Winter
Price band | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037
$300 - $500 | 77.73 | 99.7444 | 123.2241 | 146.852 | 170.0697 | 194.4421 | 215.5349 | 240.6048 | 266.5367 | 290.9246 | 316.3731 | 336.7103 | 361.6822 | 384.5123 | 410.448 | 435.4217 | 461.4406 | 483.1775 | 511.1711 | 535.8229
$500 - $1,000 | 0.27 | 0.34647 | 0.42803 | 0.5101 | 0.59075 | 0.67541 | 0.74867 | 0.83576 | 0.92583 | 1.0105 | 1.0989 | 1.1696 | 1.2563 | 1.3356 | 1.4257 | 1.5125 | 1.6028 | 1.6783 | 1.7756 | 1.8612
$1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$7,500 - MPC | 27.01 | 34.6597 | 42.8185 | 51.0289 | 59.0967 | 67.5657 | 74.8951 | 83.6065 | 92.6175 | 101.0919 | 109.9349 | 117.0017 | 125.6791 | 133.6122 | 142.6245 | 151.3024 | 160.3436 | 167.8969 | 177.6242 | 186.1904
MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Victoria
Summer
Price band | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
$300 - $500 | 28.3775 | 36.477 | 44.655 | 52.9262 | 61.1607 | 68.83 | 79.1677 | 88.382 | 97.5547 | 107.5022 | 115.6123 | 123.798 | 133.9254 | 142.2641 | 151.6663 | 159.6314 | 166.2229 | 182.4354 | 192.7905 | 202.7611
$500 - $1,000 | 3.04 | 3.9077 | 4.7838 | 5.6698 | 6.552 | 7.3736 | 8.481 | 9.4681 | 10.4508 | 11.5164 | 12.3852 | 13.2621 | 14.3471 | 15.2404 | 16.2476 | 17.1009 | 17.807 | 19.5438 | 20.6531 | 21.7212
$1,000 - $7,500 | 1.6 | 2.0567 | 2.5178 | 2.9841 | 3.4484 | 3.8808 | 4.4637 | 4.9832 | 5.5004 | 6.0613 | 6.5185 | 6.9801 | 7.5511 | 8.0212 | 8.5514 | 9.0005 | 9.3721 | 10.2862 | 10.8701 | 11.4322
$7,500 - MPC | 0.66 | 0.84838 | 1.0386 | 1.231 | 1.4225 | 1.6008 | 1.8413 | 2.0556 | 2.2689 | 2.5003 | 2.6889 | 2.8793 | 3.1148 | 3.3088 | 3.5274 | 3.7127 | 3.866 | 4.2431 | 4.4839 | 4.7158
MPC | 43.5 | 55.9159 | 68.4519 | 81.1309 | 93.7536 | 105.5099 | 121.3566 | 135.4813 | 149.5422 | 164.7907 | 177.2227 | 189.7706 | 205.2951 | 218.0775 | 232.4901 | 244.6999 | 254.804 | 279.6564 | 295.5296 | 310.8137
Winter
Price band | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037
$300 - $500 | 28.3775 | 42.0027 | 55.8353 | 69.5673 | 84.0319 | 98.4561 | 113.2009 | 128.7267 | 143.2602 | 158.0867 | 174.0511 | 187.0908 | 201.6314 | 217.202 | 232.053 | 247.5899 | 262.2023 | 277.5009 | 294.4607 | 311.0968
$500 - $1,000 | 3.04 | 4.4996 | 5.9815 | 7.4526 | 9.0021 | 10.5473 | 12.1269 | 13.7901 | 15.3471 | 16.9354 | 18.6456 | 20.0425 | 21.6002 | 23.2682 | 24.8592 | 26.5236 | 28.089 | 29.7279 | 31.5448 | 33.3269
$1,000 - $7,500 | 1.6 | 2.3682 | 3.1481 | 3.9224 | 4.738 | 5.5512 | 6.3826 | 7.258 | 8.0774 | 8.9134 | 9.8135 | 10.5487 | 11.3685 | 12.2464 | 13.0838 | 13.9598 | 14.7837 | 15.6463 | 16.6025 | 17.5405
$7,500 - MPC | 0.66 | 0.97689 | 1.2986 | 1.618 | 1.9544 | 2.2899 | 2.6328 | 2.9939 | 3.3319 | 3.6768 | 4.0481 | 4.3513 | 4.6895 | 5.0517 | 5.3971 | 5.7584 | 6.0983 | 6.4541 | 6.8485 | 7.2355
MPC | 6.5 | 9.6209 | 12.7893 | 15.9347 | 19.2479 | 22.5519 | 25.9292 | 29.4855 | 32.8144 | 36.2105 | 39.8673 | 42.8541 | 46.1847 | 49.7512 | 53.1529 | 56.7117 | 60.0587 | 63.5629 | 67.4477 | 71.2582
South Australia
Summer
Price band | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
$300 - $500 | 1.2201 | 2.6899 | 4.206 | 5.5475 | 6.9365 | 8.3085 | 9.7354 | 11.351 | 12.8297 | 14.144 | 15.5487 | 16.7871 | 18.3041 | 19.7434 | 21.2268 | 22.4805 | 23.7152 | 25.3123 | 27.1335 | 28.6408
$500 - $1,000 | 0.86 | 1.896 | 2.9647 | 3.9103 | 4.8893 | 5.8564 | 6.8622 | 8.0009 | 9.0432 | 9.9696 | 10.9597 | 11.8326 | 12.9019 | 13.9164 | 14.962 | 15.8457 | 16.7159 | 17.8417 | 19.1254 | 20.1878
$1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$7,500 - MPC | 4.35 | 9.5904 | 14.9956 | 19.7786 | 24.7306 | 29.6223 | 34.7097 | 40.4697 | 45.7415 | 50.4276 | 55.4358 | 59.851 | 65.2595 | 70.391 | 75.6799 | 80.1495 | 84.5515 | 90.2459 | 96.739 | 102.1127
MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Winter
Price band | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037
$300 - $500 | 1.2201 | 2.4973 | 3.883 | 5.1948 | 6.4998 | 7.8362 | 9.101 | 10.4031 | 11.7923 | 13.163 | 14.4541 | 15.6651 | 16.8378 | 18.1251 | 19.5999 | 20.8973 | 22.2441 | 23.6157 | 24.7861 | 26.1414
$500 - $1,000 | 0.86 | 1.7603 | 2.737 | 3.6616 | 4.5815 | 5.5235 | 6.4149 | 7.3327 | 8.3119 | 9.2781 | 10.1882 | 11.0417 | 11.8683 | 12.7757 | 13.8152 | 14.7297 | 15.6791 | 16.6458 | 17.4708 | 18.4261
$1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$7,500 - MPC | 4.35 | 8.9036 | 13.844 | 18.521 | 23.1737 | 27.9385 | 32.4477 | 37.0901 | 42.0429 | 46.9298 | 51.5332 | 55.8507 | 60.0317 | 64.6213 | 69.8795 | 74.505 | 79.3069 | 84.197 | 88.3698 | 93.2019
MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tasmania
Summer
Price band | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
$300 - $500 | 5.55 | 5.8719 | 6.1368 | 6.4151 | 6.4474 | 6.7338 | 6.9858 | 7.2793 | 7.6076 | 7.9156 | 8.2754 | 8.6004 | 8.8678 | 9.1692 | 9.4339 | 9.6614 | 10.0128 | 10.3676 | 10.7166 | 10.9872
$500 - $1,000 | 13.2 | 13.9656 | 14.5957 | 15.2575 | 15.3343 | 16.0155 | 16.6148 | 17.313 | 18.0936 | 18.8264 | 19.682 | 20.455 | 21.091 | 21.8078 | 22.4374 | 22.9784 | 23.8143 | 24.6581 | 25.488 | 26.1318
$1,000 - $7,500 | 0.5 | 0.529 | 0.55287 | 0.57793 | 0.58084 | 0.60665 | 0.62935 | 0.65579 | 0.68537 | 0.71312 | 0.74553 | 0.77481 | 0.7989 | 0.82605 | 0.8499 | 0.8704 | 0.90206 | 0.93402 | 0.96546 | 0.98984
$7,500 - MPC | 2.29 | 2.4228 | 2.5321 | 2.6469 | 2.6603 | 2.7784 | 2.8824 | 3.0035 | 3.139 | 3.2661 | 3.4145 | 3.5486 | 3.659 | 3.7833 | 3.8925 | 3.9864 | 4.1314 | 4.2778 | 4.4218 | 4.5335
MPC | 1.667 | 1.7636 | 1.8432 | 1.9268 | 1.9365 | 2.0225 | 2.0982 | 2.1864 | 2.2849 | 2.3775 | 2.4855 | 2.5832 | 2.6635 | 2.754 | 2.8335 | 2.9018 | 3.0074 | 3.1139 | 3.2187 | 3.3
Winter
Price band | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037
$300 - $500 | 5.55 | 5.9812 | 6.3293 | 6.709 | 6.8833 | 7.2426 | 7.6369 | 8.0365 | 8.4674 | 8.9292 | 9.342 | 9.7796 | 10.197 | 10.5463 | 10.9239 | 11.289 | 11.7284 | 12.1782 | 12.6026 | 13.0134
$500 - $1,000 | 13.2 | 14.2257 | 15.0534 | 15.9566 | 16.371 | 17.2256 | 18.1634 | 19.1138 | 20.1387 | 21.2369 | 22.2189 | 23.2595 | 24.2522 | 25.0831 | 25.9812 | 26.8495 | 27.8945 | 28.9643 | 29.9737 | 30.9507
$1,000 - $7,500 | 0.5 | 0.53885 | 0.5702 | 0.60442 | 0.62011 | 0.65249 | 0.68801 | 0.72401 | 0.76283 | 0.80443 | 0.84162 | 0.88104 | 0.91864 | 0.95012 | 0.98414 | 1.017 | 1.0566 | 1.0971 | 1.1354 | 1.1724
$7,500 - MPC | 2.29 | 2.4679 | 2.6115 | 2.7682 | 2.8401 | 2.9884 | 3.1511 | 3.316 | 3.4938 | 3.6843 | 3.8546 | 4.0352 | 4.2074 | 4.3515 | 4.5073 | 4.658 | 4.8393 | 5.0249 | 5.2 | 5.3695
MPC | 1.667 | 1.7965 | 1.901 | 2.0151 | 2.0674 | 2.1753 | 2.2937 | 2.4138 | 2.5432 | 2.6819 | 2.8059 | 2.9373 | 3.0627 | 3.1676 | 3.281 | 3.3907 | 3.5226 | 3.6577 | 3.7852 | 3.9086
Weak
Queensland
Summer
Price band | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
$300 - $500 | 32.46 | 32.6254 | 32.2053 | 33.0832 | 33.0322 | 33.1417 | 33.5322 | 33.0302 | 33.5945 | 34.6407 | 35.0112 | 34.8193 | 34.7606 | 34.3475 | 34.2557 | 34.9482 | 35.1158 | 35.3714 | 35.451 | 34.4576
$500 - $1,000 | 0.36 | 0.36183 | 0.35718 | 0.36691 | 0.36635 | 0.36756 | 0.37189 | 0.36632 | 0.37258 | 0.38419 | 0.38829 | 0.38617 | 0.38552 | 0.38093 | 0.37992 | 0.3876 | 0.38945 | 0.39229 | 0.39317 | 0.38215
$1,000 - $7,500 | 1.09 | 1.0956 | 1.0814 | 1.1109 | 1.1092 | 1.1129 | 1.126 | 1.1091 | 1.1281 | 1.1632 | 1.1757 | 1.1692 | 1.1673 | 1.1534 | 1.1503 | 1.1736 | 1.1792 | 1.1878 | 1.1904 | 1.1571
$7,500 - MPC | 6.39 | 6.4226 | 6.3399 | 6.5127 | 6.5026 | 6.5242 | 6.6011 | 6.5022 | 6.6133 | 6.8193 | 6.8922 | 6.8544 | 6.8429 | 6.7616 | 6.7435 | 6.8798 | 6.9128 | 6.9631 | 6.9788 | 6.7832
MPC | 176.07 | 176.9672 | 174.6884 | 179.4501 | 179.1739 | 179.7678 | 181.8861 | 179.1627 | 182.2237 | 187.8988 | 189.9082 | 188.8674 | 188.549 | 186.308 | 185.8103 | 189.5667 | 190.4758 | 191.862 | 192.2936 | 186.9056
Winter
Price band | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037
$300 - $500 | 32.46 | 32.8114 | 32.9898 | 33.4978 | 33.93 | 34.1711 | 34.2412 | 34.54 | 35.6044 | 36.0336 | 36.2186 | 36.1085 | 36.4755 | 36.8712 | 37.2451 | 37.437 | 37.4246 | 37.3218 | 38.062 | 37.8934
$500 - $1,000 | 0.36 | 0.3639 | 0.36588 | 0.37151 | 0.3763 | 0.37898 | 0.37975 | 0.38307 | 0.39487 | 0.39963 | 0.40168 | 0.40046 | 0.40453 | 0.40892 | 0.41307 | 0.4152 | 0.41506 | 0.41392 | 0.42213 | 0.42026
$1,000 - $7,500 | 1.09 | 1.1018 | 1.1078 | 1.1248 | 1.1394 | 1.1475 | 1.1498 | 1.1598 | 1.1956 | 1.21 | 1.2162 | 1.2125 | 1.2248 | 1.2381 | 1.2507 | 1.2571 | 1.2567 | 1.2533 | 1.2781 | 1.2725
$7,500 - MPC | 6.39 | 6.4592 | 6.4943 | 6.5943 | 6.6794 | 6.7268 | 6.7406 | 6.7995 | 7.009 | 7.0935 | 7.1299 | 7.1082 | 7.1805 | 7.2584 | 7.332 | 7.3698 | 7.3673 | 7.3471 | 7.4928 | 7.4596
MPC | 156.07 | 157.7596 | 158.6175 | 161.0598 | 163.1376 | 164.2971 | 164.6341 | 166.0709 | 171.1885 | 173.2523 | 174.1414 | 173.6124 | 175.3766 | 177.2794 | 179.0773 | 179.9997 | 179.9403 | 179.4459 | 183.0047 | 182.1944
New South Wales
Summer
Price band | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
$300 - $500 | 77.73 | 77.6823 | 77.6913 | 78.3968 | 78.4007 | 78.568 | 78.5777 | 79.8719 | 81.2272 | 82.4161 | 82.0305 | 81.8411 | 83.147 | 82.7215 | 82.8984 | 83.5999 | 83.7869 | 84.1972 | 86.2372 | 85.7714
$500 - $1,000 | 0.27 | 0.26983 | 0.26987 | 0.27232 | 0.27233 | 0.27291 | 0.27294 | 0.27744 | 0.28215 | 0.28628 | 0.28494 | 0.28428 | 0.28882 | 0.28734 | 0.28795 | 0.29039 | 0.29104 | 0.29246 | 0.29955 | 0.29793
$1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$7,500 - MPC | 27.01 | 26.9934 | 26.9966 | 27.2417 | 27.2431 | 27.3012 | 27.3046 | 27.7543 | 28.2252 | 28.6384 | 28.5043 | 28.4386 | 28.8923 | 28.7445 | 28.8059 | 29.0497 | 29.1147 | 29.2572 | 29.9661 | 29.8043
MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Winter
Price band | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037
$300 - $500 | 77.73 | 77.2433 | 78.405 | 79.0881 | 79.7768 | 80.7923 | 80.8109 | 82.4225 | 84.0113 | 85.1329 | 86.2064 | 86.0342 | 86.6982 | 88.1715 | 88.8118 | 90.1206 | 91.7168 | 91.647 | 93.8397 | 93.9344
$500 - $1,000 | 0.27 | 0.26831 | 0.27234 | 0.27472 | 0.27711 | 0.28064 | 0.2807 | 0.2863 | 0.29182 | 0.29571 | 0.29944 | 0.29885 | 0.30115 | 0.30627 | 0.30849 | 0.31304 | 0.31858 | 0.31834 | 0.32596 | 0.32629
$1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$7,500 - MPC | 27.01 | 26.8409 | 27.2445 | 27.4819 | 27.7212 | 28.0741 | 28.0806 | 28.6406 | 29.1927 | 29.5824 | 29.9554 | 29.8956 | 30.1263 | 30.6383 | 30.8608 | 31.3155 | 31.8702 | 31.8459 | 32.6079 | 32.6408
MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Victoria
Summer
Price band | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
$300 - $500 | 28.3775 | 28.2944 | 27.9064 | 28.3152 | 27.609 | 26.8461 | 27.2408 | 27.2198 | 27.3301 | 27.5852 | 27.6233 | 27.8881 | 27.7667 | 28.0869 | 28.3199 | 28.128 | 27.8409 | 28.4521 | 28.9027 | 28.6505
$500 - $1,000 | 3.04 | 3.0311 | 2.9895 | 3.0333 | 2.9577 | 2.8759 | 2.9182 | 2.916 | 2.9278 | 2.9551 | 2.9592 | 2.9876 | 2.9746 | 3.0089 | 3.0338 | 3.0133 | 2.9825 | 3.048 | 3.0963 | 3.0692
$1,000 - $7,500 | 1.6 | 1.5953 | 1.5734 | 1.5965 | 1.5567 | 1.5137 | 1.5359 | 1.5347 | 1.5409 | 1.5553 | 1.5575 | 1.5724 | 1.5656 | 1.5836 | 1.5968 | 1.5859 | 1.5697 | 1.6042 | 1.6296 | 1.6154
$7,500 - MPC | 0.66 | 0.65807 | 0.64904 | 0.65855 | 0.64213 | 0.62438 | 0.63356 | 0.63307 | 0.63564 | 0.64157 | 0.64246 | 0.64862 | 0.64579 | 0.65324 | 0.65866 | 0.6542 | 0.64752 | 0.66174 | 0.67222 | 0.66635
MPC | 43.5 | 43.3727 | 42.7779 | 43.4045 | 42.322 | 41.1525 | 41.7576 | 41.7254 | 41.8945 | 42.2855 | 42.344 | 42.7498 | 42.5637 | 43.0546 | 43.4117 | 43.1176 | 42.6775 | 43.6144 | 44.3051 | 43.9185
Winter
Price band | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037
$300 - $500 | 28.3775 | 28.5491 | 28.7314 | 28.8428 | 28.5782 | 28.5394 | 28.4173 | 28.2126 | 28.8496 | 29.0621 | 29.4677 | 29.575 | 29.5023 | 30.1406 | 30.4026 | 30.4779 | 30.788 | 31.0508 | 31.4567 | 31.8964
$500 - $1,000 | 3.04 | 3.0584 | 3.0779 | 3.0898 | 3.0615 | 3.0573 | 3.0443 | 3.0223 | 3.0906 | 3.1133 | 3.1568 | 3.1683 | 3.1605 | 3.2289 | 3.257 | 3.265 | 3.2982 | 3.3264 | 3.3699 | 3.417
$1,000 - $7,500 | 1.6 | 1.6097 | 1.62 | 1.6262 | 1.6113 | 1.6091 | 1.6022 | 1.5907 | 1.6266 | 1.6386 | 1.6615 | 1.6675 | 1.6634 | 1.6994 | 1.7142 | 1.7184 | 1.7359 | 1.7507 | 1.7736 | 1.7984
$7,500 - MPC | 0.66 | 0.66399 | 0.66823 | 0.67082 | 0.66467 | 0.66377 | 0.66093 | 0.65617 | 0.67098 | 0.67592 | 0.68536 | 0.68785 | 0.68616 | 0.70101 | 0.7071 | 0.70885 | 0.71606 | 0.72217 | 0.73162 | 0.74184
MPC | 6.5 | 6.5393 | 6.5811 | 6.6066 | 6.546 | 6.5371 | 6.5091 | 6.4622 | 6.6081 | 6.6568 | 6.7497 | 6.7743 | 6.7576 | 6.9039 | 6.9639 | 6.9811 | 7.0521 | 7.1123 | 7.2053 | 7.306
South Australia
Summer
Price band | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
$300 - $500 | 1.2201 | 1.229 | 1.2437 | 1.2231 | 1.2138 | 1.2218 | 1.2065 | 1.2278 | 1.2329 | 1.219 | 1.2175 | 1.2111 | 1.2258 | 1.2357 | 1.2341 | 1.2267 | 1.2202 | 1.2196 | 1.2328 | 1.2448
$500 - $1,000 | 0.86 | 0.86628 | 0.87665 | 0.86212 | 0.85559 | 0.86118 | 0.85045 | 0.86545 | 0.86901 | 0.85921 | 0.8582 | 0.85368 | 0.864 | 0.87101 | 0.8699 | 0.86464 | 0.86009 | 0.85964 | 0.86892 | 0.87743
$1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$7,500 - MPC | 4.35 | 4.3817 | 4.4342 | 4.3607 | 4.3277 | 4.356 | 4.3017 | 4.3776 | 4.3956 | 4.346 | 4.3409 | 4.318 | 4.3702 | 4.4057 | 4.4001 | 4.3735 | 4.3504 | 4.3482 | 4.3951 | 4.4382
MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Winter
Price band | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037
$300 - $500 | 1.2201 | 1.2103 | 1.2375 | 1.2328 | 1.243 | 1.256 | 1.2556 | 1.2635 | 1.278 | 1.2881 | 1.2988 | 1.2973 | 1.2989 | 1.3166 | 1.3289 | 1.3343 | 1.3449 | 1.3548 | 1.3591 | 1.3694
$500 - $1,000 | 0.86 | 0.85311 | 0.87226 | 0.86895 | 0.87614 | 0.88531 | 0.88505 | 0.89061 | 0.90079 | 0.90796 | 0.91546 | 0.91445 | 0.91555 | 0.92806 | 0.9367 | 0.94049 | 0.94795 | 0.95496 | 0.958 | 0.96526
$1,000 - $7,500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$7,500 - MPC | 4.35 | 4.3151 | 4.412 | 4.3953 | 4.4317 | 4.478 | 4.4767 | 4.5048 | 4.5563 | 4.5926 | 4.6305 | 4.6254 | 4.631 | 4.6942 | 4.738 | 4.7571 | 4.7949 | 4.8303 | 4.8457 | 4.8824
MPC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tasmania
Summer
Price band | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
$300 - $500 | 5.55 | 5.5982 | 5.5931 | 5.6309 | 5.4322 | 5.431 | 5.4591 | 5.4813 | 5.5189 | 5.5443 | 5.6163 | 5.6581 | 5.7062 | 5.699 | 5.6775 | 5.6812 | 5.7281 | 5.792 | 5.7973 | 5.8427
$500 - $1,000 | 13.2 | 13.3146 | 13.3024 | 13.3924 | 12.9199 | 12.917 | 12.9837 | 13.0367 | 13.126 | 13.1864 | 13.3577 | 13.457 | 13.5715 | 13.5544 | 13.5034 | 13.512 | 13.6236 | 13.7756 | 13.7881 | 13.8962
$1,000 - $7,500 | 0.5 | 0.50434 | 0.50388 | 0.50729 | 0.48939 | 0.48928 | 0.49181 | 0.49381 | 0.4972 | 0.49949 | 0.50597 | 0.50973 | 0.51407 | 0.51343 | 0.51149 | 0.51182 | 0.51604 | 0.5218 | 0.52228 | 0.52637
$7,500 - MPC | 2.29 | 2.3099 | 2.3078 | 2.3234 | 2.2414 | 2.2409 | 2.2525 | 2.2617 | 2.2772 | 2.2876 | 2.3174 | 2.3346 | 2.3545 | 2.3515 | 2.3426 | 2.3441 | 2.3635 | 2.3899 | 2.392 | 2.4108
MPC | 1.667 | 1.6814 | 1.6799 | 1.6913 | 1.6316 | 1.6312 | 1.6396 | 1.6463 | 1.6576 | 1.6652 | 1.6869 | 1.6994 | 1.7139 | 1.7117 | 1.7053 | 1.7064 | 1.7204 | 1.7396 | 1.7412 | 1.7549
Winter
Price band | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037
$300 - $500 | 5.55 | 5.6148 | 5.6257 | 5.6642 | 5.513 | 5.5163 | 5.5574 | 5.5486 | 5.6025 | 5.6803 | 5.7243 | 5.7848 | 5.7911 | 5.8158 | 5.8311 | 5.8284 | 5.8424 | 5.8915 | 5.9339 | 5.9686
$500 - $1,000 | 13.2 | 13.3542 | 13.38 | 13.4715 | 13.1121 | 13.1198 | 13.2177 | 13.1967 | 13.3249 | 13.51 | 13.6145 | 13.7585 | 13.7734 | 13.8321 | 13.8685 | 13.8621 | 13.8955 | 14.0121 | 14.113 | 14.1956
$1,000 - $7,500 | 0.5 | 0.50584 | 0.50682 | 0.51029 | 0.49667 | 0.49696 | 0.50067 | 0.49988 | 0.50473 | 0.51174 | 0.5157 | 0.52116 | 0.52172 | 0.52394 | 0.52532 | 0.52508 | 0.52635 | 0.53076 | 0.53458 | 0.53771
$7,500 - MPC | 2.29 | 2.3168 | 2.3212 | 2.3371 | 2.2748 | 2.2761 | 2.2931 | 2.2894 | 2.3117 | 2.3438 | 2.3619 | 2.3869 | 2.3895 | 2.3997 | 2.406 | 2.4049 | 2.4107 | 2.4309 | 2.4484 | 2.4627
MPC | 1.667 | 1.6864 | 1.6897 | 1.7012 | 1.6559 | 1.6568 | 1.6692 | 1.6665 | 1.6827 | 1.7061 | 1.7193 | 1.7375 | 1.7394 | 1.7468 | 1.7514 | 1.7506 | 1.7548 | 1.7695 | 1.7822 | 1.7927

## Battery aggregation
Go to Assumptions Summary
Battery aggregation
Embedded residential battery installations by NEM region. The use of batteries in managing consumer demand is 'netted' off the operational demand forecasts if 'non-aggregated', whereas the 'aggregated' share is modelled like a Virtual Power Plant, operated by a retailer / aggregator and an alternative supply source for arbitrage or emergency response.
Neutral capacity growth (all small-scale batteries, MW)
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 96.2979 | 152.7898 | 173.0813 | 188.9008 | 217.2696 | 265.1952 | 317.3725 | 343.036 | 358.9115 | 386.9227 | 418.1938 | 465.3264 | 503.45 | 561.1893 | 631.5003 | 711.6297 | 796.6618 | 866.2593 | 939.0398 | 1015.4004
Qld | 39.8202 | 59.7635 | 66.5311 | 71.5953 | 80.4655 | 98.6703 | 120.0067 | 131.541 | 141.7573 | 158.9075 | 178.0448 | 202.4895 | 224.2554 | 256.4465 | 295.2006 | 338.2785 | 386.9851 | 429.0319 | 474.5246 | 523.9231
SA | 37.102 | 85.8749 | 169.4655 | 170.5155 | 171.6794 | 173.0193 | 174.4005 | 175.6073 | 177.1424 | 179.3404 | 181.4392 | 183.4549 | 185.585 | 188.2483 | 195.4507 | 210.173 | 231.8751 | 250.9678 | 271.1765 | 292.5995
Tas | 8.1365 | 12.2562 | 13.424 | 14.3075 | 15.923 | 18.6469 | 21.7395 | 23.7024 | 25.5847 | 29.012 | 32.8115 | 37.219 | 41.0157 | 46.0031 | 51.2917 | 56.7432 | 62.5535 | 67.2841 | 72.3243 | 77.7213
Vic | 44.5068 | 73.8458 | 82.9582 | 90.2506 | 103.3587 | 125.7678 | 155.0154 | 172.1933 | 185.7182 | 214.0396 | 244.1701 | 279.821 | 313.7244 | 359.8776 | 411.7624 | 469.0673 | 532.1048 | 585.1408 | 642.0117 | 703.2382
Fast capacity growth (all small-scale batteries, MW)
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 47.3991 | 79.1544 | 121.3374 | 167.7588 | 230.4651 | 306.2132 | 398.3386 | 504.8265 | 627.7756 | 765.0044 | 915.4665 | 1079.4152 | 1258.7397 | 1462.998 | 1697.1756 | 1965.6771 | 2276.1157 | 2636.5453 | 3036.817 | 3468.6874
Qld | 47.3056 | 75.4576 | 115.214 | 163.6495 | 223.0687 | 292.902 | 375.0192 | 467.526 | 569.8549 | 684.2927 | 808.8914 | 946.4078 | 1108.1498 | 1298.7704 | 1532.7767 | 1815.0791 | 2145.6653 | 2512.8671 | 2872.0233 | 3191.0258
SA | 29.3453 | 49.5456 | 75.7799 | 107.6032 | 145.2399 | 187.0912 | 232.0715 | 282.1929 | 336.7334 | 398.007 | 468.5544 | 547.9523 | 629.4095 | 704.2329 | 772.2185 | 835.381 | 894.784 | 951.2647 | 1004.9796 | 1055.8335
Tas | 2.6025 | 4.2463 | 6.5075 | 9.4378 | 13.1771 | 17.8563 | 23.601 | 31.2604 | 40.2812 | 50.6909 | 62.6975 | 76.0416 | 90.6383 | 106.3983 | 123.6859 | 142.2183 | 162.1509 | 184.1957 | 208.8757 | 236.144
Vic | 30.5885 | 51.2284 | 79.4063 | 116.746 | 169.3875 | 235.2992 | 318.4423 | 417.8303 | 536.1291 | 671.4232 | 822.782 | 990.3998 | 1180.4713 | 1396.8429 | 1652.3354 | 1971.8358 | 2370.1291 | 2856.4074 | 3413.8589 | 3999.0365
Aggregation trajectories
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
45% | 0% | 5.663% | 10.02% | 13.73% | 16.97% | 19.83% | 22.37% | 24.64% | 26.68% | 28.51% | 30.17% | 31.66% | 33.02% | 34.24% | 35.36% | 36.37% | 37.3% | 38.14% | 38.91% | 39.61%
90% | 0% | 11.33% | 20.04% | 27.46% | 33.94% | 39.66% | 44.74% | 49.28% | 53.36% | 57.02% | 60.33% | 63.32% | 66.03% | 68.49% | 70.72% | 72.75% | 74.6% | 76.28% | 77.82% | 79.22%
10% | 0% | 1.259% | 2.226% | 3.052% | 3.771% | 4.406% | 4.971% | 5.476% | 5.928% | 6.336% | 6.704% | 7.036% | 7.337% | 7.61% | 7.858% | 8.083% | 8.289% | 8.476% | 8.646% | 8.802%
Neutral capacity growth, 45% aggregation by 2050 (MW)
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 0 | 8.6529 | 17.3412 | 25.9398 | 36.8717 | 52.5844 | 70.995 | 84.5261 | 95.7505 | 110.3178 | 126.1515 | 147.3284 | 166.2177 | 192.1753 | 223.2997 | 258.8552 | 297.1456 | 330.3975 | 365.3671 | 402.1952
Qld | 0 | 3.3846 | 6.6658 | 9.8315 | 13.6554 | 19.5649 | 26.845 | 32.4125 | 37.8181 | 45.3071 | 53.7086 | 64.1108 | 74.0396 | 87.8183 | 104.3835 | 123.0488 | 144.3409 | 163.6359 | 184.6308 | 207.5234
SA | 0 | 4.8634 | 16.979 | 23.4152 | 29.1348 | 34.3072 | 39.0127 | 43.2706 | 47.2581 | 51.1328 | 54.7326 | 58.0842 | 61.2722 | 64.4643 | 69.1118 | 76.4504 | 86.4867 | 95.7209 | 105.5109 | 115.8972
Tas | 0 | 0.6941 | 1.345 | 1.9647 | 2.7022 | 3.6974 | 4.863 | 5.8404 | 6.8255 | 8.2718 | 9.8978 | 11.784 | 13.5416 | 15.7534 | 18.1368 | 20.6403 | 23.3317 | 25.6626 | 28.1404 | 30.785
Vic | 0 | 4.1821 | 8.3117 | 12.3932 | 17.5404 | 24.9379 | 34.6764 | 42.4294 | 49.546 | 61.0261 | 73.6559 | 88.595 | 103.5784 | 123.2375 | 145.6 | 170.6232 | 198.4689 | 223.1769 | 249.7977 | 278.5493
Neutral capacity growth, 90% aggregation by 2050 (MW)
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 0 | 17.3059 | 34.6825 | 51.8797 | 73.7433 | 105.1687 | 141.9901 | 169.0521 | 191.5011 | 220.6357 | 252.3031 | 294.6568 | 332.4354 | 384.3506 | 446.5994 | 517.7104 | 594.2912 | 660.795 | 730.7342 | 804.3905
Qld | 0 | 6.7692 | 13.3317 | 19.6629 | 27.3107 | 39.1298 | 53.6901 | 64.8249 | 75.6361 | 90.6141 | 107.4173 | 128.2216 | 148.0791 | 175.6366 | 208.767 | 246.0976 | 288.6819 | 327.2717 | 369.2616 | 415.0468
SA | 0 | 9.7267 | 33.9579 | 46.8303 | 58.2696 | 68.6145 | 78.0255 | 86.5413 | 94.5162 | 102.2657 | 109.4652 | 116.1684 | 122.5445 | 128.9286 | 138.2235 | 152.9008 | 172.9735 | 191.4419 | 211.0219 | 231.7945
Tas | 0 | 1.3882 | 2.6899 | 3.9294 | 5.4044 | 7.3948 | 9.7261 | 11.6808 | 13.651 | 16.5436 | 19.7957 | 23.5681 | 27.0833 | 31.5068 | 36.2737 | 41.2806 | 46.6634 | 51.3253 | 56.2807 | 61.5701
Vic | 0 | 8.3642 | 16.6234 | 24.7864 | 35.0809 | 49.8759 | 69.3528 | 84.8589 | 99.0919 | 122.0522 | 147.3117 | 177.1899 | 207.1568 | 246.475 | 291.2 | 341.2463 | 396.9378 | 446.3538 | 499.5953 | 557.0986
Neutral capacity growth, 10% aggregation by 2050 (MW)
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 0 | 1.9229 | 3.8536 | 5.7644 | 8.1937 | 11.6854 | 15.7767 | 18.7836 | 21.2779 | 24.5151 | 28.0337 | 32.7396 | 36.9373 | 42.7056 | 49.6222 | 57.5234 | 66.0324 | 73.4217 | 81.1927 | 89.3767
Qld | 0 | 0.75213 | 1.4813 | 2.1848 | 3.0345 | 4.3478 | 5.9656 | 7.2028 | 8.404 | 10.0682 | 11.9353 | 14.2468 | 16.4532 | 19.5152 | 23.1963 | 27.3442 | 32.0758 | 36.3635 | 41.0291 | 46.1163
SA | 0 | 1.0807 | 3.7731 | 5.2034 | 6.4744 | 7.6238 | 8.6695 | 9.6157 | 10.5018 | 11.3629 | 12.1628 | 12.9076 | 13.6161 | 14.3254 | 15.3582 | 16.989 | 19.2193 | 21.2713 | 23.4469 | 25.7549
Tas | 0 | 0.15425 | 0.29888 | 0.4366 | 0.60049 | 0.82165 | 1.0807 | 1.2979 | 1.5168 | 1.8382 | 2.1995 | 2.6187 | 3.0093 | 3.5008 | 4.0304 | 4.5867 | 5.1848 | 5.7028 | 6.2534 | 6.8411
Vic | 0 | 0.92936 | 1.847 | 2.754 | 3.8979 | 5.5418 | 7.7059 | 9.4288 | 11.0102 | 13.5614 | 16.368 | 19.6878 | 23.0174 | 27.3861 | 32.3556 | 37.9163 | 44.1042 | 49.5949 | 55.5106 | 61.8998
Strong capacity growth, 90% aggregation by 2050 (MW)
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38
NSW | 0 | 8.9655 | 24.3139 | 46.0732 | 78.222 | 121.4353 | 178.2137 | 248.7844 | 334.9564 | 436.23 | 552.3156 | 683.5138 | 831.1642 | 1001.9866 | 1200.249 | 1430.0296 | 1697.9294 | 2011.1945 | 2363.165 | 2747.8609
Qld | 0 | 8.5468 | 23.0869 | 44.9447 | 75.7116 | 116.1565 | 167.7808 | 230.4022 | 304.0521 | 390.2056 | 488.0172 | 599.2901 | 731.7275 | 889.5094 | 1083.9856 | 1320.4695 | 1600.6164 | 1916.8511 | 2234.9272 | 2527.9001
SA | 0 | 5.6118 | 15.185 | 29.5521 | 49.2958 | 74.1949 | 103.8271 | 139.0679 | 179.6677 | 226.9563 | 282.6864 | 346.9777 | 415.6083 | 482.3191 | 546.1159 | 607.7394 | 667.4881 | 725.6383 | 782.0467 | 836.4212
Tas | 0 | 0.48096 | 1.304 | 2.592 | 4.4724 | 7.0813 | 10.5589 | 15.4055 | 21.4925 | 28.9056 | 37.8264 | 48.1515 | 59.8498 | 72.8707 | 87.4712 | 103.4638 | 120.9608 | 140.5072 | 162.5411 | 187.071
Vic | 0 | 5.8024 | 15.9116 | 32.0631 | 57.4917 | 93.3129 | 142.4687 | 205.9116 | 286.0574 | 382.867 | 496.3976 | 627.1469 | 779.4824 | 956.6779 | 1168.5379 | 1434.51 | 1768.0612 | 2178.9085 | 2656.5683 | 3167.9984
Average non-aggregated Summer battery daily charge/discharge profile (14 kWh Battery, max discharge 5.4 kW)
NEM Time | 00:30 | 01:00 | 01:30 | 02:00 | 02:30 | 03:00 | 03:30 | 04:00 | 04:30 | 05:00 | 05:30 | 06:00 | 06:30 | 07:00 | 07:30 | 08:00 | 08:30 | 09:00 | 09:30 | 10:00 | 12:00 | 12:30 | 13:00 | 13:30 | 14:00 | 14:30 | 15:00 | 15:30 | 16:00 | 16:30 | 17:00 | 17:30 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 20:30 | 21:00 | 21:30 | 22:00 | 22:30 | 23:00 | 23:30 | 00:00
Battery | -0.72253 | -1.2601 | -1.2951 | -1.2933 | -1.3421 | -1.3154 | -1.3673 | -1.3041 | -0.96312 | -0.52515 | -0.35719 | -0.35985 | -0.39504 | -0.50008 | -0.50786 | -0.48198 | -0.12184 | 0.27931 | 0.99578 | 1.1822 | 2.6689 | 2.7741 | 1.9293 | 1.2166 | 1.01 | 0.62736 | 0.37605 | 0.22388 | 0.12443 | 0.052688 | 0.044391 | 0.041559 | 0.035788 | -0.010284 | -0.15043 | -0.050756 | -0.51942 | -0.91791 | -1.0495 | -0.73075 | -0.63169 | -0.67188 | -0.56989 | -0.53785 | -0.64234
Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0087399 | 0.19064 | 0.41691 | 0.6889 | 1.0166 | 2.2148 | 2.4181 | 2.5861 | 2.6758 | 2.7607 | 2.7404 | 2.7273 | 2.6177 | 2.499 | 2.2789 | 2.0497 | 1.7853 | 1.4943 | 1.1862 | 0.86667 | 0.53501 | 0.26575 | 0.096118 | 0.002774 | 0.00030341 | 0 | 0 | 0 | 0 | 0
Average non-aggregated battery daily summer charge/discharge profile | 2027-28: Percentage aggregation trajectory
Average weekday Summer profile, but actual charge / discharge profile will depend on the actual availability of solar resources to charge the battery system.
(14 kWh Battery, max discharge 5.4 kW)
Note that the charge / discharge profile of batteries, and the daily production profile from solar is indicative only, for an average summer day. The actual PV generation profile for example depends on the daily conditions experienced, with solar irradiance measurements influencing the solar generation profile.

## Renewable Policy Targets
Go to Assumptions Summary
Federal Large-scale Renewable Energy Target
Financial year | Australia-wide LRET Target (GWh) | Base NEM Target (including grandfathered hydro) (GWh) | GreenPower (GWh) | Desalination (GWh) | Effective Target (GWh) | Penalty Price ($/MWh)1
2018-19 | 29940.5 | 39366.4 | 558.4 | 103.1 | 40027.9 | 90.5923
2019-20 | 32547 | 41537.6 | 469.8 | 101.9 | 42109.3 | 88.3828
2020-21 | 33425 | 42269 | 395.2 | 101.2 | 42765.4 | 86.2271
2021-22 | 33000 | 41915 | 332.4 | 101.2 | 42348.6 | 84.124
2022-23 | 33000 | 41915 | 279.7 | 101.2 | 42295.9 | 82.0722
2023-24 | 33000 | 41915 | 235.3 | 101.4 | 42251.7 | 80.0704
2024-25 | 33000 | 41915 | 197.9 | 101.2 | 42214.1 | 78.1175
2025-26 | 33000 | 41915 | 166.5 | 101.2 | 42182.7 | 76.2122
2026-27 | 33000 | 41915 | 140.1 | 101.2 | 42156.3 | 74.3533
2027-28 | 33000 | 41915 | 117.8 | 101.4 | 42134.2 | 72.5399
2028-29 | 33000 | 41915 | 99.1 | 101.2 | 42115.3 | 70.7706
2029-30 | 33000 | 41915 | 83.4 | 101.2 | 42099.6 | 69.0445
1. Penalty price is calculated as an uplift of the $65 nominal penalty adjusted by a 30% corporate tax rate and a 2.5% annual CPI adjustment
Queensland Renewable Energy Target
50% of Queensland consumption to be provided by renewable generation by 2030 target
Financial year | Queensland large-scale renewable generation (GWh)
2020-21 | 0
2021-22 | 300
2022-23 | 3000
2023-24 | 5700
2024-25 | 8400
2025-26 | 11100
2026-27 | 13700
2027-28 | 16500
2028-29 | 19300
2029-30 | 22200
Trajectory of total large scale generation of renewable energy required, including Q400 auction eligible, as calculated by the QLD Government Expert Panel report: https://www.dnrm.qld.gov.au/__data/assets/pdf_file/0018/1259010/qreep-renewable-energy-target-report.pdf
Victorian Renewable Energy Target
New entry renewable capacity required to meet the 25% target by 2020 and 50% target by 2030
Targets adjusted based on existing generation, committed capacity and successful projects of the VRET 2018
Financial year | Victorian new entry renewable capacity, in addition to existing commitments (MW)
| Solar | Wind | Total
2019-20 | 0 | 0 | 0
2029-30 | 900 | 2500 | 3400
Given committed capacity to be installed in Victoria following the recent reverse auction allocations, AEMO proposes to implement the 2030 50% target as installations between 2020 and 2030.
As the 50% target is a generation target, the build capacities above are subject to change depending on modelled outcomes.

## Interconnector Capability
Go to Assumptions Summary
Interconnector Transfer Capability (MW)
Worst-case transfer limits at times of peak demand in the receiving region. Used in capacity expansion modelling†
Interconnector | Forward Direction | Forward capability | Reverse Capability
QNI | NSW to QLD | 410‡ | 1125‡
Terranora | NSW to QLD | 50 | 150
VIC-NSW | VIC to NSW | 700 | 400
Heywood | VIC to SA | 650 | 650
Murraylink* | VIC to SA | 220 | 200
Basslink | TAS to VIC | 478 | 478
† Time-sequential modelling uses higher thermal limits combined with constraint equations to better capture network conditions impacting flow capability. In real time operation transfer capability is determined by constraint equations.
‡ For the purpose of describing limits on the NSW-QLD interconnector, NSW generation connected to the 330 kV network north of Armidale (e.g. Sapphire Wind Farm) is assumed to belong to the Queensland region.
* Forward capability is limited by thermal limitations in the Victorian 220kV transmission network. Reverse capability is limited by thermal limitations in the South Australian 132kV transmission network.

## Proportioning factors
Go to Assumptions Summary
Proportioning Factors for Inter-Regional Losses
Losses due to interconnector flow are assigned asymmetrically to regions either side of the interconnector1
Notional Interconnector | Proportioning Factor | Region applied to
Queensland - New South Wales (QNI) | 0.68 | New South Wales
Queensland - New South Wales (Terranora) | 0.66 | New South Wales
Victoria - New South Wales (VNI) | 0.32 | Victoria
Victoria - South Australia (Heywood) | 0.78 | Victoria
Victoria - South Australia (Murraylink) | 0.67 | Victoria
Tasmania - Victoria (Basslink) | 0.5 | Victoria
Queensland - New South Wales (QNI augmentation options)2 | 0.68 | New South Wales
Victoria - New South Wales (VNI augmentation options)2 | 0.32 | Victoria
South Australia-New South Wales3 | 0.5 | New South Wales
1. For derivation of loss factors for existing interconnectors, see Regional Boundaries and Marginal Loss Factors for the 2018-19 Financial Year
2. The model applies the same proportioning factors to new interconnector developments as are calculated for the existing interconnectors between the same regions
3. Proposed connection between New South Wales and South Australia assumed a proportioning factor of 0.5

## Maximum capacity
Go to Assumptions Summary
Generator nameplate capacity
Existing generators |  | Committed Projects 1 |  |  | Advanced VRET Projects 1 |  |  | Existing and Committed Battery storage Projects
Generator | Installed capacity (MW) | Generator | Installed capacity (MW) | Commissioning date | Generator | Installed capacity (MW) | Indicative commissioning date2 | Storage | Maximum capacity (MW) | Energy (MWh) | Indicative commissioning date
Bayswater | 2640 | Barker Inlet | 210 | Aug 2019 | Carwarp Solar | 121.6 | 2020-01-01 | Kennedy Energy Park | 2 | 4 | 2019-04-01
Eraring | 2880 | Bodangora WF | 113.19 | 2018-11-01 | Cohuna Solar | 34.2 | 2019-08-01 | Lakeland | 1.4 | 5.3 | In service
Liddell | 2000 | Crookwell 2 WF | 91 | 2018-11-02 | Winton Solar | 98.8 | 2020-01-01 | Hornsdale | 100 | 129 | In service
Mount Piper | 1320 | Mt Emerald WF | 180.5 | Oct 2018 | Dundonnel WF | 336 | 2020-07-01 | ESCRI Dalrymple | 30 | 8 | In service
Vales Point | 1320 | Coopers Gap WF | 453 | Aug 2019 | Mortlake South WF | 157.5 | 2020-07-01 | Ballarat | 30 | 30 | In service
Callide B | 700 | Kennedy Energy Park WF | 43.2 | Apr 2019 | Berrybank WF | 331.8 | 2020-09-01 | Bulgana | 20 | 34 | 2019-08-01
Callide Power Plant | 900 | Crudine Ridge WF | 135 | 2019-11-01 |  |  |  | Gannawarra Energy Storage System | 25 | 50 | In service
Gladstone | 1680 | Crowlands WF | 79.95 | 2019-05-01 | 1. Successful projects for the Victorian Renewable Energy Auction Scheme (VREAS) as announced on Tuesday 11 September, 2018.
Kogan Creek | 744 | Lincoln Gap WF | 126 | Apr 2019
Millmerran | 852 | Willogoleche WF | 119.4 | 2019-03-01
Stanwell | 1460 | Cattle Hill WF | 144 | Dec 2019
Tarong | 1400 | Granville Harbour WF | 111.6 | 2019-11-01
Tarong North | 450 | Mt Gellibrand WF | 132 | 2018-05-01
Loy Yang A | 2210 | Murra Warra WF | 225.7 | 2019-05-01
Loy Yang B | 1000 | Bulgana WF | 194 | May 2019
Yallourn | 1450 | Cherry Tree WF | 58 | May 2020
Colongra | 724 | Lal Lal Elaine WF | 83.6 | Jul 2019
Smithfield1 | 170.9 | Lal Lal Yendon WF | 144.4 | Mar 2019
Tallawarra | 435 | Moorabool WF | 320 | Sep 2019
Uranquinty | 664 | Stockyard Hill WF | 532 | Dec 2019
Barcaldine | 37 | Bomen Solar | 120 | Feb 2020
Braemar | 504 | Daydream Solar | 167.5 | Early 2019
Braemar 2 | 519 | Darlington Point Solar | 275 | Nov 2019
Condamine | 144 | Finley Solar | 133 | Oct 2019
Darling Downs | 644.5 | Hayman Solar | 50 | Early 2019
Oakey | 282 | Brigalow Solar | 34.5 | Mar 2020
Roma | 80 | Childers Solar | 56 | Feb 2019
Swanbank E2 | 385 | Clermont Solar | 92.5 | Oct 2018
Yabulu | 242 | Collinsville Solar | 42.5 | Aug 2018
Yarwun | 180 | Haughton Solar | 100 | 2019-11-01
Somerton | 160 | Kennedy Energy Park Solar | 15 | Apr 2019
Bairnsdale | 94 | Lilyvale Solar | 100 | Oct 2018
Jeeralang A | 212 | Limondale 1 Solar | 220 | Apr 2020
Jeeralang B | 228 | Limondale 2 Solar | 29 | Apr 2019
Laverton North | 312 | Oakey Solar | 25 | Mar 2019
Mortlake | 566 | Oakey 2 Solar | 55 | Mar 2019
Newport | 510 | Rugby Run Solar | 65 | Mar 2019
Valley Power | 300 | Susan River Solar | 75 | Feb 2019
Hallett GT | 234.34 | Teebar Solar | 52.5 | Jul 2019
Dry Creek | 156 | Yarranlea Solar | 102.5 | Aug 2019
Ladbroke Grove | 80 | Warwick Solar | 64.2 | Feb 2020
Mintaro | 90 | Beryl Solar | 98.4 | 2019-05-01
Osborne | 180 | Nevertire Solar | 105 | Jul 2019
Pelican Point | 529 | Sunraysia Solar | 200 | Dec 2019
Quarantine | 224 | Bungala 2 Solar | 110 | Jan 2019
Torrens Island A | 480 | Bannerton Solar | 88 | Oct 2018
Torrens Island B | 800 | Kiamal Solar | 200 | 2019-05-01
Bell Bay Three | 120 | Karadoc Solar | 90 | 2018-11-01
Tamar Valley CCGT | 208 | Numurkah Solar | 100 | 2019-05-01
Tamar Valley OCGT | 58 | Tailem Bend Solar | 108 | 2019-05-01
Hunter Valley GT | 50 | Yatpool Solar | 81 | 2019-05-01
Mackay GT | 34 | Wemen Solar | 87.75 | Oct 2018
Mount Stuart | 423.5 | 1. Committed project list reflects Generation Information update from January 2019.
Angaston | 50
Lonsdale | 20.7
Port Lincoln | 73.5
Port Stanvac | 57.6
Snuggery | 63
Blowering | 80
Guthega | 60
Hume | 29
Shoalhaven | 240
Upper Tumut | 616
Tumut 3 | 1500
Barron Gorge | 66
Kareeya | 86.4
Wivenhoe | 570
Bogong / Mackay3 | 300
Dartmouth | 185
Eildon | 135
Murray 1 | 950
Murray 2 | 552
West Kiewa | 60
Bastyan | 79.9
Catagunya / Liapootah / Wayatinah4 | 170.1
Cethana | 85
Devils Gate | 60
Fisher | 43.2
Gordon | 432
John Butters | 144
Lake Echo | 32.4
Lemonthyme / Wilmot5 | 81.6
Mackintosh | 79.9
Meadowbank | 40
Poatina | 300
Reece | 231.2
Tarraleah | 90
Trevallyn | 93
Tribute | 82.8
Tungatinah | 125
Boco Rock WF | 113
Capital WF | 140.7
Cullerin Range WF | 30
Gullen Range WF | 165.5
Gunning WF | 46.5
Silverton WF | 199
Sapphire WF | 270
Taralga WF | 106.8
White Rock WF | 172.5
Woodlawn WF | 48.3
Canunda WF | 46
Cathedral Rocks WF | 66
Clements Gap WF | 56.7
Hallett 1 Brown Hill WF | 94.5
Hallett 2 Hallett Hill WF | 71.4
Hallett 3 North Brown Hill WF | 132.3
Hallett 4 The Bluff WF | 52.5
Hornsdale S1 WF | 102.4
Hornsdale S2 WF | 102.4
Hornsdale S3 WF | 112
Lake Bonney 1 WF | 80.5
Lake Bonney 2 WF | 159
Lake Bonney 3 WF | 39
Mount Millar WF | 70
Snowtown WF | 98.7
Snowtown S2 WF | 270
Starfish Hill WF | 34.5
Waterloo WF | 130.8
Wattle Point WF | 90.75
Musselroe WF | 168
Woolnorth WF | 140
Ararat WF | 240
Bald Hills WF | 106.6
Challicum Hills WF | 52.5
Kiata WF | 31.05
Macarthur WF | 420
Mortons Lane WF | 19.5
Mount Mercer WF | 131.2
Oaklands Hill WF | 67.2
Portland WF | 151.7
Salt Creek WF | 54
Waubra WF | 192
Yambuk WF | 30
Yaloak South WF | 28.7
Broken Hill Solar | 53
Coleambally Solar | 180
Griffith Solar | 29.99
Manildra Solar | 50
Moree Solar | 56
Nyngan Solar | 102
Parkes Solar | 50.5
Clare Solar | 100
Darling Downs Solar | 108.5
Hamilton Solar | 57.5
Hughenden Solar | 18
Kidston Solar | 50
Longreach Solar | 17
Ross River Solar | 128
Sun Metals Solar | 124
Gannawarra Solar | 55
Bungala one Solar | 110
Whitsunday Solar | 57.5
1. Smithfield operating as a fast start OCGT from late 2017
2. Swanbank E return to service in 2018
3. Bogong 140MW and Mackay 162MW
4. Catagunya 38MW, Liapootah 48 MW and Wayatinah 84 MW
5. Lemonthyme 31 MW and Wilmot 51 MW

## Reserves
Go to Assumptions Summary
Initial Regional Reserve
In capacity outlook models each region must have a minimum level of firm capacity available. Firm capacity is allowed to be shared across interconnected regions based on interconnector capabilities and available capacity in neighbouring regions. These reserve requirements are used in capacity outlook models to deliver sufficient capacity to meet reliability requirements, and the resulting capacity is validated through time-sequential modelling. The reserve requirements typically cover approximately the largest single generating unit.
To meet these reserve requirements, the Firm Capacities listed on the Firm Capacity sheet are applied, but are subject to change based on detailed analysis of reliability outcomes from time-sequential modelling.
Region | Regional Reserve Requirements (MW)
NSW | 673.2
QLD | 666.08
SA | 273
TAS | 194
VIC | 498
ISP 2018 values. Subject to change based on detailed analysis of reliability outcomes

## Firm capacity
Go to Assumptions Summary
Firm capacity (to meet reserve requirements)
Firm capacity is power assumed to be available at times of peak demand for the purpose of meeting reserve requirements in Capacity Outlook models. Firm capacities for existing and committed generators are given only for the thermal and hydro generators; these are procured from the generators' summer ratings given in the AEMO Generation Information page (2019 Jan release).
As the solar and wind generators can not be relied upon to provide during peak hours, a peak contribution factor is given instead of firm capacity.
Existing and committed generators |  | Wind and solar peak contribution factor1,4
Generator | Firm capacity (MW) | Generator | Summer | Not summer
Bayswater | 2545 | NSW wind2 | 6.7% | 3.7%
Eraring | 2720 | VIC wind2 | 8.1% | 7.3%
Liddell | 1800 | SA wind2 | 9.4% | 6.7%
Mount Piper | 1300 | TAS wind2 | 10.5% | 7.3%
Vales Point | 1320 | Solar; existing and committed to 2020-213 | 11% | 11%
Callide B | 700 | New solar, 2021-22 to 2025-26 | 5.5% | 5.5%
Callide Power Plant | 840 | New solar, post 2025-26 | 0% | 0%
Gladstone | 1680
Kogan Creek | 713
Millmerran | 612
Stanwell | 1460 | 1. Peak contribution factor refers to the percentage of total capacity expected to be available at the time of peak demand, as used to measure the available generation reserves in the capacity outlook model
Tarong | 1400 | 2. Assumes 2017 South Australian Renewable Energy Report wind contribution factors for the entire modelling horizon. QLD value subject to review as 2017 report could not include as no wind installed in QLD at that point in time.
Tarong North | 443 | http://aemo.com.au/-/media/Files/Electricity/NEM/Planning_and_Forecasting/SA_Advisory/2017/South-Australian-Renewable-Energy-Report-2017.pdf
Loy Yang A | 2144 | 3. As solar penetration increases, peak demand moves away from times where solar energy is available
Loy Yang B | 980 | 4. All other new entrant technologies are assumed to have a 100% firm contribution factor
Yallourn | 1420
Colongra | 648
Smithfield | 108.999
Tallawarra | 378
Uranquinty | 640
Barcaldine | 34
Braemar | 491
Braemar 2 | 495
Condamine | 89.5
Darling Downs | 580
Oakey | 282
Roma | 54
Swanbank E | 350
Yabulu | 155
Yarwun | 180
Somerton | 140
Bairnsdale | 78
Jeeralang A | 189
Jeeralang B | 216
Laverton North | 300
Mortlake | 518
Newport | 475
Valley Power | 270
Hallett GT | 193
Dry Creek | 112
Ladbroke Grove | 68
Mintaro | 68
Osborne | 172
Pelican Point | 478
Quarantine | 189
Torrens Island A | 240
Torrens Island B | 780
Bell Bay Three | 105
Tamar Valley OCGT | 58
Hunter Valley GT | 30
Mackay GT | 34
Mount Stuart | 400
Angaston | 50
Lonsdale | 20.7
Port Lincoln | 56
Port Stanvac | 57.6
Snuggery | 54
Blowering | 80
Guthega | 68
Hume | 29
Shoalhaven | 240
Upper Tumut | 544
Tumut 3 | 1800
Barron Gorge | 66
Kareeya | 86.4
Wivenhoe | 570
Bogong / Mackay | 300
Dartmouth | 165
Eildon | 100
Murray 1 | 855
Murray 2 | 560
West Kiewa | 68
Bastyan | 81
Catagunya / Liapootah / Wayatinah | 149.7
Cethana | 95
Devils Gate | 63
Fisher | 46
Gordon | 370.8
John Butters | 140
Lake Echo | 30
Lemonthyme / Wilmot | 32
Mackintosh | 81
Meadowbank | 43.8
Poatina | 342
Reece | 232
Tarraleah | 90
Trevallyn | 81.9
Tribute | 88
Tungatinah | 104.4

## Generation limits
Go to Assumptions Summary
Generator operating limits and behaviours
The following modelling assumptions are based on GHD and AEMO analysis of historical generator performance. The minimum operating loads are applied to target reasonable operating levels of units and/or power stations.
Coal minimum load |  |  | GPG minimum load1 |  | Capacity factor constraints
Generator Station | Generating unit | Minimum Load (MW) | Generator | Minimum Load (MW) | Generator | Min Capacity Factors | Max Capacity Factors | End time
Bayswater | BW01 | 291 | Tallawarra | 190 | Liddell |  | 50% | Date of retirement
Bayswater | BW02 | 291 | Condamine | 60 | Osborne* | 50% |  | Depending on timing of SA interconnector expansion
Bayswater | BW03 | 291 | Darling Downs | 109 | Pelican Point* | 50% |  | Depending on timing of SA interconnector expansion
Bayswater | BW04 | 291 | Yarwun | 120 | Torrens Island B* | 20% |  | Depending on timing of SA interconnector expansion
Eraring | ER01 | 230 |  |  | * South Australian minimum capacity factors are reduced consistent with the timing of a possible second synchronous interconnector.
Eraring | ER02 | 230 | 1. Total power station minimum load conditions reflect assumed efficient use of gas and steam turbines in CCGT operating mode.
Eraring | ER03 | 230
Eraring | ER04 | 230
Liddell | LD01 | 219
Liddell | LD02 | 219
Mount Piper | MP1 | 294
Mount Piper | MP2 | 294
Vales Point | VP5 | 251
Vales Point | VP6 | 251
Callide B | CALL_B_1 | 172
Callide B | CALL_B_2 | 172
Callide Power Plant | CPP_3 | 222
Callide Power Plant | CPP_4 | 222
Gladstone | GSTONE1 | 110
Gladstone | GSTONE2 | 110
Gladstone | GSTONE3 | 110
Gladstone | GSTONE4 | 110
Kogan Creek | KPP_1 | 350
Millmerran | MPP_1 | 170
Millmerran | MPP_2 | 170
Stanwell | STAN-1 | 183
Stanwell | STAN-2 | 183
Stanwell | STAN-3 | 183
Tarong | TARONG#1 | 140
Tarong | TARONG#2 | 140
Tarong | TARONG#3 | 140
Tarong North | TNPS1 | 178
Loy Yang B | LOYYB1 | 305
Loy Yang B | LOYYB2 | 305
Loy Yang A | LYA1 | 347
Loy Yang A | LYA2 | 310
Loy Yang A | LYA3 | 347
Loy Yang A | LYA4 | 347
Yallourn | YWPS1 | 210
Yallourn | YWPS2 | 210
Yallourn | YWPS3 | 225
Yallourn | YWPS4 | 228

## Seasonal ratings
Go to Assumptions Summary
Seasonal ratings (available for dispatch in each season)
Generator capacity may vary with weather conditions. Refer AEMO Generation Information page (2019 January release) for seasonal ratings for the first 10 years of the model period.
Not all committed or advanced projects have ratings listed in Generation Information. Where information is absent nameplate capacity is used.
Existing generators1 |  |  | Committed and advanced projects1
Generator | Summer (MW) | Not summer (MW) | Generator | Summer (MW) | Not summer (MW)
Bayswater | 2545 | 2665 | Barker Inlet | 210 | 210
Eraring | 2720 | 2880 | Bodangora WF | 113.19 | 113.19
Liddell | 1800 | 1800 | Crookwell 2 WF | 91 | 91
Mount Piper | 1300 | 1400 | Mt Emerald WF | 180.45 | 180.45
Vales Point | 1320 | 1320 | Coopers Gap WF | 453 | 453
Callide B | 700 | 700 | Kennedy Energy Park WF | 43.2 | 43.2
Callide Power Plant | 840 | 840 | Crudine Ridge WF | 135 | -
Gladstone | 1680 | 1680 | Crowlands WF | 79.95 | 79.95
Kogan Creek | 713 | 750 | Lincoln Gap WF | 126 | 126
Millmerran | 612 | 852 | Willogoleche WF | 119.4 | 119.4
Stanwell | 1460 | 1460 | Cattle Hill WF | 144 | 144
Tarong | 1400 | 1400 | Granville Harbour WF | 111.6 | -
Tarong North | 443 | 443 | Mt Gellibrand WF | 132 | 132
Loy Yang A | 2144 | 2210 | Murra Warra WF | 226 | 226
Loy Yang B | 980 | 1150 | Bulgana WF | 194 | 194
Yallourn | 1420 | 1528 | Cherry Tree WF | - | -
Colongra | 648 | 724 | Lal Lal Elaine WF | 83.6 | -
Smithfield1 | 108.999 | 108.999 | Lal Lal Yendon WF | 144.4 | 144.4
Tallawarra | 378 | 440 | Moorabool WF2 | 320 | 320
Uranquinty | 640 | 664 | Stockyard Hill WF | 400 | 532
Barcaldine | 34 | 37 | Bomen Solar | 100 | 100
Braemar | 491 | 530 | Daydream Solar | 150 | 150
Braemar 2 | 495 | 519 | Darlington Point Solar | 263.333 | 275
Condamine | 89.5 | 100 | Finley Solar | 133 | 133
Darling Downs | 580 | 633 | Hayman Solar | 50 | 50
Oakey | 282 | 346 | Brigalow Solar | 0 | 34.5
Roma | 54 | 68 | Childers Solar | 56 | 56
Swanbank E2 | 350 | 365 | Clermont Solar | 75 | 75
Yabulu | 155 | 161 | Collinsville Solar | 42.5 | 42.5
Yarwun1 | 180 | 180 | Haughton Solar | 100 | 97.3
Somerton | 140 | 160 | Kennedy Energy Park Solar | 15 | 15
Bairnsdale | 78 | 84 | Lilyvale Solar | 99.3 | 79.8
Jeeralang A | 189 | 224 | Limondale 1 Solar | 0 | 220
Jeeralang B | 216 | 255 | Limondale 2 Solar | 29 | 29
Laverton North | 300 | 340 | Oakey Solar | 25 | 25
Mortlake | 518 | 584 | Oakey 2 Solar | 55 | 55
Newport | 475 | 510 | Rugby Run Solar | 65 | -
Valley Power | 270 | 336 | Susan River Solar | 75 | 75
Hallett GT | 193 | 216 | Teebar Solar | 52.5 | 52.5
Dry Creek | 112 | 143 | Yarranlea Solar | 102.5 | 102.5
Ladbroke Grove | 68 | 84 | Warwick Solar | 0 | 64.2
Mintaro | 68 | 90 | Beryl Solar | 87 | 83
Osborne | 172 | 188 | Nevertire Solar | 105 | 105
Pelican Point | 478 | 529 | Sunraysia Solar | - | 200
Quarantine | 189 | 221 | Bungala 2 Solar | 110 | 110
Torrens Island A | 240 | 240 | Bannerton Solar | 88 | 88
Torrens Island B | 780 | 800 | Kiamal Solar2 | 200 | 200
Bell Bay Three | 105 | 105 | Karadoc Solar | 90 | 90
Tamar Valley CCGT | 0 | 0 | Numurkah Solar | 100 | 100
Tamar Valley OCGT | 58 | 58 | Tailem Bend Solar | 95 | 95
Hunter Valley GT | 30 | 40 | Yatpool Solar | 81 | 81
Mackay GT | 34 | 34 | Wemen Solar | 87.75 | 87.75
Mount Stuart | 400 | 428 | Note:
Angaston | 50 | 50 | 1. "Summer" ratings are 2019/20 summer ratings and "not summer" ratings are 2020 winter ratings
Lonsdale | 20.7 | 20.7
Port Lincoln | 56 | 73.5 | 2. Seasonal ratings are absent and nameplate capacities are used.
Port Stanvac | 57.6 | 57.6
Snuggery | 54 | 63
Blowering | 80 | 80
Guthega | 68 | 68
Hume | 29 | 0
Shoalhaven | 240 | 240
Upper Tumut | 544 | 616
Tumut 3 | 1800 | 1800
Barron Gorge | 66 | 66
Kareeya | 86.4 | 86.4
Wivenhoe | 570 | 570
Bogong / Mackay | 300 | 300
Dartmouth | 165 | 165
Eildon | 100 | 100
Murray 1 | 855 | 950
Murray 2 | 560 | 420
West Kiewa | 68 | 68
Bastyan | 81 | 81
Catagunya / Liapootah / Wayatinah | 149.7 | 173.7
Cethana | 95 | 95
Devils Gate | 63 | 63
Fisher | 46 | 46
Gordon | 370.8 | 370.8
John Butters | 140 | 140
Lake Echo | 30 | 0
Lemonthyme / Wilmot | 32 | 86
Mackintosh | 81 | 81
Meadowbank | 43.8 | 43.8
Poatina | 342 | 342
Reece | 232 | 232
Tarraleah | 90 | 90
Trevallyn | 81.9 | 102.8
Tribute | 88 | 88
Tungatinah | 104.4 | 130.5
Boco Rock WF | 104.09 | 113.18
Capital WF2 | 140.7 | 140.7
Cullerin Range WF2 | 30 | 30
Gullen Range WF | 165.5 | 165.5
Gunning WF | 46.5 | 46.5
Silverton WF | 198 | 198
Sapphire WF | 187 | 270
Taralga WF | 106.8 | 106.8
White Rock WF | 172.5 | 172.5
Woodlawn WF | 48.3 | 48.3
Canunda WF2 | 46 | 46
Cathedral Rocks WF2 | 66 | 66
Clements Gap WF | 56.7 | 56.7
Hallett 1 Brown Hill WF | 58.5 | 94.5
Hallett 2 Hallett Hill WF | 44.2 | 71.4
Hallett 3 North Brown Hill WF | 81.9 | 132.3
Hallett 4 The Bluff WF | 32.5 | 52.5
Hornsdale S1 WF | 100 | 100
Hornsdale S2 WF | 100 | 100
Hornsdale S3 WF | 109 | 109
Lake Bonney 1 WF2 | 80.5 | 80.5
Lake Bonney 2 WF | 159 | 159
Lake Bonney 3 WF | 39 | 39
Mount Millar WF1 | 70 | 70
Snowtown WF | 98.7 | 98.7
Snowtown S2 WF | 270 | 270
Starfish Hill WF2 | 34.5 | 34.5
Waterloo WF | 130.8 | 130.8
Wattle Point WF2 | 90.75 | 90.75
Musselroe WF | 168 | 168
Woolnorth WF2 | 140 | 140
Ararat WF | 195 | 240
Bald Hills WF | 106.6 | 106.6
Challicum Hills WF2 | 52.5 | 52.5
Kiata WF | 31.05 | 31.05
Macarthur WF | 420 | 420
Mortons Lane WF2 | 19.5 | 19.5
Mount Mercer WF | 131.2 | 131.2
Oaklands Hill WF | 41.6 | 63
Portland WF1 | 151.7 | 151.7
Salt Creek WF | 54 | 54
Waubra WF2 | 192 | 192
Yambuk WF2 | 30 | 30
Yaloak South WF2 | 28.7 | 28.7
Broken Hill Solar | 53 | 53
Coleambally Solar | 150 | 130
Griffith Solar2 | 29.99 | 29.99
Manildra Solar | 46.7 | 45
Moree Solar | 55.2 | 44.4
Nyngan Solar | 102 | 102
Parkes Solar | 55 | 53.5
Clare Solar | 99.3 | 79.8
Darling Downs Solar | 108.5 | 108.5
Hamilton Solar | 57.5 | 57.5
Hughenden Solar2 | 18 | 18
Kidston Solar | 48.5 | 48.5
Longreach Solar2 | 17 | 17
Ross River Solar | 116 | 116
Sun Metals Solar | 124 | 124
Gannawarra Solar | 50 | 50
Bungala one Solar | 110 | 110
Whitsunday Solar | 57.5 | 57.5
Note:
1. Summer ratings are 2019/20 summer ratings and not summer ratngs are 2020 winter ratings
2. Seasonal ratings are absent and Name plate Capacities are used.

## Generator Reliability Settings
Go to Assumptions Summary
Generator Reliability Settings
All units take the outage rate of their respective fuel type.
Existing generator outage rates are based on the most recent three years outage data.
Existing generators | [6 empty] | New entrant technologies
Fuel type | Forced Outage Rate (%) 2 |  | Mean time to repair (hrs) 3 |  | Partial Outage Derating Factor 4 | Expected Forced Outage Rate | Fuel type | Forced Outage Rate (%) |  | Mean time to repair (hrs) |  | Equivalent forced outage rate (%)
| Full outage % of time | Partial outage % of time | Full outage | Partial outage |  |  |  | Full outage % of time | Partial outage % of time | Full outage | Partial outage
Black Coal (Qld) | 2.42% | 13.51% | 53 | 16 | 16.94% | 4.709% | Black Coal (supercritical PC) | 2 | 1 | - | - | 2.3
Black Coal (NSW) - until 2022 | 6.56% | 25.81% | 135 | 19 | 19.98% | 11.72% | Black Coal (supercritical PC) with CCS | 2 | 1 | - | - | 2.3
Black Coal (NSW) - post 2022 | 3.88% | 23.45% | 102 | 16 | 17.76% | 8.045% | Brown Coal (supercritical PC) | 2 | 1 | - | - | 2.3
Brown Coal (Vic) | 5.34% | 13.32% | 40 | 7 | 19.18% | 7.895% | Brown Coal (supercritical PC) with CCS | 2 | 1 | - | - | 2.3
Hydro | 1.58% | 0.01% | 15 | 7 | 17.26% | 1.582% | OCGT | 1 | 1 | - | - | 1.1
Liquid Fuel | 3.56% | 0.28% | 15 | 21 | 26.91% | 3.635% | CCGT | 2 | 1 | - | - | 2.4
Gas-powered steam turbine | 4.58% | 11.25% | 124 | 75 | 22.85% | 7.151% | CCGT with CCS | 2 | 1 | - | - | 2.4
CCGT | 1.33% | 0.36% | 17 | 36 | 42.76% | 1.484% | Biomass | 3 | 2 | - | - | 3.6
OCGT | 3.56% | 0.28% | 15 | 21 | 26.91% | 3.635% | Large scale Solar PV | 0.4 | 0.8 | 36 | 96 | 0.0048
[7 empty] | Solar Thermal (8hrs Storage) | 4 | 0 | 10 | 0 | 8
1. Gas-powered steam turbines include Darling Downs, Newport and Torrens Island A and B | [6 empty] | Nuclear (SMR) | <0.8 | 4.8 | 700 | 420 | 5.6
2. The percentage of time per year that a generator is expected to be out of service due to forced outage. | [6 empty] | Battery Storage (2hrs storage) | 1.5 | 3 | 48 | 96 | 0.021
3. The average time take to return a generating unit to service | [6 empty] | Wind | 3.5 | - | 300 | - | 0
4. The loss of capacity during a partial outage, relative to generator unit rating. If the outage factor is 20%, the generator will operate at 80% capacity during a partial outage. | [6 empty] | Pumped hydro (6 hrs storage) | - | - | - | - | 1

## Maintenance
Go to Assumptions Summary
Maintenance rate
The percentage of time per year that a generator is expected to be out of service for maintenance.
Existing generators |  |  |  | New entrant technologies
Generator type | % of time out | Planned outages per year | Equivalent average days per year on planned outage | Generator type | % of time out | Planned outages per year | Equivalent average days per year on planned outage
Black Coal | 5.479% | 1 | 20 | Black Coal (supercritical PC) | 5.753% | - | 21
Brown Coal | 5.479% | 1 | 20 | Black Coal (supercritical PC) with CCS | 5.753% | - | 21
Hydro | 0.274% | 1 | 1 | Brown Coal (supercritical PC) | 5.753% | - | 21
CCGT | 5.479% | 1 | 20 | Brown Coal (supercritical PC) with CCS | 5.753% | - | 21
OCGT | 1.37% | 1 | 5 | OCGT | 1.096% | - | 4
Gas-fired Steam turbine | 0.6849% | 1 | 2.5 | CCGT | 2.74% | - | 10
Reciprocating Engine | 1.644% | 1 | 6 | CCGT with CCS | 2.74% | - | 10
|  |  |  | Biomass | 8.219% | - | 30
|  |  |  | Large scale Solar PV | 0.8219% | 2 | 3
|  |  |  | Solar Thermal (8hrs Storage) | 2.192% | 2 | 8
|  |  |  | Nuclear (SMR) | 4.795% | 1 | 17.5
|  |  |  | Battery Storage (2hrs storage) | 1.096% | 2 | 4
|  |  |  | Wind | 3.501% | 2 | 12.78
|  |  |  | Pumped hydro (6 hrs storage) | 0.274% | 1 | 1

## Build costs
Go to Assumptions Summary
Capital Cost Projections (real 2019 dollars)
Cost to construct new generation, not including connection costs.
These capital cost trajectories are developed by CSIRO GALLM (see Electricity generation technology cost projections: 2017-2050 for more details) based on the technology specific capital cost estimates provided by GHD ( AEMO costs and technical parameter review).
Battery storage capital cost estimates provided by GHD have been revised by CSIRO to be comparable with other studies.
Wind capital cost projections given by CSIRO have been adjusted to capture increasing wind turbine efficiency over time.
Expected build costs - global temperature growth of 4 degrees |  | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
Black Coal (supercritical PC) | $/kW | 3252 | 3247 | 3242 | 3236 | 3231 | 3226 | 3221 | 3216 | 3211 | 3205 | 3200 | 3195 | 3190 | 3185 | 3180 | 3175 | 3170 | 3165 | 3160 | 3154 | 3149 | 3144 | 3139 | 3134 | 3129 | 3124 | 3119 | 3114 | 3109 | 3104 | 3099 | 3094
Black Coal (supercritical PC) with CCS | $/kW | 6002 | 5995 | 5988 | 5981 | 5974 | 5968 | 5961 | 5954 | 5947 | 5940 | 5934 | 5927 | 5920 | 5913 | 5907 | 5900 | 5893 | 5880 | 5696 | 5617 | 5518 | 5425 | 5336 | 5302 | 5293 | 5276 | 5265 | 5254 | 5246 | 5239 | 5232 | 5224
Brown Coal (supercritical PC) | $/kW | 5019 | 5011 | 5003 | 4995 | 4987 | 4979 | 4971 | 4963 | 4955 | 4947 | 4939 | 4932 | 4924 | 4916 | 4908 | 4900 | 4892 | 4884 | 4877 | 4869 | 4861 | 4853 | 4845 | 4838 | 4830 | 4822 | 4814 | 4807 | 4799 | 4791 | 4784 | 4776
Brown Coal (supercritical PC) with CCS | $/kW | 9212 | 9201 | 9189 | 9178 | 9166 | 9155 | 9144 | 9132 | 9121 | 9110 | 9099 | 9087 | 9076 | 9065 | 9054 | 9043 | 9032 | 9012 | 8785 | 8685 | 8562 | 8445 | 8334 | 8289 | 8275 | 8252 | 8235 | 8219 | 8207 | 8195 | 8184 | 8171
OCGT | $/kW | 893 | 891 | 890 | 889 | 887 | 886 | 884 | 883 | 881 | 880 | 879 | 877 | 876 | 874 | 873 | 872 | 870 | 869 | 867 | 866 | 865 | 863 | 862 | 861 | 859 | 858 | 856 | 855 | 854 | 852 | 851 | 850
CCGT | $/kW | 1276 | 1274 | 1272 | 1270 | 1268 | 1266 | 1264 | 1262 | 1260 | 1258 | 1256 | 1254 | 1252 | 1250 | 1248 | 1246 | 1244 | 1242 | 1240 | 1238 | 1236 | 1234 | 1232 | 1230 | 1228 | 1226 | 1224 | 1222 | 1220 | 1218 | 1216 | 1214
CCGT with CCS | $/kW | 3781 | 3778 | 3776 | 3774 | 3772 | 3769 | 3767 | 3765 | 3762 | 3760 | 3758 | 3756 | 3753 | 3751 | 3749 | 3747 | 3744 | 3733 | 3487 | 3384 | 3255 | 3133 | 3017 | 2977 | 2971 | 2955 | 2946 | 2939 | 2935 | 2932 | 2929 | 2924
Biomass | $/kW | 12567 | 12523 | 12518 | 12507 | 12507 | 12507 | 12507 | 12507 | 12507 | 12507 | 12507 | 12507 | 12505 | 12505 | 12504 | 12504 | 12502 | 12501 | 12501 | 12501 | 12501 | 12499 | 12493 | 12493 | 12493 | 12493 | 12493 | 12493 | 12445 | 12368 | 12341 | 12265
Large scale Solar PV | $/kW | 1458 | 1349 | 1175 | 1118 | 1068 | 1029 | 990 | 957 | 926 | 891 | 860 | 832 | 806 | 792 | 774 | 755 | 749 | 721 | 712 | 703 | 697 | 688 | 667 | 647 | 629 | 611 | 594 | 578 | 570 | 560 | 546 | 543
Solar Thermal (8hrs Storage) | $/kW | 5814 | 5216 | 5216 | 5216 | 5216 | 5216 | 5216 | 5216 | 5216 | 5216 | 5216 | 5207 | 5200 | 5159 | 5123 | 4674 | 4502 | 4411 | 4232 | 4111 | 4023 | 3957 | 3905 | 3864 | 3830 | 3802 | 3778 | 3757 | 3705 | 3642 | 3586 | 3537
Nuclear (SMR) | $/kW | 16000 | 16000 | 15987 | 15969 | 15969 | 15969 | 15969 | 15969 | 15966 | 15963 | 15954 | 15949 | 15860 | 15855 | 15850 | 15847 | 15845 | 15844 | 15844 | 15844 | 15844 | 15844 | 15844 | 15831 | 15827 | 15824 | 15824 | 15824 | 15824 | 15824 | 15823 | 15823
Battery storage (2 hrs) | $/kWh | 222 | 198 | 191 | 175 | 159 | 144 | 128 | 102 | 83 | 71 | 64 | 46 | 46 | 46 | 45 | 45 | 45 | 44 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 42 | 42 | 42
Battery storage BOP | $/kWh | 508 | 489 | 474 | 462 | 451 | 438 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 422 | 417 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409
Wind | $/kW | 1864.43 | 1842.0147 | 1820.7275 | 1803.316 | 1787.8945 | 1772.6106 | 1759.28 | 1746.0674 | 1735.6733 | 1725.3704 | 1715.1575 | 1705.0334 | 1694.997 | 1684.1658 | 1662.0198 | 1633.9467 | 1624.3836 | 1614.9015 | 1605.4994 | 1596.1764 | 1586.9314 | 1576.9115 | 1567.8231 | 1558.8098 | 1550.7122 | 1541.8429 | 1533.8806 | 1525.983 | 1517.3216 | 1507.9056 | 1498.5652 | 1488.4817
Notes
1. The capital costs are overnight costs for construction in Melbourne. To calculate the capital costs of these technologies elsewhere in Australia use Regional costs adjustments factors given in the Regional Cost Factors worksheet.
Aggressive build costs - global temperature growth of 2 degrees |  | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
Black Coal (supercritical PC) | $/kW | 3252 | 3247 | 3242 | 3236 | 3231 | 3226 | 3221 | 3216 | 3211 | 3205 | 3200 | 3195 | 3190 | 3185 | 3180 | 3175 | 3170 | 3165 | 3160 | 3154 | 3149 | 3144 | 3139 | 3134 | 3129 | 3124 | 3119 | 3114 | 3109 | 3104 | 3099 | 3094
Black Coal (supercritical PC) with CCS | $/kW | 6002 | 5995 | 5988 | 5981 | 5974 | 5968 | 5961 | 5954 | 5947 | 5940 | 5779 | 5705 | 5598 | 5498 | 5461 | 5427 | 5399 | 5370 | 5353 | 5334 | 5314 | 5299 | 5289 | 5282 | 5274 | 5267 | 5260 | 5252 | 5245 | 5238 | 5230 | 5222
Brown Coal (supercritical PC) | $/kW | 5019 | 5011 | 5003 | 4995 | 4987 | 4979 | 4971 | 4963 | 4955 | 4947 | 4939 | 4932 | 4924 | 4916 | 4908 | 4900 | 4892 | 4884 | 4877 | 4869 | 4861 | 4853 | 4845 | 4838 | 4830 | 4822 | 4814 | 4807 | 4799 | 4791 | 4784 | 4776
Brown Coal (supercritical PC) with CCS | $/kW | 9212 | 9201 | 9189 | 9178 | 9166 | 9155 | 9144 | 9132 | 9121 | 9110 | 8910 | 8817 | 8683 | 8558 | 8509 | 8465 | 8429 | 8390 | 8367 | 8341 | 8313 | 8291 | 8276 | 8264 | 8253 | 8241 | 8229 | 8217 | 8205 | 8193 | 8182 | 8169
OCGT | $/kW | 893 | 891 | 890 | 889 | 887 | 886 | 884 | 883 | 881 | 880 | 879 | 877 | 876 | 874 | 873 | 872 | 870 | 869 | 867 | 866 | 865 | 863 | 862 | 861 | 859 | 858 | 856 | 855 | 854 | 852 | 851 | 850
CCGT | $/kW | 1276 | 1274 | 1272 | 1270 | 1268 | 1266 | 1264 | 1262 | 1260 | 1258 | 1256 | 1254 | 1252 | 1250 | 1248 | 1246 | 1244 | 1242 | 1240 | 1238 | 1236 | 1234 | 1232 | 1230 | 1228 | 1226 | 1224 | 1222 | 1220 | 1218 | 1216 | 1214
CCGT with CCS | $/kW | 3781 | 3778 | 3776 | 3774 | 3772 | 3769 | 3767 | 3765 | 3762 | 3760 | 3544 | 3450 | 3308 | 3178 | 3133 | 3094 | 3063 | 3030 | 3013 | 2994 | 2973 | 2959 | 2952 | 2949 | 2946 | 2943 | 2940 | 2936 | 2933 | 2930 | 2927 | 2923
Biomass | $/kW | 12595 | 12592 | 12587 | 12576 | 12576 | 12576 | 12576 | 12576 | 12576 | 12576 | 12547 | 12432 | 12427 | 12427 | 12427 | 12427 | 12424 | 12395 | 12261 | 12249 | 12249 | 12082 | 11909 | 11895 | 11895 | 11872 | 11872 | 11868 | 11868 | 11864 | 11864 | 11864
Large scale Solar PV | $/kW | 1450 | 1280 | 1218 | 1170 | 1122 | 1081 | 986 | 903 | 877 | 853 | 830 | 817 | 791 | 781 | 769 | 753 | 746 | 728 | 725 | 715 | 710 | 699 | 688 | 682 | 665 | 645 | 632 | 608 | 605 | 593 | 582 | 579
Solar Thermal (8hrs Storage) | $/kW | 5993 | 5377 | 5377 | 5377 | 5377 | 5377 | 5377 | 5377 | 5370 | 5355 | 5328 | 5281 | 5281 | 5281 | 5280 | 5266 | 5104 | 4878 | 4653 | 4547 | 4348 | 4218 | 4126 | 4058 | 4005 | 3964 | 3930 | 3902 | 3878 | 3834 | 3763 | 3701
Nuclear (SMR) | $/kW | 15992 | 15991 | 15989 | 15971 | 15971 | 15971 | 15971 | 15968 | 15966 | 15963 | 15956 | 15953 | 15868 | 15843 | 15843 | 15843 | 15843 | 15843 | 15843 | 15843 | 15843 | 15843 | 15842 | 15823 | 15823 | 15823 | 15823 | 15823 | 15823 | 15823 | 15823 | 15823
Battery storage (2 hrs) | $/kWh | 220 | 196 | 191 | 177 | 164 | 151 | 137 | 107 | 86 | 73 | 65 | 47 | 47 | 46 | 46 | 46 | 45 | 45 | 45 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Battery storage BOP | $/kWh | 486 | 471 | 462 | 455 | 450 | 446 | 443 | 442 | 441 | 441 | 440 | 440 | 439 | 438 | 437 | 436 | 435 | 434 | 433 | 432 | 432 | 431 | 431 | 431 | 431 | 431 | 431 | 430 | 430 | 430 | 429 | 429
Wind | $/kW | 1875.6334 | 1863.3903 | 1848.4825 | 1833.709 | 1819.068 | 1783.5639 | 1762.9149 | 1738.8298 | 1719.4605 | 1699.3643 | 1689.265 | 1665.919 | 1651.6263 | 1636.5755 | 1622.5314 | 1606.8599 | 1592.1917 | 1579.3806 | 1570.1284 | 1559.2358 | 1551.0008 | 1540.2787 | 1525.4036 | 1517.4105 | 1509.4832 | 1495.7552 | 1487.1465 | 1478.6077 | 1469.3103 | 1459.2635 | 1450.1185 | 1438.5931
Notes
1. The capital costs are overnight costs for construction in Melbourne. To calculate the capital costs of these technologies elsewhere in Australia use Regional costs adjustments factors given in the Regional Cost Factors worksheet.

## Regional Cost Factors
Go to Assumptions Summary
Regional Cost Factors
The Regional cost factors for each of the cost components have been estimated by GHD to provide an indication of the variation in project costs between geographic regions.
CSIRO build costs projections for new entrants are overnight costs for construction in Melbourne. These regional cost factors are used to convert the Melbourne cost estimates to each region-specific cost estimate.
Refer to the REZ Sheet for the definition of each geographic area.
Regional cost factors
Region | Equipment costs | Fuel connection costs | Cost of land and development | Installation costs | O&M costs
Vic low | 1 | 1 | 1 | 1 | 1
Vic medium | 1.03 | 1.03 | 1 | 1.03 | 1.03
Vic high | 1.05 | 1.05 | 1 | 1.05 | 1.05
Qld low | 1 | 1.05 | 1 | 1.1 | 1.07
Qld medium | 1.05 | 1.16 | 1 | 1.27 | 1.2
Qld high | 1.1 | 1.27 | 1 | 1.44 | 1.34
NSW low | 1 | 1.09 | 1 | 1.18 | 1.13
NSW medium | 1.05 | 1.17 | 1 | 1.3 | 1.22
NSW high | 1.1 | 1.26 | 1 | 1.42 | 1.32
SA Low | 1 | 1.01 | 1 | 1.02 | 1.01
SA medium | 1.05 | 1.11 | 1 | 1.17 | 1.13
SA high | 1.1 | 1.21 | 1 | 1.32 | 1.25
WA low | 1 | 1.06 | 1 | 1.11 | 1.08
WA medium | 1.05 | 1.22 | 1 | 1.39 | 1.29
WA high | 1.1 | 1.38 | 1 | 1.67 | 1.5
NT low | 1 | 1.13 | 1 | 1.27 | 1.19
NT medium | 1.05 | 1.32 | 1 | 1.59 | 1.42
NT high | 1.1 | 1.5 | 1 | 1.9 | 1.66
Tas low | 1 | 1.04 | 1 | 1.07 | 1.05
Tas medium | 1.05 | 1.11 | 1 | 1.18 | 1.14
Tas high | 1.1 | 1.19 | 1 | 1.29 | 1.23

## Generator Regional Build costs
Go to Assumptions Summary
Example generator build cost, after application of regional cost factors ($/kW, real 2019 dollars)
Example build cost for the 4 degrees scenario, for information purposes. The regional capital costs are for the 4 degrees scenario including fuel connection costs. Method for applying the regional cost factors applies to both 4 degrees and 2 degrees capital cost scenarios.
Cost trajectories calculated by applying Regional Cost factors to baseline provided for a region-specific cost estimate, as developed by CSIRO and GHD.
Technology Type | Generator Name | Region | Regional Cost Zone | Cost Scenario | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
Large scale Solar PV | Barcaldine | Qld | Qld medium | 4 Degrees | 1548.094 | 1432.3586 | 1247.6066 | 1187.0844 | 1133.9948 | 1092.5849 | 1051.175 | 1016.1358 | 983.2202 | 946.0575 | 913.1419 | 883.4117 | 855.8051 | 840.94 | 821.8277 | 801.6536 | 795.2829 | 765.5527 | 755.9965 | 746.4404 | 740.0696 | 730.5135 | 708.2159 | 686.98 | 667.8677 | 648.7555 | 630.705 | 613.7163 | 605.2219 | 594.604 | 579.7389 | 576.5535
Large scale Solar PV | Darling Downs | Qld | Qld medium | 4 Degrees | 1548.094 | 1432.3586 | 1247.6066 | 1187.0844 | 1133.9948 | 1092.5849 | 1051.175 | 1016.1358 | 983.2202 | 946.0575 | 913.1419 | 883.4117 | 855.8051 | 840.94 | 821.8277 | 801.6536 | 795.2829 | 765.5527 | 755.9965 | 746.4404 | 740.0696 | 730.5135 | 708.2159 | 686.98 | 667.8677 | 648.7555 | 630.705 | 613.7163 | 605.2219 | 594.604 | 579.7389 | 576.5535
Large scale Solar PV | Fitzroy | Qld | Qld low | 4 Degrees | 1468.0319 | 1358.2819 | 1183.0847 | 1125.6925 | 1075.3484 | 1036.0801 | 996.8118 | 963.5847 | 932.3714 | 897.1306 | 865.9173 | 837.7246 | 811.5457 | 797.4494 | 779.3256 | 760.1948 | 754.1535 | 725.9609 | 716.899 | 707.837 | 701.7957 | 692.7338 | 671.5893 | 651.4517 | 633.3279 | 615.204 | 598.0871 | 581.977 | 573.9219 | 563.8531 | 549.7568 | 546.7361
Large scale Solar PV | Isaac | Qld | Qld low | 4 Degrees | 1468.0319 | 1358.2819 | 1183.0847 | 1125.6925 | 1075.3484 | 1036.0801 | 996.8118 | 963.5847 | 932.3714 | 897.1306 | 865.9173 | 837.7246 | 811.5457 | 797.4494 | 779.3256 | 760.1948 | 754.1535 | 725.9609 | 716.899 | 707.837 | 701.7957 | 692.7338 | 671.5893 | 651.4517 | 633.3279 | 615.204 | 598.0871 | 581.977 | 573.9219 | 563.8531 | 549.7568 | 546.7361
Large scale Solar PV | North Queensland Clean Energy Hub | Qld | Qld medium | 4 Degrees | 1548.094 | 1432.3586 | 1247.6066 | 1187.0844 | 1133.9948 | 1092.5849 | 1051.175 | 1016.1358 | 983.2202 | 946.0575 | 913.1419 | 883.4117 | 855.8051 | 840.94 | 821.8277 | 801.6536 | 795.2829 | 765.5527 | 755.9965 | 746.4404 | 740.0696 | 730.5135 | 708.2159 | 686.98 | 667.8677 | 648.7555 | 630.705 | 613.7163 | 605.2219 | 594.604 | 579.7389 | 576.5535
Large scale Solar PV | Northern Queensland | Qld | Qld low | 4 Degrees | 1468.0319 | 1358.2819 | 1183.0847 | 1125.6925 | 1075.3484 | 1036.0801 | 996.8118 | 963.5847 | 932.3714 | 897.1306 | 865.9173 | 837.7246 | 811.5457 | 797.4494 | 779.3256 | 760.1948 | 754.1535 | 725.9609 | 716.899 | 707.837 | 701.7957 | 692.7338 | 671.5893 | 651.4517 | 633.3279 | 615.204 | 598.0871 | 581.977 | 573.9219 | 563.8531 | 549.7568 | 546.7361
Large scale Solar PV | Broken Hill | NSW | NSW high | 4 Degrees | 1626.2369 | 1504.6595 | 1310.5819 | 1247.0047 | 1191.2353 | 1147.7351 | 1104.2349 | 1067.4271 | 1032.85 | 993.8114 | 959.2344 | 928.0035 | 899.0034 | 883.3879 | 863.3109 | 842.1186 | 835.4262 | 804.1953 | 794.1568 | 784.1183 | 777.426 | 767.3875 | 743.9643 | 721.6566 | 701.5796 | 681.5026 | 662.541 | 644.6947 | 635.7716 | 624.6177 | 609.0023 | 605.6561
Large scale Solar PV | Central West New South Wales | NSW | NSW high | 4 Degrees | 1626.2369 | 1504.6595 | 1310.5819 | 1247.0047 | 1191.2353 | 1147.7351 | 1104.2349 | 1067.4271 | 1032.85 | 993.8114 | 959.2344 | 928.0035 | 899.0034 | 883.3879 | 863.3109 | 842.1186 | 835.4262 | 804.1953 | 794.1568 | 784.1183 | 777.426 | 767.3875 | 743.9643 | 721.6566 | 701.5796 | 681.5026 | 662.541 | 644.6947 | 635.7716 | 624.6177 | 609.0023 | 605.6561
Large scale Solar PV | Murray River (NSW) | NSW | NSW high | 4 Degrees | 1626.2369 | 1504.6595 | 1310.5819 | 1247.0047 | 1191.2353 | 1147.7351 | 1104.2349 | 1067.4271 | 1032.85 | 993.8114 | 959.2344 | 928.0035 | 899.0034 | 883.3879 | 863.3109 | 842.1186 | 835.4262 | 804.1953 | 794.1568 | 784.1183 | 777.426 | 767.3875 | 743.9643 | 721.6566 | 701.5796 | 681.5026 | 662.541 | 644.6947 | 635.7716 | 624.6177 | 609.0023 | 605.6561
Large scale Solar PV | North West New South Wales | NSW | NSW medium | 4 Degrees | 1550.973 | 1435.0223 | 1249.9268 | 1189.292 | 1136.1037 | 1094.6167 | 1053.1298 | 1018.0255 | 985.0487 | 947.8168 | 914.84 | 885.0545 | 857.3966 | 842.5038 | 823.356 | 803.1444 | 796.7618 | 766.9763 | 757.4024 | 747.8285 | 741.4459 | 731.872 | 709.5329 | 688.2576 | 669.1097 | 649.9619 | 631.8779 | 614.8576 | 606.3475 | 595.7098 | 580.817 | 577.6257
Large scale Solar PV | New England | NSW | NSW low | 4 Degrees | 1475.709 | 1365.3851 | 1189.2717 | 1131.5794 | 1080.9721 | 1041.4984 | 1002.0247 | 968.6238 | 937.2473 | 901.8222 | 870.4457 | 842.1056 | 815.7898 | 801.6197 | 783.4011 | 764.1703 | 758.0974 | 729.7574 | 720.648 | 711.5387 | 705.4658 | 696.3565 | 675.1015 | 654.8585 | 636.6399 | 618.4213 | 601.2148 | 585.0205 | 576.9233 | 566.8018 | 552.6318 | 549.5953
Large scale Solar PV | Riverland (NSW) | NSW | NSW high | 4 Degrees | 1626.2369 | 1504.6595 | 1310.5819 | 1247.0047 | 1191.2353 | 1147.7351 | 1104.2349 | 1067.4271 | 1032.85 | 993.8114 | 959.2344 | 928.0035 | 899.0034 | 883.3879 | 863.3109 | 842.1186 | 835.4262 | 804.1953 | 794.1568 | 784.1183 | 777.426 | 767.3875 | 743.9643 | 721.6566 | 701.5796 | 681.5026 | 662.541 | 644.6947 | 635.7716 | 624.6177 | 609.0023 | 605.6561
Large scale Solar PV | Southern New South Wales Tablelands | NSW | NSW low | 4 Degrees | 1475.709 | 1365.3851 | 1189.2717 | 1131.5794 | 1080.9721 | 1041.4984 | 1002.0247 | 968.6238 | 937.2473 | 901.8222 | 870.4457 | 842.1056 | 815.7898 | 801.6197 | 783.4011 | 764.1703 | 758.0974 | 729.7574 | 720.648 | 711.5387 | 705.4658 | 696.3565 | 675.1015 | 654.8585 | 636.6399 | 618.4213 | 601.2148 | 585.0205 | 576.9233 | 566.8018 | 552.6318 | 549.5953
Large scale Solar PV | Murray River | NSW | NSW high | 4 Degrees | 1626.2369 | 1504.6595 | 1310.5819 | 1247.0047 | 1191.2353 | 1147.7351 | 1104.2349 | 1067.4271 | 1032.85 | 993.8114 | 959.2344 | 928.0035 | 899.0034 | 883.3879 | 863.3109 | 842.1186 | 835.4262 | 804.1953 | 794.1568 | 784.1183 | 777.426 | 767.3875 | 743.9643 | 721.6566 | 701.5796 | 681.5026 | 662.541 | 644.6947 | 635.7716 | 624.6177 | 609.0023 | 605.6561
Large scale Solar PV | Eastern Eyre Peninsula | SA | SA medium | 4 Degrees | 1538.4975 | 1423.4795 | 1239.8728 | 1179.7258 | 1126.9653 | 1085.812 | 1044.6588 | 1009.8369 | 977.1253 | 940.1929 | 907.4814 | 877.9355 | 850.5 | 835.7271 | 816.7333 | 796.6843 | 790.353 | 760.8071 | 751.3102 | 741.8133 | 735.482 | 725.9851 | 703.8257 | 682.7215 | 663.7277 | 644.7339 | 626.7953 | 609.9119 | 601.4702 | 590.9181 | 576.1452 | 572.9795
Large scale Solar PV | Leigh Creek | SA | SA medium | 4 Degrees | 1538.4975 | 1423.4795 | 1239.8728 | 1179.7258 | 1126.9653 | 1085.812 | 1044.6588 | 1009.8369 | 977.1253 | 940.1929 | 907.4814 | 877.9355 | 850.5 | 835.7271 | 816.7333 | 796.6843 | 790.353 | 760.8071 | 751.3102 | 741.8133 | 735.482 | 725.9851 | 703.8257 | 682.7215 | 663.7277 | 644.7339 | 626.7953 | 609.9119 | 601.4702 | 590.9181 | 576.1452 | 572.9795
Large scale Solar PV | Northern South Australia | SA | SA medium | 4 Degrees | 1538.4975 | 1423.4795 | 1239.8728 | 1179.7258 | 1126.9653 | 1085.812 | 1044.6588 | 1009.8369 | 977.1253 | 940.1929 | 907.4814 | 877.9355 | 850.5 | 835.7271 | 816.7333 | 796.6843 | 790.353 | 760.8071 | 751.3102 | 741.8133 | 735.482 | 725.9851 | 703.8257 | 682.7215 | 663.7277 | 644.7339 | 626.7953 | 609.9119 | 601.4702 | 590.9181 | 576.1452 | 572.9795
Large scale Solar PV | Riverland (SA) | SA | SA medium | 4 Degrees | 1538.4975 | 1423.4795 | 1239.8728 | 1179.7258 | 1126.9653 | 1085.812 | 1044.6588 | 1009.8369 | 977.1253 | 940.1929 | 907.4814 | 877.9355 | 850.5 | 835.7271 | 816.7333 | 796.6843 | 790.353 | 760.8071 | 751.3102 | 741.8133 | 735.482 | 725.9851 | 703.8257 | 682.7215 | 663.7277 | 644.7339 | 626.7953 | 609.9119 | 601.4702 | 590.9181 | 576.1452 | 572.9795
Large scale Solar PV | Roxby Downs | SA | SA medium | 4 Degrees | 1538.4975 | 1423.4795 | 1239.8728 | 1179.7258 | 1126.9653 | 1085.812 | 1044.6588 | 1009.8369 | 977.1253 | 940.1929 | 907.4814 | 877.9355 | 850.5 | 835.7271 | 816.7333 | 796.6843 | 790.353 | 760.8071 | 751.3102 | 741.8133 | 735.482 | 725.9851 | 703.8257 | 682.7215 | 663.7277 | 644.7339 | 626.7953 | 609.9119 | 601.4702 | 590.9181 | 576.1452 | 572.9795
Large scale Solar PV | Western Eyre Peninsula | SA | SA medium | 4 Degrees | 1538.4975 | 1423.4795 | 1239.8728 | 1179.7258 | 1126.9653 | 1085.812 | 1044.6588 | 1009.8369 | 977.1253 | 940.1929 | 907.4814 | 877.9355 | 850.5 | 835.7271 | 816.7333 | 796.6843 | 790.353 | 760.8071 | 751.3102 | 741.8133 | 735.482 | 725.9851 | 703.8257 | 682.7215 | 663.7277 | 644.7339 | 626.7953 | 609.9119 | 601.4702 | 590.9181 | 576.1452 | 572.9795
Solar Thermal 8hrs | Barcaldine | Qld | Qld medium | 4 Degrees | 6227.8463 | 5587.2801 | 5587.2801 | 5587.2801 | 5587.2801 | 5587.2801 | 5587.2801 | 5587.2801 | 5587.2801 | 5587.2801 | 5587.2801 | 5577.6395 | 5570.1412 | 5526.2228 | 5487.6603 | 5006.7 | 4822.4569 | 4724.9794 | 4533.238 | 4403.6251 | 4309.3612 | 4238.6632 | 4182.9618 | 4139.0434 | 4102.6232 | 4072.6302 | 4046.9218 | 4024.427 | 3968.7256 | 3901.2412 | 3841.2551 | 3788.7672
Solar Thermal 8hrs | Darling Downs | Qld | Qld medium | 4 Degrees | 6227.8463 | 5587.2801 | 5587.2801 | 5587.2801 | 5587.2801 | 5587.2801 | 5587.2801 | 5587.2801 | 5587.2801 | 5587.2801 | 5587.2801 | 5577.6395 | 5570.1412 | 5526.2228 | 5487.6603 | 5006.7 | 4822.4569 | 4724.9794 | 4533.238 | 4403.6251 | 4309.3612 | 4238.6632 | 4182.9618 | 4139.0434 | 4102.6232 | 4072.6302 | 4046.9218 | 4024.427 | 3968.7256 | 3901.2412 | 3841.2551 | 3788.7672
Solar Thermal 8hrs | Fitzroy | Qld | Qld low | 4 Degrees | 5877.439 | 5272.914 | 5272.914 | 5272.914 | 5272.914 | 5272.914 | 5272.914 | 5272.914 | 5272.914 | 5272.914 | 5272.914 | 5263.8158 | 5256.7394 | 5215.292 | 5178.8992 | 4725 | 4551.1232 | 4459.1303 | 4278.1772 | 4155.8569 | 4066.8967 | 4000.1765 | 3947.6091 | 3906.1617 | 3871.7908 | 3843.4852 | 3819.2234 | 3797.9942 | 3745.4268 | 3681.7394 | 3625.1284 | 3575.5937
Solar Thermal 8hrs | Isaac | Qld | Qld low | 4 Degrees | 5877.439 | 5272.914 | 5272.914 | 5272.914 | 5272.914 | 5272.914 | 5272.914 | 5272.914 | 5272.914 | 5272.914 | 5272.914 | 5263.8158 | 5256.7394 | 5215.292 | 5178.8992 | 4725 | 4551.1232 | 4459.1303 | 4278.1772 | 4155.8569 | 4066.8967 | 4000.1765 | 3947.6091 | 3906.1617 | 3871.7908 | 3843.4852 | 3819.2234 | 3797.9942 | 3745.4268 | 3681.7394 | 3625.1284 | 3575.5937
Solar Thermal 8hrs | North Queensland Clean Energy Hub | Qld | Qld medium | 4 Degrees | 6227.8463 | 5587.2801 | 5587.2801 | 5587.2801 | 5587.2801 | 5587.2801 | 5587.2801 | 5587.2801 | 5587.2801 | 5587.2801 | 5587.2801 | 5577.6395 | 5570.1412 | 5526.2228 | 5487.6603 | 5006.7 | 4822.4569 | 4724.9794 | 4533.238 | 4403.6251 | 4309.3612 | 4238.6632 | 4182.9618 | 4139.0434 | 4102.6232 | 4072.6302 | 4046.9218 | 4024.427 | 3968.7256 | 3901.2412 | 3841.2551 | 3788.7672
Solar Thermal 8hrs | Northern Queensland | Qld | Qld low | 4 Degrees | 5877.439 | 5272.914 | 5272.914 | 5272.914 | 5272.914 | 5272.914 | 5272.914 | 5272.914 | 5272.914 | 5272.914 | 5272.914 | 5263.8158 | 5256.7394 | 5215.292 | 5178.8992 | 4725 | 4551.1232 | 4459.1303 | 4278.1772 | 4155.8569 | 4066.8967 | 4000.1765 | 3947.6091 | 3906.1617 | 3871.7908 | 3843.4852 | 3819.2234 | 3797.9942 | 3745.4268 | 3681.7394 | 3625.1284 | 3575.5937
Solar Thermal 8hrs | Broken Hill | NSW | NSW high | 4 Degrees | 6565.5659 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5880.1 | 5872.1951 | 5825.8951 | 5785.2415 | 5278.2 | 5083.9659 | 4981.2024 | 4779.0634 | 4642.422 | 4543.0463 | 4468.5146 | 4409.7927 | 4363.4927 | 4325.0976 | 4293.478 | 4266.3756 | 4242.661 | 4183.939 | 4112.7951 | 4049.5561 | 3994.222
Solar Thermal 8hrs | Central West New South Wales | NSW | NSW high | 4 Degrees | 6565.5659 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5880.1 | 5872.1951 | 5825.8951 | 5785.2415 | 5278.2 | 5083.9659 | 4981.2024 | 4779.0634 | 4642.422 | 4543.0463 | 4468.5146 | 4409.7927 | 4363.4927 | 4325.0976 | 4293.478 | 4266.3756 | 4242.661 | 4183.939 | 4112.7951 | 4049.5561 | 3994.222
Solar Thermal 8hrs | Murray River (NSW) | NSW | NSW high | 4 Degrees | 6565.5659 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5880.1 | 5872.1951 | 5825.8951 | 5785.2415 | 5278.2 | 5083.9659 | 4981.2024 | 4779.0634 | 4642.422 | 4543.0463 | 4468.5146 | 4409.7927 | 4363.4927 | 4325.0976 | 4293.478 | 4266.3756 | 4242.661 | 4183.939 | 4112.7951 | 4049.5561 | 3994.222
Solar Thermal 8hrs | North West New South Wales | NSW | NSW medium | 4 Degrees | 6246.878 | 5604.3543 | 5604.3543 | 5604.3543 | 5604.3543 | 5604.3543 | 5604.3543 | 5604.3543 | 5604.3543 | 5604.3543 | 5604.3543 | 5594.6842 | 5587.163 | 5543.1104 | 5504.43 | 5022 | 4837.1938 | 4739.4185 | 4547.0911 | 4417.0822 | 4322.5302 | 4251.6162 | 4195.7445 | 4151.6919 | 4115.1605 | 4085.0757 | 4059.2888 | 4036.7253 | 3980.8537 | 3913.163 | 3852.9936 | 3800.3453
Solar Thermal 8hrs | New England | NSW | NSW low | 4 Degrees | 5928.1902 | 5318.4452 | 5318.4452 | 5318.4452 | 5318.4452 | 5318.4452 | 5318.4452 | 5318.4452 | 5318.4452 | 5318.4452 | 5318.4452 | 5309.2684 | 5302.1309 | 5260.3257 | 5223.6186 | 4765.8 | 4590.4218 | 4497.6345 | 4315.1189 | 4191.7424 | 4102.014 | 4034.7177 | 3981.6964 | 3939.8911 | 3905.2234 | 3876.6734 | 3852.2021 | 3830.7896 | 3777.7683 | 3713.5309 | 3656.4311 | 3606.4687
Solar Thermal 8hrs | Riverland (NSW) | NSW | NSW high | 4 Degrees | 6565.5659 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5880.1 | 5872.1951 | 5825.8951 | 5785.2415 | 5278.2 | 5083.9659 | 4981.2024 | 4779.0634 | 4642.422 | 4543.0463 | 4468.5146 | 4409.7927 | 4363.4927 | 4325.0976 | 4293.478 | 4266.3756 | 4242.661 | 4183.939 | 4112.7951 | 4049.5561 | 3994.222
Solar Thermal 8hrs | Southern New South Wales Tablelands | NSW | NSW low | 4 Degrees | 5928.1902 | 5318.4452 | 5318.4452 | 5318.4452 | 5318.4452 | 5318.4452 | 5318.4452 | 5318.4452 | 5318.4452 | 5318.4452 | 5318.4452 | 5309.2684 | 5302.1309 | 5260.3257 | 5223.6186 | 4765.8 | 4590.4218 | 4497.6345 | 4315.1189 | 4191.7424 | 4102.014 | 4034.7177 | 3981.6964 | 3939.8911 | 3905.2234 | 3876.6734 | 3852.2021 | 3830.7896 | 3777.7683 | 3713.5309 | 3656.4311 | 3606.4687
Solar Thermal 8hrs | Murray River | NSW | NSW high | 4 Degrees | 6565.5659 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5890.2634 | 5880.1 | 5872.1951 | 5825.8951 | 5785.2415 | 5278.2 | 5083.9659 | 4981.2024 | 4779.0634 | 4642.422 | 4543.0463 | 4468.5146 | 4409.7927 | 4363.4927 | 4325.0976 | 4293.478 | 4266.3756 | 4242.661 | 4183.939 | 4112.7951 | 4049.5561 | 3994.222
Solar Thermal 8hrs | Eastern Eyre Peninsula | SA | SA medium | 4 Degrees | 6164.4073 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5520.8237 | 5513.4018 | 5469.9307 | 5431.761 | 4955.7 | 4773.3336 | 4676.8491 | 4487.0608 | 4358.7682 | 4265.4645 | 4195.4867 | 4140.3527 | 4096.8816 | 4060.8325 | 4031.1449 | 4005.6985 | 3983.4328 | 3928.2988 | 3861.5018 | 3802.1267 | 3750.1735
Solar Thermal 8hrs | Leigh Creek | SA | SA medium | 4 Degrees | 6164.4073 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5520.8237 | 5513.4018 | 5469.9307 | 5431.761 | 4955.7 | 4773.3336 | 4676.8491 | 4487.0608 | 4358.7682 | 4265.4645 | 4195.4867 | 4140.3527 | 4096.8816 | 4060.8325 | 4031.1449 | 4005.6985 | 3983.4328 | 3928.2988 | 3861.5018 | 3802.1267 | 3750.1735
Solar Thermal 8hrs | Northern South Australia | SA | SA medium | 4 Degrees | 6164.4073 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5520.8237 | 5513.4018 | 5469.9307 | 5431.761 | 4955.7 | 4773.3336 | 4676.8491 | 4487.0608 | 4358.7682 | 4265.4645 | 4195.4867 | 4140.3527 | 4096.8816 | 4060.8325 | 4031.1449 | 4005.6985 | 3983.4328 | 3928.2988 | 3861.5018 | 3802.1267 | 3750.1735
Solar Thermal 8hrs | Riverland (SA) | SA | SA Low | 4 Degrees | 5826.6878 | 5227.3828 | 5227.3828 | 5227.3828 | 5227.3828 | 5227.3828 | 5227.3828 | 5227.3828 | 5227.3828 | 5227.3828 | 5227.3828 | 5218.3632 | 5211.3479 | 5170.2584 | 5134.1798 | 4684.2 | 4511.8246 | 4420.6261 | 4241.2354 | 4119.9714 | 4031.7793 | 3965.6353 | 3913.5218 | 3872.4323 | 3838.3582 | 3810.297 | 3786.2447 | 3765.1988 | 3713.0854 | 3649.9479 | 3593.8257 | 3544.7187
Solar Thermal 8hrs | Roxby Downs | SA | SA medium | 4 Degrees | 6164.4073 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5520.8237 | 5513.4018 | 5469.9307 | 5431.761 | 4955.7 | 4773.3336 | 4676.8491 | 4487.0608 | 4358.7682 | 4265.4645 | 4195.4867 | 4140.3527 | 4096.8816 | 4060.8325 | 4031.1449 | 4005.6985 | 3983.4328 | 3928.2988 | 3861.5018 | 3802.1267 | 3750.1735
Solar Thermal 8hrs | Western Eyre Peninsula | SA | SA medium | 4 Degrees | 6164.4073 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5530.3661 | 5520.8237 | 5513.4018 | 5469.9307 | 5431.761 | 4955.7 | 4773.3336 | 4676.8491 | 4487.0608 | 4358.7682 | 4265.4645 | 4195.4867 | 4140.3527 | 4096.8816 | 4060.8325 | 4031.1449 | 4005.6985 | 3983.4328 | 3928.2988 | 3861.5018 | 3802.1267 | 3750.1735
Wind | Barcaldine | Qld | Qld medium | 4 Degrees | 2013.9447 | 1989.7319 | 1966.7375 | 1947.9298 | 1931.2715 | 1914.762 | 1900.3624 | 1886.0902 | 1874.8626 | 1863.7335 | 1852.7016 | 1841.7656 | 1830.9243 | 1819.2245 | 1795.3025 | 1764.9782 | 1754.6481 | 1744.4057 | 1734.2496 | 1724.1789 | 1714.1925 | 1703.3691 | 1693.5519 | 1683.8158 | 1675.0688 | 1665.4883 | 1656.8874 | 1648.3565 | 1639.0005 | 1628.8294 | 1618.74 | 1607.8479
Wind | Darling Downs | Qld | Qld low | 4 Degrees | 1891.4507 | 1868.7106 | 1847.1149 | 1829.451 | 1813.806 | 1798.3006 | 1784.7768 | 1771.3727 | 1760.828 | 1750.3758 | 1740.0149 | 1729.7441 | 1719.5622 | 1708.574 | 1686.107 | 1657.6271 | 1647.9254 | 1638.3059 | 1628.7675 | 1619.3094 | 1609.9304 | 1599.7652 | 1590.5452 | 1581.4013 | 1573.1862 | 1564.1885 | 1556.1107 | 1548.0987 | 1539.3118 | 1529.7593 | 1520.2836 | 1510.0539
Wind | Fitzroy | Qld | Qld low | 4 Degrees | 1891.4507 | 1868.7106 | 1847.1149 | 1829.451 | 1813.806 | 1798.3006 | 1784.7768 | 1771.3727 | 1760.828 | 1750.3758 | 1740.0149 | 1729.7441 | 1719.5622 | 1708.574 | 1686.107 | 1657.6271 | 1647.9254 | 1638.3059 | 1628.7675 | 1619.3094 | 1609.9304 | 1599.7652 | 1590.5452 | 1581.4013 | 1573.1862 | 1564.1885 | 1556.1107 | 1548.0987 | 1539.3118 | 1529.7593 | 1520.2836 | 1510.0539
Wind | Isaac | Qld | Qld low | 4 Degrees | 1891.4507 | 1868.7106 | 1847.1149 | 1829.451 | 1813.806 | 1798.3006 | 1784.7768 | 1771.3727 | 1760.828 | 1750.3758 | 1740.0149 | 1729.7441 | 1719.5622 | 1708.574 | 1686.107 | 1657.6271 | 1647.9254 | 1638.3059 | 1628.7675 | 1619.3094 | 1609.9304 | 1599.7652 | 1590.5452 | 1581.4013 | 1573.1862 | 1564.1885 | 1556.1107 | 1548.0987 | 1539.3118 | 1529.7593 | 1520.2836 | 1510.0539
Wind | North Queensland Clean Energy Hub | Qld | Qld medium | 4 Degrees | 2013.9447 | 1989.7319 | 1966.7375 | 1947.9298 | 1931.2715 | 1914.762 | 1900.3624 | 1886.0902 | 1874.8626 | 1863.7335 | 1852.7016 | 1841.7656 | 1830.9243 | 1819.2245 | 1795.3025 | 1764.9782 | 1754.6481 | 1744.4057 | 1734.2496 | 1724.1789 | 1714.1925 | 1703.3691 | 1693.5519 | 1683.8158 | 1675.0688 | 1665.4883 | 1656.8874 | 1648.3565 | 1639.0005 | 1628.8294 | 1618.74 | 1607.8479
Wind | Broken Hill | NSW | NSW high | 4 Degrees | 2131.0345 | 2105.4139 | 2081.0827 | 2061.1815 | 2043.5547 | 2026.0853 | 2010.8485 | 1995.7466 | 1983.8662 | 1972.0901 | 1960.4168 | 1948.845 | 1937.3734 | 1924.9933 | 1899.6806 | 1867.5932 | 1856.6626 | 1845.8246 | 1835.0781 | 1824.4219 | 1813.8549 | 1802.4022 | 1792.0142 | 1781.7121 | 1772.4565 | 1762.319 | 1753.2181 | 1744.1912 | 1734.2913 | 1723.5288 | 1712.8528 | 1701.3274
Wind | Central West New South Wales | NSW | NSW high | 4 Degrees | 2131.0345 | 2105.4139 | 2081.0827 | 2061.1815 | 2043.5547 | 2026.0853 | 2010.8485 | 1995.7466 | 1983.8662 | 1972.0901 | 1960.4168 | 1948.845 | 1937.3734 | 1924.9933 | 1899.6806 | 1867.5932 | 1856.6626 | 1845.8246 | 1835.0781 | 1824.4219 | 1813.8549 | 1802.4022 | 1792.0142 | 1781.7121 | 1772.4565 | 1762.319 | 1753.2181 | 1744.1912 | 1734.2913 | 1723.5288 | 1712.8528 | 1701.3274
Wind | Murray River (NSW) | Vic | NSW high | 4 Degrees | 1954.4991 | 1931.001 | 1908.6853 | 1890.4327 | 1874.2662 | 1858.2439 | 1844.2694 | 1830.4185 | 1819.5223 | 1808.7217 | 1798.0154 | 1787.4022 | 1776.8809 | 1765.5264 | 1742.3106 | 1712.8813 | 1702.8562 | 1692.9161 | 1683.0598 | 1673.2864 | 1663.5947 | 1653.0908 | 1643.5633 | 1634.1147 | 1625.6258 | 1616.3281 | 1607.9811 | 1599.702 | 1590.6222 | 1580.7513 | 1570.9597 | 1560.3891
Wind | North West New South Wales | NSW | NSW medium | 4 Degrees | 2022.0509 | 1997.7406 | 1974.6537 | 1955.7703 | 1939.045 | 1922.469 | 1908.0114 | 1893.6818 | 1882.409 | 1871.2351 | 1860.1588 | 1849.1788 | 1838.2938 | 1826.5469 | 1802.5287 | 1772.0823 | 1761.7107 | 1751.427 | 1741.2301 | 1731.1188 | 1721.0922 | 1710.2252 | 1700.3685 | 1690.5933 | 1681.811 | 1672.1919 | 1663.5565 | 1654.9912 | 1645.5976 | 1635.3855 | 1625.2555 | 1614.3196
Wind | New England | NSW | NSW low | 4 Degrees | 1913.0673 | 1890.0673 | 1868.2247 | 1850.3591 | 1834.5352 | 1818.8526 | 1805.1743 | 1791.617 | 1780.9518 | 1770.3801 | 1759.9008 | 1749.5126 | 1739.2143 | 1728.1005 | 1705.3768 | 1676.5714 | 1666.7588 | 1657.0294 | 1647.382 | 1637.8158 | 1628.3296 | 1618.0483 | 1608.7228 | 1599.4744 | 1591.1655 | 1582.0649 | 1573.8949 | 1565.7913 | 1556.9039 | 1547.2423 | 1537.6582 | 1527.3117
Wind | Riverland (NSW) | NSW | NSW high | 4 Degrees | 2131.0345 | 2105.4139 | 2081.0827 | 2061.1815 | 2043.5547 | 2026.0853 | 2010.8485 | 1995.7466 | 1983.8662 | 1972.0901 | 1960.4168 | 1948.845 | 1937.3734 | 1924.9933 | 1899.6806 | 1867.5932 | 1856.6626 | 1845.8246 | 1835.0781 | 1824.4219 | 1813.8549 | 1802.4022 | 1792.0142 | 1781.7121 | 1772.4565 | 1762.319 | 1753.2181 | 1744.1912 | 1734.2913 | 1723.5288 | 1712.8528 | 1701.3274
Wind | Southern New South Wales Tablelands | NSW | NSW low | 4 Degrees | 1913.0673 | 1890.0673 | 1868.2247 | 1850.3591 | 1834.5352 | 1818.8526 | 1805.1743 | 1791.617 | 1780.9518 | 1770.3801 | 1759.9008 | 1749.5126 | 1739.2143 | 1728.1005 | 1705.3768 | 1676.5714 | 1666.7588 | 1657.0294 | 1647.382 | 1637.8158 | 1628.3296 | 1618.0483 | 1608.7228 | 1599.4744 | 1591.1655 | 1582.0649 | 1573.8949 | 1565.7913 | 1556.9039 | 1547.2423 | 1537.6582 | 1527.3117
Wind | Gippsland | Vic | Vic medium | 4 Degrees | 1918.4714 | 1895.4065 | 1873.5022 | 1855.5861 | 1839.7175 | 1823.9906 | 1810.2736 | 1796.678 | 1785.9827 | 1775.3812 | 1764.8722 | 1754.4547 | 1744.1273 | 1732.9822 | 1710.1943 | 1681.3075 | 1671.4671 | 1661.7102 | 1652.0357 | 1642.4424 | 1632.9294 | 1622.619 | 1613.2672 | 1603.9927 | 1595.6603 | 1586.534 | 1578.3409 | 1570.2144 | 1561.3019 | 1551.613 | 1542.0019 | 1531.6261
Wind | Moyne | Vic | Vic medium | 4 Degrees | 1918.4714 | 1895.4065 | 1873.5022 | 1855.5861 | 1839.7175 | 1823.9906 | 1810.2736 | 1796.678 | 1785.9827 | 1775.3812 | 1764.8722 | 1754.4547 | 1744.1273 | 1732.9822 | 1710.1943 | 1681.3075 | 1671.4671 | 1661.7102 | 1652.0357 | 1642.4424 | 1632.9294 | 1622.619 | 1613.2672 | 1603.9927 | 1595.6603 | 1586.534 | 1578.3409 | 1570.2144 | 1561.3019 | 1551.613 | 1542.0019 | 1531.6261
Wind | Murray River | Vic | Vic high | 4 Degrees | 1954.4991 | 1931.001 | 1908.6853 | 1890.4327 | 1874.2662 | 1858.2439 | 1844.2694 | 1830.4185 | 1819.5223 | 1808.7217 | 1798.0154 | 1787.4022 | 1776.8809 | 1765.5264 | 1742.3106 | 1712.8813 | 1702.8562 | 1692.9161 | 1683.0598 | 1673.2864 | 1663.5947 | 1653.0908 | 1643.5633 | 1634.1147 | 1625.6258 | 1616.3281 | 1607.9811 | 1599.702 | 1590.6222 | 1580.7513 | 1570.9597 | 1560.3891
Wind | Western Victoria | Vic | Vic high | 4 Degrees | 1954.4991 | 1931.001 | 1908.6853 | 1890.4327 | 1874.2662 | 1858.2439 | 1844.2694 | 1830.4185 | 1819.5223 | 1808.7217 | 1798.0154 | 1787.4022 | 1776.8809 | 1765.5264 | 1742.3106 | 1712.8813 | 1702.8562 | 1692.9161 | 1683.0598 | 1673.2864 | 1663.5947 | 1653.0908 | 1643.5633 | 1634.1147 | 1625.6258 | 1616.3281 | 1607.9811 | 1599.702 | 1590.6222 | 1580.7513 | 1570.9597 | 1560.3891
Wind | Eastern Eyre Peninsula | SA | SA medium | 4 Degrees | 1986.9239 | 1963.036 | 1940.3502 | 1921.7948 | 1905.36 | 1889.072 | 1874.8655 | 1860.7849 | 1849.7079 | 1838.7281 | 1827.8442 | 1817.0549 | 1806.3591 | 1794.8163 | 1771.2153 | 1741.2978 | 1731.1063 | 1721.0013 | 1710.9815 | 1701.046 | 1691.1935 | 1680.5153 | 1670.8298 | 1661.2244 | 1652.5947 | 1643.1427 | 1634.6573 | 1626.2408 | 1617.0104 | 1606.9757 | 1597.0217 | 1586.2757
Wind | Leigh Creek | SA | SA medium | 4 Degrees | 1986.9239 | 1963.036 | 1940.3502 | 1921.7948 | 1905.36 | 1889.072 | 1874.8655 | 1860.7849 | 1849.7079 | 1838.7281 | 1827.8442 | 1817.0549 | 1806.3591 | 1794.8163 | 1771.2153 | 1741.2978 | 1731.1063 | 1721.0013 | 1710.9815 | 1701.046 | 1691.1935 | 1680.5153 | 1670.8298 | 1661.2244 | 1652.5947 | 1643.1427 | 1634.6573 | 1626.2408 | 1617.0104 | 1606.9757 | 1597.0217 | 1586.2757
Wind | Mid-North South Australia | SA | SA Low | 4 Degrees | 1869.8341 | 1847.3539 | 1826.005 | 1808.543 | 1793.0768 | 1777.7486 | 1764.3794 | 1751.1285 | 1740.7043 | 1730.3715 | 1720.129 | 1709.9756 | 1699.91 | 1689.0474 | 1666.8372 | 1638.6828 | 1629.0919 | 1619.5824 | 1610.1531 | 1600.803 | 1591.5312 | 1581.4822 | 1572.3675 | 1563.3281 | 1555.207 | 1546.312 | 1538.3266 | 1530.4062 | 1521.7196 | 1512.2763 | 1502.9089 | 1492.7962
Wind | Northern South Australia | SA | SA medium | 4 Degrees | 1986.9239 | 1963.036 | 1940.3502 | 1921.7948 | 1905.36 | 1889.072 | 1874.8655 | 1860.7849 | 1849.7079 | 1838.7281 | 1827.8442 | 1817.0549 | 1806.3591 | 1794.8163 | 1771.2153 | 1741.2978 | 1731.1063 | 1721.0013 | 1710.9815 | 1701.046 | 1691.1935 | 1680.5153 | 1670.8298 | 1661.2244 | 1652.5947 | 1643.1427 | 1634.6573 | 1626.2408 | 1617.0104 | 1606.9757 | 1597.0217 | 1586.2757
Wind | Riverland (SA) | SA | SA Low | 4 Degrees | 1869.8341 | 1847.3539 | 1826.005 | 1808.543 | 1793.0768 | 1777.7486 | 1764.3794 | 1751.1285 | 1740.7043 | 1730.3715 | 1720.129 | 1709.9756 | 1699.91 | 1689.0474 | 1666.8372 | 1638.6828 | 1629.0919 | 1619.5824 | 1610.1531 | 1600.803 | 1591.5312 | 1581.4822 | 1572.3675 | 1563.3281 | 1555.207 | 1546.312 | 1538.3266 | 1530.4062 | 1521.7196 | 1512.2763 | 1502.9089 | 1492.7962
Wind | South East South Australia | SA | SA medium | 4 Degrees | 1986.9239 | 1963.036 | 1940.3502 | 1921.7948 | 1905.36 | 1889.072 | 1874.8655 | 1860.7849 | 1849.7079 | 1838.7281 | 1827.8442 | 1817.0549 | 1806.3591 | 1794.8163 | 1771.2153 | 1741.2978 | 1731.1063 | 1721.0013 | 1710.9815 | 1701.046 | 1691.1935 | 1680.5153 | 1670.8298 | 1661.2244 | 1652.5947 | 1643.1427 | 1634.6573 | 1626.2408 | 1617.0104 | 1606.9757 | 1597.0217 | 1586.2757
Wind | Western Eyre Peninsula | SA | SA medium | 4 Degrees | 1986.9239 | 1963.036 | 1940.3502 | 1921.7948 | 1905.36 | 1889.072 | 1874.8655 | 1860.7849 | 1849.7079 | 1838.7281 | 1827.8442 | 1817.0549 | 1806.3591 | 1794.8163 | 1771.2153 | 1741.2978 | 1731.1063 | 1721.0013 | 1710.9815 | 1701.046 | 1691.1935 | 1680.5153 | 1670.8298 | 1661.2244 | 1652.5947 | 1643.1427 | 1634.6573 | 1626.2408 | 1617.0104 | 1606.9757 | 1597.0217 | 1586.2757
Wind | Yorke Peninsula | SA | SA Low | 4 Degrees | 1869.8341 | 1847.3539 | 1826.005 | 1808.543 | 1793.0768 | 1777.7486 | 1764.3794 | 1751.1285 | 1740.7043 | 1730.3715 | 1720.129 | 1709.9756 | 1699.91 | 1689.0474 | 1666.8372 | 1638.6828 | 1629.0919 | 1619.5824 | 1610.1531 | 1600.803 | 1591.5312 | 1581.4822 | 1572.3675 | 1563.3281 | 1555.207 | 1546.312 | 1538.3266 | 1530.4062 | 1521.7196 | 1512.2763 | 1502.9089 | 1492.7962
Wind | North East Tasmania | Tas | Tas high | 4 Degrees | 2095.9075 | 2070.7093 | 2046.7792 | 2027.206 | 2009.8698 | 1992.6883 | 1977.7027 | 1962.8497 | 1951.1651 | 1939.5831 | 1928.1022 | 1916.7212 | 1905.4386 | 1893.2627 | 1868.3671 | 1836.8087 | 1826.0582 | 1815.3989 | 1804.8296 | 1794.349 | 1783.9562 | 1772.6922 | 1762.4755 | 1752.3432 | 1743.2402 | 1733.2698 | 1724.3189 | 1715.4408 | 1705.704 | 1695.119 | 1684.619 | 1673.2836
Wind | North West Tasmania | Tas | Tas medium | 4 Degrees | 1989.626 | 1965.7056 | 1942.9889 | 1924.4083 | 1907.9511 | 1891.641 | 1877.4152 | 1863.3154 | 1852.2234 | 1841.2286 | 1830.3299 | 1819.526 | 1808.8156 | 1797.2571 | 1773.624 | 1743.6658 | 1733.4605 | 1723.3417 | 1713.3083 | 1703.3593 | 1693.4934 | 1682.8007 | 1673.102 | 1663.4835 | 1654.8421 | 1645.3773 | 1636.8803 | 1628.4524 | 1619.2094 | 1609.1611 | 1599.1935 | 1588.4329
Wind | Tasmania Midlands | Tas | Tas medium | 4 Degrees | 1989.626 | 1965.7056 | 1942.9889 | 1924.4083 | 1907.9511 | 1891.641 | 1877.4152 | 1863.3154 | 1852.2234 | 1841.2286 | 1830.3299 | 1819.526 | 1808.8156 | 1797.2571 | 1773.624 | 1743.6658 | 1733.4605 | 1723.3417 | 1713.3083 | 1703.3593 | 1693.4934 | 1682.8007 | 1673.102 | 1663.4835 | 1654.8421 | 1645.3773 | 1636.8803 | 1628.4524 | 1619.2094 | 1609.1611 | 1599.1935 | 1588.4329
Black Coal | Black Coal (supercritical PC) | QLD | Qld low | 4 Degrees | 3423.9713 | 3418.7069 | 3413.4425 | 3407.1252 | 3401.8608 | 3396.5964 | 3391.332 | 3386.0676 | 3380.8032 | 3374.4859 | 3369.2215 | 3363.9571 | 3358.6927 | 3353.4283 | 3348.1638 | 3342.8994 | 3337.635 | 3332.3706 | 3327.1062 | 3320.7889 | 3315.5245 | 3310.2601 | 3304.9957 | 3299.7313 | 3294.4669 | 3289.2025 | 3283.9381 | 3278.6736 | 3273.4092 | 3268.1448 | 3262.8804 | 3257.616
Black Coal | Black Coal (supercritical PC) | NSW | NSW low | 4 Degrees | 3454.94 | 3449.628 | 3444.316 | 3437.9416 | 3432.6295 | 3427.3175 | 3422.0055 | 3416.6935 | 3411.3814 | 3405.007 | 3399.695 | 3394.383 | 3389.0709 | 3383.7589 | 3378.4469 | 3373.1349 | 3367.8228 | 3362.5108 | 3357.1988 | 3350.8244 | 3345.5123 | 3340.2003 | 3334.8883 | 3329.5763 | 3324.2643 | 3318.9522 | 3313.6402 | 3308.3282 | 3303.0162 | 3297.7041 | 3292.3921 | 3287.0801
Black Coal with CCS | Black Coal (supercritical PC) with CCS | QLD | Qld low | 4 Degrees | 6358.3637 | 6350.9481 | 6343.5325 | 6336.1169 | 6328.7012 | 6322.345 | 6314.9294 | 6307.5138 | 6300.0981 | 6292.6825 | 6286.3263 | 6278.9107 | 6271.495 | 6264.0794 | 6257.7232 | 6250.3075 | 6242.8919 | 6229.1201 | 6034.1952 | 5950.5047 | 5845.6266 | 5747.1048 | 5652.8205 | 5616.8018 | 5607.2674 | 5589.2581 | 5577.605 | 5565.9518 | 5557.4768 | 5550.0612 | 5542.6456 | 5534.1706
Black Coal with CCS | Black Coal (supercritical PC) with CCS | NSW | NSW low | 4 Degrees | 6537.0625 | 6529.4385 | 6521.8144 | 6514.1904 | 6506.5664 | 6500.0315 | 6492.4075 | 6484.7834 | 6477.1594 | 6469.5354 | 6463.0005 | 6455.3764 | 6447.7524 | 6440.1284 | 6433.5935 | 6425.9695 | 6418.3454 | 6404.1865 | 6203.7834 | 6117.7408 | 6009.9152 | 5908.6245 | 5811.6904 | 5774.6593 | 5764.857 | 5746.3415 | 5734.3609 | 5722.3803 | 5713.6671 | 5706.0431 | 5698.419 | 5689.7058
Brown Coal | Brown Coal (supercritical PC) | Vic | Vic low | 4 Degrees | 5019.185 | 5011.1847 | 5003.1844 | 4995.1842 | 4987.1839 | 4979.1836 | 4971.1833 | 4963.183 | 4955.1827 | 4947.1824 | 4939.1821 | 4932.1818 | 4924.1815 | 4916.1812 | 4908.1809 | 4900.1807 | 4892.1804 | 4884.1801 | 4877.1798 | 4869.1795 | 4861.1792 | 4853.1789 | 4845.1786 | 4838.1784 | 4830.1781 | 4822.1778 | 4814.1775 | 4807.1772 | 4799.1769 | 4791.1766 | 4784.1764 | 4776.1761
Brown Coal with CCS | Brown Coal (supercritical PC) with CCS | Vic | Vic low | 4 Degrees | 9212.4115 | 9201.411 | 9189.4105 | 9178.41 | 9166.4095 | 9155.409 | 9144.4085 | 9132.4079 | 9121.4074 | 9110.407 | 9099.4065 | 9087.4059 | 9076.4054 | 9065.4049 | 9054.4045 | 9043.404 | 9032.4035 | 9012.4026 | 8785.3924 | 8685.388 | 8562.3825 | 8445.3772 | 8334.3723 | 8289.3703 | 8275.3697 | 8252.3686 | 8235.3679 | 8219.3672 | 8207.3666 | 8195.3661 | 8184.3656 | 8171.365
OCGT | OCGT | QLD | Qld low | 4 Degrees | 898.7384 | 896.7255 | 895.7191 | 894.7127 | 892.6998 | 891.6934 | 889.6805 | 888.6741 | 886.6613 | 885.6548 | 884.6484 | 882.6356 | 881.6291 | 879.6163 | 878.6099 | 877.6034 | 875.5906 | 874.5842 | 872.5713 | 871.5649 | 870.5585 | 868.5456 | 867.5392 | 866.5328 | 864.5199 | 863.5135 | 861.5006 | 860.4942 | 859.4878 | 857.4749 | 856.4685 | 855.4621
OCGT | OCGT | NSW | NSW low | 4 Degrees | 903.0045 | 900.9821 | 899.9709 | 898.9597 | 896.9373 | 895.9261 | 893.9037 | 892.8925 | 890.8701 | 889.8589 | 888.8477 | 886.8252 | 885.814 | 883.7916 | 882.7804 | 881.7692 | 879.7468 | 878.7356 | 876.7132 | 875.702 | 874.6908 | 872.6684 | 871.6572 | 870.646 | 868.6236 | 867.6124 | 865.59 | 864.5788 | 863.5676 | 861.5452 | 860.534 | 859.5228
OCGT | OCGT | SA | SA low | 4 Degrees | 894.4723 | 892.469 | 891.4673 | 890.4657 | 888.4624 | 887.4607 | 885.4574 | 884.4558 | 882.4525 | 881.4508 | 880.4492 | 878.4459 | 877.4442 | 875.4409 | 874.4393 | 873.4376 | 871.4343 | 870.4327 | 868.4294 | 867.4278 | 866.4261 | 864.4228 | 863.4212 | 862.4195 | 860.4162 | 859.4146 | 857.4113 | 856.4096 | 855.408 | 853.4047 | 852.403 | 851.4014
OCGT | OCGT | Tas | Tas low | 4 Degrees | 897.1392 | 895.13 | 894.1253 | 893.1207 | 891.1114 | 890.1068 | 888.0975 | 887.0929 | 885.0836 | 884.079 | 883.0743 | 881.0651 | 880.0604 | 878.0512 | 877.0465 | 876.0419 | 874.0326 | 873.028 | 871.0187 | 870.0141 | 869.0094 | 867.0002 | 865.9955 | 864.9909 | 862.9816 | 861.977 | 859.9677 | 858.9631 | 857.9585 | 855.9492 | 854.9445 | 853.9399
OCGT | OCGT | Vic | Vic low | 4 Degrees | 893.4057 | 891.4048 | 890.4044 | 889.4039 | 887.403 | 886.4026 | 884.4016 | 883.4012 | 881.4003 | 880.3998 | 879.3994 | 877.3985 | 876.398 | 874.3971 | 873.3967 | 872.3962 | 870.3953 | 869.3948 | 867.3939 | 866.3935 | 865.393 | 863.3921 | 862.3917 | 861.3912 | 859.3903 | 858.3898 | 856.3889 | 855.3885 | 854.388 | 852.3871 | 851.3867 | 850.3862
CCGT | CCGT | QLD | Qld low | 4 Degrees | 1284.5939 | 1282.5804 | 1280.5669 | 1278.5534 | 1276.54 | 1274.5265 | 1272.513 | 1270.4996 | 1268.4861 | 1266.4726 | 1264.4592 | 1262.4457 | 1260.4322 | 1258.4187 | 1256.4053 | 1254.3918 | 1252.3783 | 1250.3649 | 1248.3514 | 1246.3379 | 1244.3245 | 1242.311 | 1240.2975 | 1238.284 | 1236.2706 | 1234.2571 | 1232.2436 | 1230.2302 | 1228.2167 | 1226.2032 | 1224.1898 | 1222.1763
CCGT | CCGT | NSW | NSW low | 4 Degrees | 1291.4058 | 1289.3817 | 1287.3575 | 1285.3334 | 1283.3092 | 1281.2851 | 1279.261 | 1277.2368 | 1275.2127 | 1273.1885 | 1271.1644 | 1269.1402 | 1267.1161 | 1265.0919 | 1263.0678 | 1261.0436 | 1259.0195 | 1256.9953 | 1254.9712 | 1252.947 | 1250.9229 | 1248.8987 | 1246.8746 | 1244.8505 | 1242.8263 | 1240.8022 | 1238.778 | 1236.7539 | 1234.7297 | 1232.7056 | 1230.6814 | 1228.6573
CCGT | CCGT | SA | SA low | 4 Degrees | 1277.7819 | 1275.7791 | 1273.7763 | 1271.7735 | 1269.7707 | 1267.7679 | 1265.7651 | 1263.7623 | 1261.7595 | 1259.7567 | 1257.7539 | 1255.7511 | 1253.7484 | 1251.7456 | 1249.7428 | 1247.74 | 1245.7372 | 1243.7344 | 1241.7316 | 1239.7288 | 1237.726 | 1235.7232 | 1233.7204 | 1231.7176 | 1229.7148 | 1227.712 | 1225.7093 | 1223.7065 | 1221.7037 | 1219.7009 | 1217.6981 | 1215.6953
CCGT | CCGT | Tas | Tas low | 4 Degrees | 1282.04 | 1280.0306 | 1278.0211 | 1276.0116 | 1274.0022 | 1271.9927 | 1269.9832 | 1267.9738 | 1265.9643 | 1263.9548 | 1261.9454 | 1259.9359 | 1257.9264 | 1255.917 | 1253.9075 | 1251.898 | 1249.8886 | 1247.8791 | 1245.8696 | 1243.8602 | 1241.8507 | 1239.8412 | 1237.8318 | 1235.8223 | 1233.8128 | 1231.8034 | 1229.7939 | 1227.7844 | 1225.775 | 1223.7655 | 1221.756 | 1219.7466
CCGT | CCGT | Vic | Vic low | 4 Degrees | 1276.0789 | 1274.0788 | 1272.0786 | 1270.0785 | 1268.0784 | 1266.0783 | 1264.0781 | 1262.078 | 1260.0779 | 1258.0778 | 1256.0776 | 1254.0775 | 1252.0774 | 1250.0773 | 1248.0771 | 1246.077 | 1244.0769 | 1242.0768 | 1240.0766 | 1238.0765 | 1236.0764 | 1234.0763 | 1232.0762 | 1230.076 | 1228.0759 | 1226.0758 | 1224.0757 | 1222.0755 | 1220.0754 | 1218.0753 | 1216.0752 | 1214.075
CCGT with CCS | CCGT with CCS | QLD | Qld low | 4 Degrees | 4000.1475 | 3996.9736 | 3994.8577 | 3992.7418 | 3990.6259 | 3987.452 | 3985.3361 | 3983.2201 | 3980.0463 | 3977.9303 | 3975.8144 | 3973.6985 | 3970.5246 | 3968.4087 | 3966.2928 | 3964.1769 | 3961.003 | 3949.3654 | 3689.1072 | 3580.1373 | 3443.6604 | 3314.5893 | 3191.8659 | 3149.5475 | 3143.1997 | 3126.2724 | 3116.7507 | 3109.345 | 3105.1132 | 3101.9393 | 3098.7654 | 3093.4756
CCGT with CCS | CCGT with CCS | NSW | NSW low | 4 Degrees | 4175.411 | 4172.0981 | 4169.8894 | 4167.6808 | 4165.4722 | 4162.1592 | 4159.9506 | 4157.742 | 4154.429 | 4152.2204 | 4150.0118 | 4147.8032 | 4144.4902 | 4142.2816 | 4140.073 | 4137.8643 | 4134.5514 | 4122.4039 | 3850.7427 | 3736.9984 | 3594.5419 | 3459.8156 | 3331.7152 | 3287.5426 | 3280.9167 | 3263.2477 | 3253.3089 | 3245.5787 | 3241.1614 | 3237.8485 | 3234.5355 | 3229.014
CCGT with CCS | CCGT with CCS | SA | SA low | 4 Degrees | 3824.884 | 3821.8492 | 3819.826 | 3817.8028 | 3815.7796 | 3812.7447 | 3810.7215 | 3808.6983 | 3805.6635 | 3803.6403 | 3801.6171 | 3799.5939 | 3796.559 | 3794.5358 | 3792.5126 | 3790.4894 | 3787.4546 | 3776.3269 | 3527.4717 | 3423.2763 | 3292.779 | 3169.363 | 3052.0167 | 3011.5524 | 3005.4828 | 2989.2971 | 2980.1926 | 2973.1114 | 2969.065 | 2966.0301 | 2962.9953 | 2957.9373
CCGT with CCS | CCGT with CCS | Tas | Tas low | 4 Degrees | 3934.4244 | 3931.3027 | 3929.2215 | 3927.1404 | 3925.0592 | 3921.9375 | 3919.8563 | 3917.7752 | 3914.6534 | 3912.5723 | 3910.4911 | 3908.41 | 3905.2882 | 3903.2071 | 3901.1259 | 3899.0448 | 3895.923 | 3884.4767 | 3628.4946 | 3521.3151 | 3387.0805 | 3260.13 | 3139.423 | 3097.7999 | 3091.5565 | 3074.9072 | 3065.542 | 3058.258 | 3054.0957 | 3050.9739 | 3047.8522 | 3042.6493
CCGT with CCS | CCGT with CCS | Vic | Vic low | 4 Degrees | 3781.0681 | 3778.0681 | 3776.0681 | 3774.068 | 3772.068 | 3769.0679 | 3767.0679 | 3765.0679 | 3762.0678 | 3760.0678 | 3758.0677 | 3756.0677 | 3753.0676 | 3751.0676 | 3749.0676 | 3747.0675 | 3744.0675 | 3733.0673 | 3487.0628 | 3384.061 | 3255.0587 | 3133.0565 | 3017.0544 | 2977.0537 | 2971.0535 | 2955.0533 | 2946.0531 | 2939.053 | 2935.0529 | 2932.0528 | 2929.0528 | 2924.0527
Biomass | Biomass | QLD | Qld low | 4 Degrees | 13239.5149 | 13193.1603 | 13187.8927 | 13176.3041 | 13176.3041 | 13176.3041 | 13176.3041 | 13176.3041 | 13176.3041 | 13176.3041 | 13176.3041 | 13176.3041 | 13174.197 | 13174.197 | 13173.1435 | 13173.1435 | 13171.0365 | 13169.983 | 13169.983 | 13169.983 | 13169.983 | 13167.876 | 13161.5549 | 13161.5549 | 13161.5549 | 13161.5549 | 13161.5549 | 13161.5549 | 13110.9862 | 13029.8656 | 13001.4207 | 12921.3536
Biomass | Biomass | NSW | NSW low | 4 Degrees | 13777.4204 | 13729.1825 | 13723.7009 | 13711.6414 | 13711.6414 | 13711.6414 | 13711.6414 | 13711.6414 | 13711.6414 | 13711.6414 | 13711.6414 | 13711.6414 | 13709.4488 | 13709.4488 | 13708.3525 | 13708.3525 | 13706.1598 | 13705.0635 | 13705.0635 | 13705.0635 | 13705.0635 | 13702.8709 | 13696.293 | 13696.293 | 13696.293 | 13696.293 | 13696.293 | 13696.293 | 13643.6697 | 13559.2533 | 13529.6527 | 13446.3326
Biomass | Biomass | SA | SA low | 4 Degrees | 12701.6094 | 12657.1381 | 12652.0846 | 12640.9667 | 12640.9667 | 12640.9667 | 12640.9667 | 12640.9667 | 12640.9667 | 12640.9667 | 12640.9667 | 12640.9667 | 12638.9453 | 12638.9453 | 12637.9346 | 12637.9346 | 12635.9132 | 12634.9025 | 12634.9025 | 12634.9025 | 12634.9025 | 12632.881 | 12626.8168 | 12626.8168 | 12626.8168 | 12626.8168 | 12626.8168 | 12626.8168 | 12578.3026 | 12500.4779 | 12473.1887 | 12396.3746
Biomass | Biomass | Tas | Tas low | 4 Degrees | 13037.8004 | 12992.152 | 12986.9647 | 12975.5526 | 12975.5526 | 12975.5526 | 12975.5526 | 12975.5526 | 12975.5526 | 12975.5526 | 12975.5526 | 12975.5526 | 12973.4776 | 12973.4776 | 12972.4402 | 12972.4402 | 12970.3653 | 12969.3278 | 12969.3278 | 12969.3278 | 12969.3278 | 12967.2529 | 12961.0281 | 12961.0281 | 12961.0281 | 12961.0281 | 12961.0281 | 12961.0281 | 12911.2298 | 12831.3452 | 12803.3337 | 12724.4865
Biomass | Biomass | Vic | Vic low | 4 Degrees | 12567.133 | 12523.1326 | 12518.1325 | 12507.1324 | 12507.1324 | 12507.1324 | 12507.1324 | 12507.1324 | 12507.1324 | 12507.1324 | 12507.1324 | 12507.1324 | 12505.1324 | 12505.1324 | 12504.1324 | 12504.1324 | 12502.1323 | 12501.1323 | 12501.1323 | 12501.1323 | 12501.1323 | 12499.1323 | 12493.1323 | 12493.1323 | 12493.1323 | 12493.1323 | 12493.1323 | 12493.1323 | 12445.1317 | 12368.1309 | 12341.1306 | 12265.1298

## Storage Regional Build costs
Go to Assumptions Summary
Example storage build costs, after application of regional cost factors ($/kW, real 2019 dollars)
Example build cost for the 4 degrees scenario, for information purposes. Battery cost trajectories calculated by applying regional cost factors to base costs provided for a region-specific cost estimate.
Pumped hydro cost trajectories are derived from the Pumped Hydro regional capital cost estimates provided by Entura and capital cost projections given by CSIRO.
Solar thermal development costs are provided on the Generator Regional Build Costs sheet.
Storage Type | Region | Regional Cost Zone | Cost Scenario | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
Battery storage 2hrs | QLD | Qld low | 4 Degrees | 1496.5574 | 1408.4041 | 1363.3023 | 1305.9001 | 1250.548 | 1193.1458 | 1127.5433 | 1074.2412 | 1035.2897 | 1010.6888 | 996.3382 | 959.4368 | 959.4368 | 959.4368 | 957.3868 | 957.3868 | 957.3868 | 955.3367 | 955.3367 | 955.3367 | 943.0362 | 926.6356 | 926.6356 | 926.6356 | 926.6356 | 926.6356 | 926.6356 | 924.5855 | 924.5855 | 924.5855 | 924.5855 | 924.5855
Battery storage 2hrs | NSW | NSW low | 4 Degrees | 1525.8034 | 1435.9273 | 1389.9442 | 1331.4202 | 1274.9864 | 1216.4624 | 1149.5779 | 1095.2342 | 1055.5215 | 1030.4398 | 1015.8088 | 978.1863 | 978.1863 | 978.1863 | 976.0962 | 976.0962 | 976.0962 | 974.006 | 974.006 | 974.006 | 961.4652 | 944.744 | 944.744 | 944.744 | 944.744 | 944.744 | 944.744 | 942.6539 | 942.6539 | 942.6539 | 942.6539 | 942.6539
Battery storage 2hrs | SA | SA low | 4 Degrees | 1467.3115 | 1380.8808 | 1336.6605 | 1280.38 | 1226.1096 | 1169.8292 | 1105.5087 | 1053.2482 | 1015.0579 | 990.9378 | 976.8676 | 940.6874 | 940.6874 | 940.6874 | 938.6774 | 938.6774 | 938.6774 | 936.6673 | 936.6673 | 936.6673 | 924.6072 | 908.5271 | 908.5271 | 908.5271 | 908.5271 | 908.5271 | 908.5271 | 906.5171 | 906.5171 | 906.5171 | 906.5171 | 906.5171
Battery storage 2hrs | Tas | Tas low | 4 Degrees | 1485.5902 | 1398.0828 | 1353.3116 | 1296.3301 | 1241.3836 | 1184.4021 | 1119.2803 | 1066.3689 | 1027.7028 | 1003.2822 | 989.0368 | 952.4058 | 952.4058 | 952.4058 | 950.3707 | 950.3707 | 950.3707 | 948.3357 | 948.3357 | 948.3357 | 936.1253 | 919.8449 | 919.8449 | 919.8449 | 919.8449 | 919.8449 | 919.8449 | 917.8098 | 917.8098 | 917.8098 | 917.8098 | 917.8098
Battery storage 2hrs | Vic | Vic low | 4 Degrees | 1460 | 1374 | 1330 | 1274 | 1220 | 1164 | 1100 | 1048 | 1010 | 986 | 972 | 936 | 936 | 936 | 934 | 934 | 934 | 932 | 932 | 932 | 920 | 904 | 904 | 904 | 904 | 904 | 904 | 902 | 902 | 902 | 902 | 902
Pumped hydro 6 hrs | NSW | NSW | 4 Degrees | 1575.5179 | 1574.2028 | 1571.5725 | 1568.9423 | 1567.6272 | 1564.9969 | 1563.6818 | 1561.0515 | 1558.4213 | 1557.1062 | 1554.4759 | 1551.8457 | 1550.5306 | 1547.9003 | 1546.5852 | 1543.9549 | 1541.3247 | 1540.0096 | 1537.3793 | 1536.0642 | 1533.434 | 1530.8037 | 1529.4886 | 1526.8583 | 1525.5432 | 1522.913 | 1520.2827 | 1518.9676 | 1516.3373 | 1515.0222 | 1512.392 | 1511.0769
Pumped hydro 6 hrs | QLD | QLD | 4 Degrees | 1527.45 | 1526.175 | 1523.625 | 1521.075 | 1519.8 | 1517.25 | 1515.975 | 1513.425 | 1510.875 | 1509.6 | 1507.05 | 1504.5 | 1503.225 | 1500.675 | 1499.4 | 1496.85 | 1494.3 | 1493.025 | 1490.475 | 1489.2 | 1486.65 | 1484.1 | 1482.825 | 1480.275 | 1479 | 1476.45 | 1473.9 | 1472.625 | 1470.075 | 1468.8 | 1466.25 | 1464.975
Pumped hydro 6 hrs | SA | SA | 4 Degrees | 1926.7833 | 1925.175 | 1921.9583 | 1918.7417 | 1917.1333 | 1913.9167 | 1912.3083 | 1909.0917 | 1905.875 | 1904.2667 | 1901.05 | 1897.8333 | 1896.225 | 1893.0083 | 1891.4 | 1888.1833 | 1884.9667 | 1883.3583 | 1880.1417 | 1878.5333 | 1875.3167 | 1872.1 | 1870.4917 | 1867.275 | 1865.6667 | 1862.45 | 1859.2333 | 1857.625 | 1854.4083 | 1852.8 | 1849.5833 | 1847.975
Pumped hydro 6 hrs | Tas | Tas | 4 Degrees | 1158.0667 | 1157.1 | 1155.1667 | 1153.2333 | 1152.2667 | 1150.3333 | 1149.3667 | 1147.4333 | 1145.5 | 1144.5333 | 1142.6 | 1140.6667 | 1139.7 | 1137.7667 | 1136.8 | 1134.8667 | 1132.9333 | 1131.9667 | 1130.0333 | 1129.0667 | 1127.1333 | 1125.2 | 1124.2333 | 1122.3 | 1121.3333 | 1119.4 | 1117.4667 | 1116.5 | 1114.5667 | 1113.6 | 1111.6667 | 1110.7
Pumped hydro 6 hrs | Vic | Vic | 4 Degrees | 1527.45 | 1526.175 | 1523.625 | 1521.075 | 1519.8 | 1517.25 | 1515.975 | 1513.425 | 1510.875 | 1509.6 | 1507.05 | 1504.5 | 1503.225 | 1500.675 | 1499.4 | 1496.85 | 1494.3 | 1493.025 | 1490.475 | 1489.2 | 1486.65 | 1484.1 | 1482.825 | 1480.275 | 1479 | 1476.45 | 1473.9 | 1472.625 | 1470.075 | 1468.8 | 1466.25 | 1464.975
Pumped hydro 12 hrs | NSW | NSW | 4 Degrees | 1802.2853 | 1800.7809 | 1797.7721 | 1794.7632 | 1793.2588 | 1790.25 | 1788.7456 | 1785.7368 | 1782.7279 | 1781.2235 | 1778.2147 | 1775.2059 | 1773.7015 | 1770.6926 | 1769.1882 | 1766.1794 | 1763.1706 | 1761.6662 | 1758.6574 | 1757.1529 | 1754.1441 | 1751.1353 | 1749.6309 | 1746.6221 | 1745.1176 | 1742.1088 | 1739.1 | 1737.5956 | 1734.5868 | 1733.0824 | 1730.0735 | 1728.5691
Pumped hydro 12 hrs | QLD | QLD | 4 Degrees | 1826.95 | 1825.425 | 1822.375 | 1819.325 | 1817.8 | 1814.75 | 1813.225 | 1810.175 | 1807.125 | 1805.6 | 1802.55 | 1799.5 | 1797.975 | 1794.925 | 1793.4 | 1790.35 | 1787.3 | 1785.775 | 1782.725 | 1781.2 | 1778.15 | 1775.1 | 1773.575 | 1770.525 | 1769 | 1765.95 | 1762.9 | 1761.375 | 1758.325 | 1756.8 | 1753.75 | 1752.225
Pumped hydro 12 hrs | SA | SA | 4 Degrees | 2635.6 | 2633.4 | 2629 | 2624.6 | 2622.4 | 2618 | 2615.8 | 2611.4 | 2607 | 2604.8 | 2600.4 | 2596 | 2593.8 | 2589.4 | 2587.2 | 2582.8 | 2578.4 | 2576.2 | 2571.8 | 2569.6 | 2565.2 | 2560.8 | 2558.6 | 2554.2 | 2552 | 2547.6 | 2543.2 | 2541 | 2536.6 | 2534.4 | 2530 | 2527.8
Pumped hydro 12 hrs | Tas | Tas | 4 Degrees | 1277.8667 | 1276.8 | 1274.6667 | 1272.5333 | 1271.4667 | 1269.3333 | 1268.2667 | 1266.1333 | 1264 | 1262.9333 | 1260.8 | 1258.6667 | 1257.6 | 1255.4667 | 1254.4 | 1252.2667 | 1250.1333 | 1249.0667 | 1246.9333 | 1245.8667 | 1243.7333 | 1241.6 | 1240.5333 | 1238.4 | 1237.3333 | 1235.2 | 1233.0667 | 1232 | 1229.8667 | 1228.8 | 1226.6667 | 1225.6
Pumped hydro 12 hrs | Vic | Vic | 4 Degrees | 1747.0833 | 1745.625 | 1742.7083 | 1739.7917 | 1738.3333 | 1735.4167 | 1733.9583 | 1731.0417 | 1728.125 | 1726.6667 | 1723.75 | 1720.8333 | 1719.375 | 1716.4583 | 1715 | 1712.0833 | 1709.1667 | 1707.7083 | 1704.7917 | 1703.3333 | 1700.4167 | 1697.5 | 1696.0417 | 1693.125 | 1691.6667 | 1688.75 | 1685.8333 | 1684.375 | 1681.4583 | 1680 | 1677.0833 | 1675.625
Pumped hydro 24 hrs | NSW | NSW | 4 Degrees | 2115.1356 | 2113.37 | 2109.8389 | 2106.3078 | 2104.5422 | 2101.0111 | 2099.2456 | 2095.7144 | 2092.1833 | 2090.4178 | 2086.8867 | 2083.3556 | 2081.59 | 2078.0589 | 2076.2933 | 2072.7622 | 2069.2311 | 2067.4656 | 2063.9344 | 2062.1689 | 2058.6378 | 2055.1067 | 2053.3411 | 2049.81 | 2048.0444 | 2044.5133 | 2040.9822 | 2039.2167 | 2035.6856 | 2033.92 | 2030.3889 | 2028.6233
Pumped hydro 24 hrs | QLD | QLD | 4 Degrees | 2080.1636 | 2078.4273 | 2074.9545 | 2071.4818 | 2069.7455 | 2066.2727 | 2064.5364 | 2061.0636 | 2057.5909 | 2055.8545 | 2052.3818 | 2048.9091 | 2047.1727 | 2043.7 | 2041.9636 | 2038.4909 | 2035.0182 | 2033.2818 | 2029.8091 | 2028.0727 | 2024.6 | 2021.1273 | 2019.3909 | 2015.9182 | 2014.1818 | 2010.7091 | 2007.2364 | 2005.5 | 2002.0273 | 2000.2909 | 1996.8182 | 1995.0818
Pumped hydro 24 hrs | SA | SA | 4 Degrees | 3743.75 | 3740.625 | 3734.375 | 3728.125 | 3725 | 3718.75 | 3715.625 | 3709.375 | 3703.125 | 3700 | 3693.75 | 3687.5 | 3684.375 | 3678.125 | 3675 | 3668.75 | 3662.5 | 3659.375 | 3653.125 | 3650 | 3643.75 | 3637.5 | 3634.375 | 3628.125 | 3625 | 3618.75 | 3612.5 | 3609.375 | 3603.125 | 3600 | 3593.75 | 3590.625
Pumped hydro 24 hrs | Tas | Tas | 4 Degrees | 1387.6833 | 1386.525 | 1384.2083 | 1381.8917 | 1380.7333 | 1378.4167 | 1377.2583 | 1374.9417 | 1372.625 | 1371.4667 | 1369.15 | 1366.8333 | 1365.675 | 1363.3583 | 1362.2 | 1359.8833 | 1357.5667 | 1356.4083 | 1354.0917 | 1352.9333 | 1350.6167 | 1348.3 | 1347.1417 | 1344.825 | 1343.6667 | 1341.35 | 1339.0333 | 1337.875 | 1335.5583 | 1334.4 | 1332.0833 | 1330.925
Pumped hydro 24 hrs | Vic | Vic | 4 Degrees | 2246.25 | 2244.375 | 2240.625 | 2236.875 | 2235 | 2231.25 | 2229.375 | 2225.625 | 2221.875 | 2220 | 2216.25 | 2212.5 | 2210.625 | 2206.875 | 2205 | 2201.25 | 2197.5 | 2195.625 | 2191.875 | 2190 | 2186.25 | 2182.5 | 2180.625 | 2176.875 | 2175 | 2171.25 | 2167.5 | 2165.625 | 2161.875 | 2160 | 2156.25 | 2154.375
Pumped hydro 48 hrs | NSW | NSW | 4 Degrees | 2508.0352 | 2505.9417 | 2501.7546 | 2497.5676 | 2495.4741 | 2491.287 | 2489.1935 | 2485.0065 | 2480.8194 | 2478.7259 | 2474.5389 | 2470.3519 | 2468.2583 | 2464.0713 | 2461.9778 | 2457.7907 | 2453.6037 | 2451.5102 | 2447.3231 | 2445.2296 | 2441.0426 | 2436.8556 | 2434.762 | 2430.575 | 2428.4815 | 2424.2944 | 2420.1074 | 2418.0139 | 2413.8269 | 2411.7333 | 2407.5463 | 2405.4528
Pumped hydro 48 hrs | QLD | QLD | 4 Degrees | 2939.0933 | 2936.64 | 2931.7333 | 2926.8267 | 2924.3733 | 2919.4667 | 2917.0133 | 2912.1067 | 2907.2 | 2904.7467 | 2899.84 | 2894.9333 | 2892.48 | 2887.5733 | 2885.12 | 2880.2133 | 2875.3067 | 2872.8533 | 2867.9467 | 2865.4933 | 2860.5867 | 2855.68 | 2853.2267 | 2848.32 | 2845.8667 | 2840.96 | 2836.0533 | 2833.6 | 2828.6933 | 2826.24 | 2821.3333 | 2818.88
Pumped hydro 48 hrs | SA | SA | 4 Degrees | bar: 2018-19 to 2049-50
Pumped hydro 48 hrs | Tas | Tas | 4 Degrees | 1567.3833 | 1566.075 | 1563.4583 | 1560.8417 | 1559.5333 | 1556.9167 | 1555.6083 | 1552.9917 | 1550.375 | 1549.0667 | 1546.45 | 1543.8333 | 1542.525 | 1539.9083 | 1538.6 | 1535.9833 | 1533.3667 | 1532.0583 | 1529.4417 | 1528.1333 | 1525.5167 | 1522.9 | 1521.5917 | 1518.975 | 1517.6667 | 1515.05 | 1512.4333 | 1511.125 | 1508.5083 | 1507.2 | 1504.5833 | 1503.275
Pumped hydro 48 hrs | Vic | Vic | 4 Degrees | 3374.3667 | 3371.55 | 3365.9167 | 3360.2833 | 3357.4667 | 3351.8333 | 3349.0167 | 3343.3833 | 3337.75 | 3334.9333 | 3329.3 | 3323.6667 | 3320.85 | 3315.2167 | 3312.4 | 3306.7667 | 3301.1333 | 3298.3167 | 3292.6833 | 3289.8667 | 3284.2333 | 3278.6 | 3275.7833 | 3270.15 | 3267.3333 | 3261.7 | 3256.0667 | 3253.25 | 3247.6167 | 3244.8 | 3239.1667 | 3236.35

## Connection cost
Go to Assumptions Summary
Initial connection costs ($/kW) real 2019 dollars
Connection costs increase the build costs of new technologies to cater for transmission infrasturcture to connect to the grid, and varies depending on the proximity to transmission assets
Final connection costs will be subject to modelling outcomes
Renewable Energy Zone | Wind/Solar | Battery | NEM Region | Gas1 | Black Coal (USC) | Biomass | Batteries | Pumped hydro
Far North Queensland | 98.0068 | 10 | QLD | 82.18 | 42.72 | 98.01 | 10 | 98.01
North Queensland Clean Energy Hub | 111.322 | 10 | NSW | 86.5457 | 53.87 | 85.51 | 10 | 85.51
Northern Queensland | 98.0068 | 10 | VIC | 73.4587 |  | 100.05 | 10 | 100.05
Isaac | 98.0068 | 10 | SA | 82.18 | - | 98.01 | 10 | 98.01
Barcaldine | 111.322 | 10 | TAS | 73.4587 | - | 100.05 | 10 | 100.09
Fitzroy | 98.0068 | 10
Darling Downs | 98.0068 | 10
North West New South Wales | 85.5075 | 10 |  | 1. The physical location of these regional connections will depend on fuel / network infrastructure
New England | 85.5075 | 10
Central West New South Wales | 85.5075 | 10
Southern New South Wales Tablelands | 75.5212 | 10
Cooma-Monaro | 75.5212 | 10
Tumut | 75.5212 | 10
South West New South Wales | 85.5075 | 10
Broken Hill | 108.0433 | 10
Murray River | 100.0542 | 10
Western Victoria | 100.0542 | 10
Moyne | 71.4751 | 10
Ovens Murray | 100.0542 | 10
Gippsland | 108.0433 | 10
South East South Australia | 111.322 | 10
Riverland | 111.322 | 10
Mid-North South Australia | 98.0068 | 10
Yorke Peninsula | 98.0068 | 10
Northern South Australia | 98.0068 | 10
Leigh Creek | 111.322 | 10
Roxby Downs | 111.322 | 10
Eastern Eyre Peninsula | 111.322 | 10
Western Eyre Peninsula | 111.322 | 10
North West Tasmania | 100.0542 | 10
Tasmania Midlands | 100.0542 | 10
North East Tasmania | 100.0542 | 10

## Build limits
Go to Assumptions Summary
Initial Build limits (MW)
Potential in each NEM region to build different thermal and storage capacities; potential in each zone to build new renewable energy capacity
The new renewable energy capacity in each REZ zone will be moderated by transmission expansion choices in each scenario, loss factor impacts, etc
REZ # | Location | Region | NTNDP zone | Wind generation limits (MW) |  | Solar PV plus Solar thermal Limits (MW)1 | Pumped Hydro Limits (MW)2 |  |  |  | Battery Storage 2hrs (MW) | OCGT (MW) | CCGT (MW) | Biomass (MW) | Coal without CCS (MW) | Coal with CCS (MW) | Nuclear (SMR) (MW) | Transmission-limited total build in the REZ3 | Indicative transmission expansion cost ($M/MW Real 2019)4 | Additional generation capacity available (zero additional cost) in REZs due to the development of interconnectors
|  |  |  | High | Medium | Solar | 6hrs storage | 12hrs storage | 24hrs storage | 48hrs storage | [9 empty] | QNI Option 2 | QNI Option 3B | QNI Option 3C | QNI Option 3D | VNI Option 5 | VNI Option 6 | VNI Option 7 | VNI Option 8 | SA-NSW | VIC-TAS Option 1 | VIC-TAS Option 2
1 | Far North Queensland | QLD | NQ | 0 | 0 | 0 | [11 empty] | 700 | 1.1787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | North Queensland Clean Energy Hub | QLD | NQ | 2320 | 6955 | 3982 | [11 empty] | 0 | 1.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Northern Queensland | QLD | NQ | 0 | 0 | 1650 | [11 empty] | 2400 (note 5) | 0.88867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Isaac | QLD | NQ | 465 | 1395 | 3500 | [11 empty] | 2700 (note 6) | 0.68368 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Barcaldine | QLD | CQ | 475 | 1435 | 4000 | [11 empty] | 0 | 0.95222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Fitzroy | QLD | CQ | 220 | 670 | 2000 | [11 empty] | 2900 (note 7) | 0.5125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Darling Downs | QLD | SWQ | 695 | 2090 | 3743 | [11 empty] | 2743 | 0.17117 | 600 | 1200 | 1200 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | North West New South Wales | NSW | NNS | 200 | 615 | 3250 | [11 empty] | 100 | 0.29212 | 0 | 0 | 0 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | New England | NSW | NNS | 900 | 2760 | 1750 | [11 empty] | 300 | 0.29212 | 600 | 1200 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | Central West New South Wales | NSW | NCEN | 620 | 2265 | 6546.6 | [11 empty] | 0 | 0.29212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | Southern New South Wales Tablelands | NSW | CAN | 575 | 1735 | 1000 | [11 empty] | 1000 | 0.2296 | 0 | 0 | 0 | 0 | 0 | 2000 | 1000 | 2000 | 0 | 0 | 0
12 | Cooma-Monaro | NSW | CAN | 0 | 0 | 0 | [11 empty] | 200 | NA (note 8) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | Tumut | NSW | CAN | 0 | 0 | 0 | [11 empty] | 0 | NA (note 8) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | South West New South Wales | NSW | SWNSW | 530 | 1570 | 2142 | [11 empty] | 0 | 0.533 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 1000 | 600 | 0 | 0
15 | Broken Hill | NSW | SWNSW | 620 | 1870 | 4000 | [11 empty] | 100 | 0.6765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
16 | Murray River (VIC) | VIC | CVIC | 530 | 1570 | 2561.13 | [11 empty] | 0 | 0.3854 | 0 | 0 | 0 | 0 | 0 | 1000 | 2000 | 0 | 380 | 0 | 0
17 | Western Victoria | VIC | CVIC | 0 | 1042 | 0 | [11 empty] | 450 (note 9) | 0.205 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0
18 | Moyne | VIC | MEL | 0 | 1469.7 | 0 | [11 empty] | 1175 | 0.08815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | Ovens Murray | VIC | NVIC | 0 | 0 | 0 | [11 empty] | 300 | NA (note 8) | 0 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0
20 | Gippsland | VIC | LV | 35 | 105 | 0 | [11 empty] | 2000 | NA (note 8) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | South East South Australia | SA | SESA | 455 | 1355 | 0 | [11 empty] | 500 | 0.25625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | Riverland (NSW) | NSW | SWNSW | 155 | 465 | 2000 | [11 empty] | 0 | 0.533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 0
23 | Mid-North South Australia | SA | ADE | 605 | 1820 | 0 | [11 empty] | 1000 | 0.25625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | Yorke Peninsula | SA | NSA | 155 | 465 | 0 | [11 empty] | 50 | 0.12812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | Northern South Australia | SA | NSA | 0 | 0 | 1500 | [11 empty] | 1000 (see note 10) | 0.25625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | Leigh Creek | SA | NSA | 295 | 895 | 3250 | [11 empty] | 10 (see note 10) | 0.5125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | Roxby Downs | SA | NSA | 0 | 0 | 1700 | [11 empty] | 960 (see note 10) | 0.30032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | Eastern Eyre Peninsula | SA | NSA | 290 | 870 | 2500 | [11 empty] | 500 (see note 10) | 0.38437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | Western Eyre Peninsula | SA | NSA | 175 | 540 | 2000 | [11 empty] | 0 (see note 10) | 0.38437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | North West Tasmania | TAS | TAS | 388.4 | 1500 | 0 | [11 empty] | 88.4 | 0.12402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 2000
31 | Tasmania Midlands | TAS | TAS | 286 | 1300 | 0 | [11 empty] | 856 | 0.07175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | North East Tasmania | TAS | TAS | 75 | 230 | 0 | [11 empty] | 0 | 0.2296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| NSW11 | NSW |  |  |  |  | 7000 |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA
| QLD | QLD |  |  |  |  | 500 | 500 | 550 | 250 | NA | NA | NA | NA | NA | NA | NA | NA | NA
| SA | SA |  |  |  |  | 300 | 100 | 100 | 0 | NA | NA | NA | NA | NA | NA | NA | NA | NA
| TAS | TAS |  |  |  |  | 400 | 600 | 800 | 400 | NA | NA | NA | NA | NA | NA | NA | NA | NA
| VIC | VIC |  |  |  |  | 250 | 400 | 350 | 200 | NA | NA | NA | NA | NA | NA | NA | NA | NA
Notes:
1. Solar build limit determined by an assumed 0.25% of the approximate land area of the Renewable Energy Zones, allowing for typical land area requirements for solar PV, up to 4,000MW per REZ. Applies to both CST and PV.
2. Pumped hydro build limits are based on Entura report
3. Intraregional transmission augmentations may be selected by the model if economic to access larger new renewable resource locations
4. Indicative transmission cost represents indicative network expansion to connect the REZ to the nearest major load centre.
5. 2400 MW includes total build capacity in REZs 1, 2 and 3 in the existing network.
6. 2700 MW includes total build capacity in REZs 1,2,3 and 4 in the existing network.
7. 2900 MW includes total build capacity in REZs 1,2,3, 4, 5 and 6 in the existing network.
8. Available wind and solar resource capacity is less than the existing transmission capacity.
9. Western Victoria RIT-T augmentation included.
10. Existing network can accommodate up to 1600 MW from REZs 25, 26, 27, 28 and 29.
11. Pump Hydro limits based on 24 energy projects identified in the NSW Government Pumped Hydro Roadmap. AEMO will continue to refine limits based on discussions with relevant stakeholders. Total value excludes the contribution of the proposed Snowy 2.0 project. http://re100.eng.anu.edu.au/research/re/site/nsw.php

## Capacity Factors
Go to Assumptions Summary
Capacity Factors for new solar and wind generators
Approximate capacity factors of renewable resources. Capacity factors depend on the 'reference year' modelled - estimates below are for 2013-14 reference year.
Capacity factors are static for all installations. No capacity factor improvement / degradation due to technology improvement / natural reduction in best installation sites, however for wind farms the expected capacity factor improvement through time is reflected in capital cost reductions.
REZ Name | Region | Solar |  | Wind
|  | Solar PV | Solar Thermal | High | Low
North Queensland Clean Energy Hub | QLD | 29.86% | 41.79% | 51.44% | 40.47%
Northern Queensland | QLD | 29.09% | 34.37% | - | -
Barcaldine | QLD | 32.29% | 45.16% | 42.27% | 35.48%
Isaac | QLD | 28.34% | 33.44% | 48.17% | 36.28%
Fitzroy | QLD | 30.89% | 39.04% | 43.72% | 35.17%
Darling Downs | QLD | 31.9% | 40.07% | 43.86% | 37.73%
North West New South Wales | NSW | 30.8% | 40.64% | 24.82% | 24.85%
New England | NSW | 31.38% | 38.84% | 35.95% | 36.97%
Central West New South Wales | NSW | 30.28% | 39.51% | 33.59% | 29.63%
Southern New South Wales Tablelands | NSW | - | - | 44.44% | 42.93%
Murray River (NSW) | NSW | 28.25% | 33.07% | 33.87% | 31.76%
Murray River (VIC) | VIC | 28.25% | 33.07% | 33.87% | 31.76%
Riverland (NSW) | NSW | 28.75% | 34.09% | 33.34% | 32.44%
Riverland (SA) | SA | 28.75% | 34.09% | 33.34% | 32.44%
Broken Hill | NSW | 32.23% | 44.2% | 37.62% | 33.31%
Western Victoria | VIC | - | - | 46.3% | 36.28%
Moyne | VIC | - | - | 41.46% | 41.63%
Gippsland | VIC | - | - | 35% | 34.45%
South East South Australia | SA | - | - | 41.9% | 38.47%
Mid-North South Australia | SA | - | - | 41.91% | 40.23%
Yorke Peninsula | SA | - | - | 40.7% | 38.57%
Northern South Australia | SA | 29.86% | 36.74% | 37.1% | 37.17%
Leigh Creek | SA | 31.87% | 44.01% | 40.59% | 40.52%
Roxby Downs | SA | 31.78% | 41.82% | - | -
Eastern Eyre Peninsula | SA | 27.71% | 29.39% | 41.88% | 39.87%
Western Eyre Peninsula | SA | 28.76% | 33.23% | 39.67% | 36.12%
North East Tasmania | TAS | - | - | 46.04% | 45.16%
North West Tasmania | TAS | - | - | 50.87% | 44.23%
Tasmania Midlands | TAS | - | - | 53.42% | 46.9%

## Lead Time
Go to Assumptions Summary
Lead time
Development lead time considers the time necessary to undertake feasibility studies, secure necessary development approvals, and to construct the project. For capacity planning therefore, the lead time reflects the shortest time before a technology can commence operation.
GHD have provided lead time as a combination of lead time for feasibility and construction time. These values have been adjusted for some technologies to reflect the degree of active development interest, as demonstrated by the projects proposed, advancing or committed in AEMO's Generation Information page, particularly for OCGT, Wind and Solar technologies.
Technology | Feasibility Period (years) | Construction Time (years) 2 | Total lead time (years)
Black Coal (supercritical PC) | 4 | 4 | 8
Black Coal (supercritical PC) with CCS | 10 | 4 | 14
Brown Coal (supercritical PC) | 4 | 4 | 8
Brown Coal (supercritical PC) with CCS | 10 | 4 | 14
OCGT 1 | 0 | 1 | 1
CCGT | 3 | 2 | 5
CCGT with CCS | 10 | 2 | 12
Biomass | 3 | 2 | 5
Large scale Solar PV 1 | 0 | 1 | 1
Solar Thermal (8hrs Storage) | 3 | 3 | 6
Nuclear (SMR) | 10 | 5 | 15
Battery storage (2 hrs) | 1 | 1 | 2
Wind 1 | 0 | 2 | 2
Pumped hydro (6 hrs storage) | 2 | 4 | 6
Note 1: Given existing development activity in these technologies, AEMO has removed the development lead time for these technologies as stated by GHD. The total lead time therefore reflects the construction time only.
Note 2: GHD has provided construction time in weeks. AEMO has converted this time to years, and rounded up to the nearest whole year for capacity planning.

## Storage properties
Go to Assumptions Summary
Battery properties
Property | Value
Maximum power1 | 1 | MW
Energy capacity | 2 | MWh
Charge efficiency (household) | 90%
Charge efficiency (utility) | 81%
Economic life | 15 | years
Technical life | 10 | years
1. Power and capacity are defined as a 1:2 ratio. The model is free to build utility-scale batteries up to defined build limits
Pumped hydro properties
Property | Value
Maximum power | 100 | MW
Energy capacity | 6 | hours
Pump efficiency | 77.5%
Economic life | 50 | years
Technical life | 30 | years
Note:
1. Data on economic life and technical life of batteries and pumped hydro plants are from the GHD 2018 AEMO costs and technical parameter review. GHD has assumed that economic life refers to the design life of a plant and the technical life of a plant is the elapsed time between first commercial operation and decommissioning.
2. Both Economic life and technical life and are applied only for the batteries in the capacity expansion planning models as both technical life and economic life of batteries are less than the planning horizon.

## Coal and Biomass price
Go to Assumptions Summary
Coal price ($/GJ, real 2019 dollars)
Existing generators: 2016 Wood Mackenzie Coal Cost Report New entrants: Resources and Energy Quarterly (June 2018) report, Department of Industry, Innovation and Science (AEMO conversions).
Generator | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41
Bayswater | 1.6605 | 1.7527 | 1.7527 | 1.7732 | 1.8347 | 1.886 | 1.9577 | 1.9577 | 2.1525 | 2.583 | 2.8597 | 3.0032 | 3.116 | 3.157 | 3.2082 | 3.2595 | 3.3415 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825
Eraring | 2.6855 | 2.8802 | 3.0545 | 3.1262 | 3.1775 | 3.2595 | 3.4235 | 3.567 | 3.5977 | 3.7002 | 3.8335 | 3.977 | 4.0693 | 4.1307 | 4.2025 | 4.2742 | 4.3767 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428
Liddell | 1.6605 | 1.7527 | 1.7527 | 1.7732 | 1.8347 | 1.886 | 1.9577 | 1.9577 | 2.1525 | 2.583 | 2.8597 | 3.0032 | 3.116 | 3.157 | 3.2082 | 3.2595 | 3.3415 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825 | 3.3825
Mount Piper | 2.2857 | 2.46 | 2.583 | 2.6342 | 2.706 | 2.7675 | 2.9212 | 3.034 | 3.1262 | 3.28 | 3.4132 | 3.567 | 3.69 | 3.7515 | 3.7925 | 3.8437 | 3.9257 | 3.9872 | 3.9872 | 3.9872 | 3.9872 | 3.9872 | 3.9872
Vales Point | 2.5727 | 2.7675 | 2.952 | 3.0135 | 3.1775 | 3.2595 | 3.4235 | 3.567 | 3.5977 | 3.7002 | 3.8335 | 3.977 | 4.0693 | 4.1307 | 4.2025 | 4.2742 | 4.3767 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428 | 4.428
Callide B | 2.1935 | 2.2447 | 2.2857 | 2.3267 | 2.3472 | 2.3678 | 2.3882 | 2.4395 | 2.4805 | 2.4907 | 2.5215 | 2.5522 | 2.6035 | 2.8802 | 3.1262 | 3.1877 | 3.2697 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107
Callide Power Plant | 2.1935 | 2.2447 | 2.2857 | 2.3267 | 2.3472 | 2.3678 | 2.3882 | 2.4395 | 2.4805 | 2.4907 | 2.5215 | 2.5522 | 2.6035 | 2.8802 | 3.1262 | 3.1877 | 3.2697 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107 | 3.3107
Gladstone | 2.624 | 2.8802 | 3.0237 | 3.075 | 3.157 | 3.2287 | 3.3927 | 3.526 | 3.5568 | 3.6182 | 3.731 | 3.8847 | 3.9872 | 4.0385 | 4.1 | 4.182 | 4.2742 | 4.3255 | 4.3255 | 4.3255 | 4.3255 | 4.3255 | 4.3255
Kogan Creek | 1.6707 | 1.681 | 1.681 | 1.681 | 1.7015 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722 | 1.722
Millmerran | 1.3735 | 1.3735 | 1.394 | 1.394 | 1.4042 | 1.4247 | 1.4247 | 1.4247 | 1.4247 | 1.4247 | 1.4247 | 1.4247 | 1.4247 | 1.4247 | 1.435 | 1.435 | 1.435 | 1.435 | 1.435 | 1.435 | 1.4452 | 1.4452 | 1.4452
Stanwell | 2.46 | 2.542 | 2.6035 | 2.6342 | 2.665 | 2.6855 | 2.706 | 2.7265 | 2.8905 | 3.28 | 3.5875 | 3.7412 | 3.8745 | 3.9257 | 3.9872 | 4.0488 | 4.1615 | 4.2025 | 4.2025 | 4.2025 | 4.2025 | 4.2025 | 4.2025
Tarong | 3.0032 | 3.0135 | 3.0237 | 3.0237 | 3.0442 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648
Tarong North | 3.0032 | 3.0135 | 3.0237 | 3.0237 | 3.0442 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648
Loy Yang A | 0.66625 | 0.697 | 0.697 | 0.697 | 0.697 | 0.70725 | 0.70725 | 0.70725 | 0.70725 | 0.7175 | 0.7175 | 0.7175 | 0.72775 | 0.72775 | 0.738 | 0.738 | 0.7585 | 0.7585 | 0.76875 | 0.76875 | 0.779 | 0.78925 | 0.78925
Loy Yang B | 0.66625 | 0.697 | 0.697 | 0.697 | 0.697 | 0.70725 | 0.70725 | 0.70725 | 0.70725 | 0.7175 | 0.7175 | 0.7175 | 0.72775 | 0.72775 | 0.738 | 0.738 | 0.7585 | 0.7585 | 0.76875 | 0.76875 | 0.779 | 0.78925 | 0.78925
Yallourn | 0.66625 | 0.6765 | 0.68675 | 0.68675 | 0.697 | 0.697 | 0.697 | 0.697 | 0.70725 | 0.70725 | 0.70725 | 0.7175 | 0.7175 | 0.7175 | 0.72775 | 0.72775 | 0.738 | 0.738 | 0.7585 | 0.7585 | 0.76875 | 0.779 | 0.779
New entrant coal | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41
Lower estimate | 3.0135 | 3.0237 | 3.0237 | 3.0442 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648 | 3.0648
Central estimate | 5.125 | 4.3767 | 4.059 | 4.059 | 4.059 | 4.059 | 4.059 | 4.059 | 4.059 | 4.059 | 4.059 | 4.059 | 4.059 | 4.059 | 4.059 | 4.059 | 4.059 | 4.059 | 4.059 | 4.059 | 4.059 | 4.059 | 4.059
*Lower estimate equivalent to estimated contract price paid by existing generators in QLD
*Central estimate equivalent to forecast export coal price, as per June 2018 Resources and Energy Quarterly report, converted to AU$/GJ - @6000kCal/kg, 1USD=0.75AUD).
Biomass price | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41
Biomass | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53

## Gas and Liquid fuel price
Go to Assumptions Summary
Gas price ($/GJ, real 2019 dollars)
Prices are the sum of wholesale price and transportation cost.
Based on December 2018 "Delivered Wholesale Gas price Outlook 2019-2040" by Core Energy & Resources Pty Limited
Neutral
Generator | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
Bairnsdale | 9.6186 | 10.0064 | 9.475 | 8.9841 | 9.5157 | 9.6558 | 9.5189 | 10.0494 | 10.5664 | 10.7813 | 11.1783 | 11.4779 | 11.9204 | 12.3162 | 12.2085 | 12.1289 | 12.0423 | 11.9401 | 11.9535 | 12.0239 | 12.019 | 12
Barcaldine | 9.0286 | 9.4164 | 8.885 | 8.3941 | 8.9257 | 9.0658 | 8.9289 | 9.4594 | 9.9764 | 10.1913 | 10.5883 | 10.8879 | 11.3304 | 11.7262 | 11.6185 | 11.5389 | 11.4523 | 11.3501 | 11.3635 | 11.4339 | 11.429 | 11.41
Bell Bay Three | 10.5686 | 10.9564 | 10.425 | 9.9341 | 10.4657 | 10.6058 | 10.4689 | 10.9994 | 11.5164 | 11.7313 | 12.1283 | 12.4279 | 12.8704 | 13.2662 | 13.1585 | 13.0789 | 12.9923 | 12.8901 | 12.9035 | 12.9739 | 12.969 | 12.95
Braemar | 9.0286 | 9.4164 | 8.885 | 8.3941 | 8.9257 | 9.0658 | 8.9289 | 9.4594 | 9.9764 | 10.1913 | 10.5883 | 10.8879 | 11.3304 | 11.7262 | 11.6185 | 11.5389 | 11.4523 | 11.3501 | 11.3635 | 11.4339 | 11.429 | 11.41
Braemar 2 | 9.0286 | 9.4164 | 8.885 | 8.3941 | 8.9257 | 9.0658 | 8.9289 | 9.4594 | 9.9764 | 10.1913 | 10.5883 | 10.8879 | 11.3304 | 11.7262 | 11.6185 | 11.5389 | 11.4523 | 11.3501 | 11.3635 | 11.4339 | 11.429 | 11.41
Colongra | 10.1386 | 10.5264 | 9.995 | 9.5041 | 10.0357 | 10.1758 | 10.0389 | 10.5694 | 11.0864 | 11.3013 | 11.6983 | 11.9979 | 12.4404 | 12.8362 | 12.7285 | 12.6489 | 12.5623 | 12.4601 | 12.4735 | 12.5439 | 12.539 | 12.52
Condamine | 9.3286 | 9.7164 | 9.185 | 8.6941 | 9.2257 | 9.3658 | 9.2289 | 9.7594 | 10.2764 | 10.4913 | 10.8883 | 11.1879 | 11.6304 | 12.0262 | 11.9185 | 11.8389 | 11.7523 | 11.6501 | 11.6635 | 11.7339 | 11.729 | 11.71
Darling Downs | 8.8286 | 9.2164 | 8.685 | 8.1941 | 8.7257 | 8.8658 | 8.7289 | 9.2594 | 9.7764 | 9.9913 | 10.3883 | 10.6879 | 11.1304 | 11.5262 | 11.4185 | 11.3389 | 11.2523 | 11.1501 | 11.1635 | 11.2339 | 11.229 | 11.21
Dry Creek | 9.7986 | 10.1864 | 9.655 | 9.1641 | 9.6957 | 9.8358 | 9.6989 | 10.2294 | 10.7464 | 10.9613 | 11.3583 | 11.6579 | 12.1004 | 12.4962 | 12.3885 | 12.3089 | 12.2223 | 12.1201 | 12.1335 | 12.2039 | 12.199 | 12.18
Hallett | 9.7986 | 10.1864 | 9.655 | 9.1641 | 9.6957 | 9.8358 | 9.6989 | 10.2294 | 10.7464 | 10.9613 | 11.3583 | 11.6579 | 12.1004 | 12.4962 | 12.3885 | 12.3089 | 12.2223 | 12.1201 | 12.1335 | 12.2039 | 12.199 | 12.18
Jeeralang | 9.1186 | 9.5064 | 8.975 | 8.4841 | 9.0157 | 9.1558 | 9.0189 | 9.5494 | 10.0664 | 10.2813 | 10.6783 | 10.9779 | 11.4204 | 11.8162 | 11.7085 | 11.6289 | 11.5423 | 11.4401 | 11.4535 | 11.5239 | 11.519 | 11.5
Ladbroke Grove | 9.7986 | 10.1864 | 9.655 | 9.1641 | 9.6957 | 9.8358 | 9.6989 | 10.2294 | 10.7464 | 10.9613 | 11.3583 | 11.6579 | 12.1004 | 12.4962 | 12.3885 | 12.3089 | 12.2223 | 12.1201 | 12.1335 | 12.2039 | 12.199 | 12.18
Laverton North | 9.6186 | 10.0064 | 9.475 | 8.9841 | 9.5157 | 9.6558 | 9.5189 | 10.0494 | 10.5664 | 10.7813 | 11.1783 | 11.4779 | 11.9204 | 12.3162 | 12.2085 | 12.1289 | 12.0423 | 11.9401 | 11.9535 | 12.0239 | 12.019 | 12
Mintaro | 9.7986 | 10.1864 | 9.655 | 9.1641 | 9.6957 | 9.8358 | 9.6989 | 10.2294 | 10.7464 | 10.9613 | 11.3583 | 11.6579 | 12.1004 | 12.4962 | 12.3885 | 12.3089 | 12.2223 | 12.1201 | 12.1335 | 12.2039 | 12.199 | 12.18
Mortlake OCGT | 8.9186 | 9.3064 | 8.775 | 8.2841 | 8.8157 | 8.9558 | 8.8189 | 9.3494 | 9.8664 | 10.0813 | 10.4783 | 10.7779 | 11.2204 | 11.6162 | 11.5085 | 11.4289 | 11.3423 | 11.2401 | 11.2535 | 11.3239 | 11.319 | 11.3
Newport | 9.6186 | 10.0064 | 9.475 | 8.9841 | 9.5157 | 9.6558 | 9.5189 | 10.0494 | 10.5664 | 10.7813 | 11.1783 | 11.4779 | 11.9204 | 12.3162 | 12.2085 | 12.1289 | 12.0423 | 11.9401 | 11.9535 | 12.0239 | 12.019 | 12
Oakey | 9.3286 | 9.7164 | 9.185 | 8.6941 | 9.2257 | 9.3658 | 9.2289 | 9.7594 | 10.2764 | 10.4913 | 10.8883 | 11.1879 | 11.6304 | 12.0262 | 11.9185 | 11.8389 | 11.7523 | 11.6501 | 11.6635 | 11.7339 | 11.729 | 11.71
Osborne | 8.7986 | 9.1864 | 8.655 | 8.1641 | 8.6957 | 8.8358 | 8.6989 | 9.2294 | 9.7464 | 9.9613 | 10.3583 | 10.6579 | 11.1004 | 11.4962 | 11.3885 | 11.3089 | 11.2223 | 11.1201 | 11.1335 | 11.2039 | 11.199 | 11.18
Pelican Point | 9.2986 | 9.6864 | 9.155 | 8.6641 | 9.1957 | 9.3358 | 9.1989 | 9.7294 | 10.2464 | 10.4613 | 10.8583 | 11.1579 | 11.6004 | 11.9962 | 11.8885 | 11.8089 | 11.7223 | 11.6201 | 11.6335 | 11.7039 | 11.699 | 11.68
Quarantine | 9.5486 | 9.9364 | 9.405 | 8.9141 | 9.4457 | 9.5858 | 9.4489 | 9.9794 | 10.4964 | 10.7113 | 11.1083 | 11.4079 | 11.8504 | 12.2462 | 12.1385 | 12.0589 | 11.9723 | 11.8701 | 11.8835 | 11.9539 | 11.949 | 11.93
Roma | 9.3286 | 9.7164 | 9.185 | 8.6941 | 9.2257 | 9.3658 | 9.2289 | 9.7594 | 10.2764 | 10.4913 | 10.8883 | 11.1879 | 11.6304 | 12.0262 | 11.9185 | 11.8389 | 11.7523 | 11.6501 | 11.6635 | 11.7339 | 11.729 | 11.71
Smithfield | 10.1386 | 10.5264 | 9.995 | 9.5041 | 10.0357 | 10.1758 | 10.0389 | 10.5694 | 11.0864 | 11.3013 | 11.6983 | 11.9979 | 12.4404 | 12.8362 | 12.7285 | 12.6489 | 12.5623 | 12.4601 | 12.4735 | 12.5439 | 12.539 | 12.52
Somerton | 9.6186 | 10.0064 | 9.475 | 8.9841 | 9.5157 | 9.6558 | 9.5189 | 10.0494 | 10.5664 | 10.7813 | 11.1783 | 11.4779 | 11.9204 | 12.3162 | 12.2085 | 12.1289 | 12.0423 | 11.9401 | 11.9535 | 12.0239 | 12.019 | 12
Swanbank E | 9.3286 | 9.7164 | 9.185 | 8.6941 | 9.2257 | 9.3658 | 9.2289 | 9.7594 | 10.2764 | 10.4913 | 10.8883 | 11.1879 | 11.6304 | 12.0262 | 11.9185 | 11.8389 | 11.7523 | 11.6501 | 11.6635 | 11.7339 | 11.729 | 11.71
Tallawarra | 9.6386 | 10.0264 | 9.495 | 9.0041 | 9.5357 | 9.6758 | 9.5389 | 10.0694 | 10.5864 | 10.8013 | 11.1983 | 11.4979 | 11.9404 | 12.3362 | 12.2285 | 12.1489 | 12.0623 | 11.9601 | 11.9735 | 12.0439 | 12.039 | 12.02
Tamar Valley | 10.5686 | 10.9564 | 10.425 | 9.9341 | 10.4657 | 10.6058 | 10.4689 | 10.9994 | 11.5164 | 11.7313 | 12.1283 | 12.4279 | 12.8704 | 13.2662 | 13.1585 | 13.0789 | 12.9923 | 12.8901 | 12.9035 | 12.9739 | 12.969 | 12.95
Torrens Island | 9.7986 | 10.1864 | 9.655 | 9.1641 | 9.6957 | 9.8358 | 9.6989 | 10.2294 | 10.7464 | 10.9613 | 11.3583 | 11.6579 | 12.1004 | 12.4962 | 12.3885 | 12.3089 | 12.2223 | 12.1201 | 12.1335 | 12.2039 | 12.199 | 12.18
Townsville | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
Uranquinty | 9.8886 | 10.2764 | 9.745 | 9.2541 | 9.7857 | 9.9258 | 9.7889 | 10.3194 | 10.8364 | 11.0513 | 11.4483 | 11.7479 | 12.1904 | 12.5862 | 12.4785 | 12.3989 | 12.3123 | 12.2101 | 12.2235 | 12.2939 | 12.289 | 12.27
Valley Power | 9.6186 | 10.0064 | 9.475 | 8.9841 | 9.5157 | 9.6558 | 9.5189 | 10.0494 | 10.5664 | 10.7813 | 11.1783 | 11.4779 | 11.9204 | 12.3162 | 12.2085 | 12.1289 | 12.0423 | 11.9401 | 11.9535 | 12.0239 | 12.019 | 12
Yarwun | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
QLD new OCGT | 10.3286 | 10.7164 | 10.185 | 9.6941 | 10.2257 | 10.3658 | 10.2289 | 10.7594 | 11.2764 | 11.4913 | 11.8883 | 12.1879 | 12.6304 | 13.0262 | 12.9185 | 12.8389 | 12.7523 | 12.6501 | 12.6635 | 12.7339 | 12.729 | 12.71
NSW new OCGT | 11.1386 | 11.5264 | 10.995 | 10.5041 | 11.0357 | 11.1758 | 11.0389 | 11.5694 | 12.0864 | 12.3013 | 12.6983 | 12.9979 | 13.4404 | 13.8362 | 13.7285 | 13.6489 | 13.5623 | 13.4601 | 13.4735 | 13.5439 | 13.539 | 13.52
VIC new OCGT | 10.6186 | 11.0064 | 10.475 | 9.9841 | 10.5157 | 10.6558 | 10.5189 | 11.0494 | 11.5664 | 11.7813 | 12.1783 | 12.4779 | 12.9204 | 13.3162 | 13.2085 | 13.1289 | 13.0423 | 12.9401 | 12.9535 | 13.0239 | 13.019 | 13
SA new OCGT | 10.7986 | 11.1864 | 10.655 | 10.1641 | 10.6957 | 10.8358 | 10.6989 | 11.2294 | 11.7464 | 11.9613 | 12.3583 | 12.6579 | 13.1004 | 13.4962 | 13.3885 | 13.3089 | 13.2223 | 13.1201 | 13.1335 | 13.2039 | 13.199 | 13.18
TAS new OCGT | 11.2686 | 11.6564 | 11.125 | 10.6341 | 11.1657 | 11.3058 | 11.1689 | 11.6994 | 12.2164 | 12.4313 | 12.8283 | 13.1279 | 13.5704 | 13.9662 | 13.8585 | 13.7789 | 13.6923 | 13.5901 | 13.6035 | 13.6739 | 13.669 | 13.65
QLD new CCGT | 8.8286 | 9.2164 | 8.685 | 8.1941 | 8.7257 | 8.8658 | 8.7289 | 9.2594 | 9.7764 | 9.9913 | 10.3883 | 10.6879 | 11.1304 | 11.5262 | 11.4185 | 11.3389 | 11.2523 | 11.1501 | 11.1635 | 11.2339 | 11.229 | 11.21
NSW new CCGT | 9.6386 | 10.0264 | 9.495 | 9.0041 | 9.5357 | 9.6758 | 9.5389 | 10.0694 | 10.5864 | 10.8013 | 11.1983 | 11.4979 | 11.9404 | 12.3362 | 12.2285 | 12.1489 | 12.0623 | 11.9601 | 11.9735 | 12.0439 | 12.039 | 12.02
VIC new CCGT | 9.1186 | 9.5064 | 8.975 | 8.4841 | 9.0157 | 9.1558 | 9.0189 | 9.5494 | 10.0664 | 10.2813 | 10.6783 | 10.9779 | 11.4204 | 11.8162 | 11.7085 | 11.6289 | 11.5423 | 11.4401 | 11.4535 | 11.5239 | 11.519 | 11.5
SA new CCGT | 9.7986 | 10.1864 | 9.655 | 9.1641 | 9.6957 | 9.8358 | 9.6989 | 10.2294 | 10.7464 | 10.9613 | 11.3583 | 11.6579 | 12.1004 | 12.4962 | 12.3885 | 12.3089 | 12.2223 | 12.1201 | 12.1335 | 12.2039 | 12.199 | 12.18
TAS new CCGT | 10.7686 | 11.1564 | 10.625 | 10.1341 | 10.6657 | 10.8058 | 10.6689 | 11.1994 | 11.7164 | 11.9313 | 12.3283 | 12.6279 | 13.0704 | 13.4662 | 13.3585 | 13.2789 | 13.1923 | 13.0901 | 13.1035 | 13.1739 | 13.169 | 13.15
Fast Change
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
Bairnsdale | 9.6186 | 10.0064 | 9.475 | 8.9841 | 9.4606 | 9.6007 | 9.5189 | 9.9908 | 10.4475 | 10.6594 | 11.0509 | 11.2823 | 11.6486 | 11.9661 | 11.7946 | 11.6536 | 11.5067 | 11.41 | 11.3603 | 11.3645 | 11.3599 | 11.3421
Barcaldine | 8.8286 | 9.2164 | 8.685 | 8.1941 | 8.6706 | 8.8107 | 8.7289 | 9.2008 | 9.6575 | 9.8694 | 10.2609 | 10.4923 | 10.8586 | 11.1761 | 11.0046 | 10.8636 | 10.7167 | 10.62 | 10.5703 | 10.5745 | 10.5699 | 10.5521
Bell Bay Three | 10.8686 | 11.2564 | 10.725 | 10.2341 | 10.7106 | 10.8507 | 10.7689 | 11.2408 | 11.6975 | 11.9094 | 12.3009 | 12.5323 | 12.8986 | 13.2161 | 13.0446 | 12.9036 | 12.7567 | 12.66 | 12.6103 | 12.6145 | 12.6099 | 12.5921
Braemar | 8.8286 | 9.2164 | 8.685 | 8.1941 | 8.6706 | 8.8107 | 8.7289 | 9.2008 | 9.6575 | 9.8694 | 10.2609 | 10.4923 | 10.8586 | 11.1761 | 11.0046 | 10.8636 | 10.7167 | 10.62 | 10.5703 | 10.5745 | 10.5699 | 10.5521
Braemar 2 | 8.8286 | 9.2164 | 8.685 | 8.1941 | 8.6706 | 8.8107 | 8.7289 | 9.2008 | 9.6575 | 9.8694 | 10.2609 | 10.4923 | 10.8586 | 11.1761 | 11.0046 | 10.8636 | 10.7167 | 10.62 | 10.5703 | 10.5745 | 10.5699 | 10.5521
Colongra | 10.1386 | 10.5264 | 9.995 | 9.5041 | 9.9806 | 10.1207 | 10.0389 | 10.5108 | 10.9675 | 11.1794 | 11.5709 | 11.8023 | 12.1686 | 12.4861 | 12.3146 | 12.1736 | 12.0267 | 11.93 | 11.8803 | 11.8845 | 11.8799 | 11.8621
Condamine | 9.3286 | 9.7164 | 9.185 | 8.6941 | 9.1706 | 9.3107 | 9.2289 | 9.7008 | 10.1575 | 10.3694 | 10.7609 | 10.9923 | 11.3586 | 11.6761 | 11.5046 | 11.3636 | 11.2167 | 11.12 | 11.0703 | 11.0745 | 11.0699 | 11.0521
Darling Downs | 8.6286 | 9.0164 | 8.485 | 7.9941 | 8.4706 | 8.6107 | 8.5289 | 9.0008 | 9.4575 | 9.6694 | 10.0609 | 10.2923 | 10.6586 | 10.9761 | 10.8046 | 10.6636 | 10.5167 | 10.42 | 10.3703 | 10.3745 | 10.3699 | 10.3521
Dry Creek | 9.7986 | 10.1864 | 9.655 | 9.1641 | 9.6406 | 9.7807 | 9.6989 | 10.1708 | 10.6275 | 10.8394 | 11.2309 | 11.4623 | 11.8286 | 12.1461 | 11.9746 | 11.8336 | 11.6867 | 11.59 | 11.5403 | 11.5445 | 11.5399 | 11.5221
Hallett | 9.7986 | 10.1864 | 9.655 | 9.1641 | 9.6406 | 9.7807 | 9.6989 | 10.1708 | 10.6275 | 10.8394 | 11.2309 | 11.4623 | 11.8286 | 12.1461 | 11.9746 | 11.8336 | 11.6867 | 11.59 | 11.5403 | 11.5445 | 11.5399 | 11.5221
Jeeralang | 9.1186 | 9.5064 | 8.975 | 8.4841 | 8.9606 | 9.1007 | 9.0189 | 9.4908 | 9.9475 | 10.1594 | 10.5509 | 10.7823 | 11.1486 | 11.4661 | 11.2946 | 11.1536 | 11.0067 | 10.91 | 10.8603 | 10.8645 | 10.8599 | 10.8421
Ladbroke Grove | 9.7986 | 10.1864 | 9.655 | 9.1641 | 9.6406 | 9.7807 | 9.6989 | 10.1708 | 10.6275 | 10.8394 | 11.2309 | 11.4623 | 11.8286 | 12.1461 | 11.9746 | 11.8336 | 11.6867 | 11.59 | 11.5403 | 11.5445 | 11.5399 | 11.5221
Laverton North | 9.6186 | 10.0064 | 9.475 | 8.9841 | 9.4606 | 9.6007 | 9.5189 | 9.9908 | 10.4475 | 10.6594 | 11.0509 | 11.2823 | 11.6486 | 11.9661 | 11.7946 | 11.6536 | 11.5067 | 11.41 | 11.3603 | 11.3645 | 11.3599 | 11.3421
Mintaro | 9.7986 | 10.1864 | 9.655 | 9.1641 | 9.6406 | 9.7807 | 9.6989 | 10.1708 | 10.6275 | 10.8394 | 11.2309 | 11.4623 | 11.8286 | 12.1461 | 11.9746 | 11.8336 | 11.6867 | 11.59 | 11.5403 | 11.5445 | 11.5399 | 11.5221
Mortlake OCGT | 8.9186 | 9.3064 | 8.775 | 8.2841 | 8.7606 | 8.9007 | 8.8189 | 9.2908 | 9.7475 | 9.9594 | 10.3509 | 10.5823 | 10.9486 | 11.2661 | 11.0946 | 10.9536 | 10.8067 | 10.71 | 10.6603 | 10.6645 | 10.6599 | 10.6421
Newport | 9.6186 | 10.0064 | 9.475 | 8.9841 | 9.4606 | 9.6007 | 9.5189 | 9.9908 | 10.4475 | 10.6594 | 11.0509 | 11.2823 | 11.6486 | 11.9661 | 11.7946 | 11.6536 | 11.5067 | 11.41 | 11.3603 | 11.3645 | 11.3599 | 11.3421
Oakey | 9.3286 | 9.7164 | 9.185 | 8.6941 | 9.1706 | 9.3107 | 9.2289 | 9.7008 | 10.1575 | 10.3694 | 10.7609 | 10.9923 | 11.3586 | 11.6761 | 11.5046 | 11.3636 | 11.2167 | 11.12 | 11.0703 | 11.0745 | 11.0699 | 11.0521
Osborne | 8.7986 | 9.1864 | 8.655 | 8.1641 | 8.6406 | 8.7807 | 8.6989 | 9.1708 | 9.6275 | 9.8394 | 10.2309 | 10.4623 | 10.8286 | 11.1461 | 10.9746 | 10.8336 | 10.6867 | 10.59 | 10.5403 | 10.5445 | 10.5399 | 10.5221
Pelican Point | 9.2986 | 9.6864 | 9.155 | 8.6641 | 9.1406 | 9.2807 | 9.1989 | 9.6708 | 10.1275 | 10.3394 | 10.7309 | 10.9623 | 11.3286 | 11.6461 | 11.4746 | 11.3336 | 11.1867 | 11.09 | 11.0403 | 11.0445 | 11.0399 | 11.0221
Quarantine | 9.5486 | 9.9364 | 9.405 | 8.9141 | 9.3906 | 9.5307 | 9.4489 | 9.9208 | 10.3775 | 10.5894 | 10.9809 | 11.2123 | 11.5786 | 11.8961 | 11.7246 | 11.5836 | 11.4367 | 11.34 | 11.2903 | 11.2945 | 11.2899 | 11.2721
Roma | 9.3286 | 9.7164 | 9.185 | 8.6941 | 9.1706 | 9.3107 | 9.2289 | 9.7008 | 10.1575 | 10.3694 | 10.7609 | 10.9923 | 11.3586 | 11.6761 | 11.5046 | 11.3636 | 11.2167 | 11.12 | 11.0703 | 11.0745 | 11.0699 | 11.0521
Smithfield | 10.6386 | 11.0264 | 10.495 | 10.0041 | 10.4806 | 10.6207 | 10.5389 | 11.0108 | 11.4675 | 11.6794 | 12.0709 | 12.3023 | 12.6686 | 12.9861 | 12.8146 | 12.6736 | 12.5267 | 12.43 | 12.3803 | 12.3845 | 12.3799 | 12.3621
Somerton | 9.6186 | 10.0064 | 9.475 | 8.9841 | 9.4606 | 9.6007 | 9.5189 | 9.9908 | 10.4475 | 10.6594 | 11.0509 | 11.2823 | 11.6486 | 11.9661 | 11.7946 | 11.6536 | 11.5067 | 11.41 | 11.3603 | 11.3645 | 11.3599 | 11.3421
Swanbank E | 9.3286 | 9.7164 | 9.185 | 8.6941 | 9.1706 | 9.3107 | 9.2289 | 9.7008 | 10.1575 | 10.3694 | 10.7609 | 10.9923 | 11.3586 | 11.6761 | 11.5046 | 11.3636 | 11.2167 | 11.12 | 11.0703 | 11.0745 | 11.0699 | 11.0521
Tallawarra | 9.8886 | 10.2764 | 9.745 | 9.2541 | 9.7306 | 9.8707 | 9.7889 | 10.2608 | 10.7175 | 10.9294 | 11.3209 | 11.5523 | 11.9186 | 12.2361 | 12.0646 | 11.9236 | 11.7767 | 11.68 | 11.6303 | 11.6345 | 11.6299 | 11.6121
Tamar Valley | 10.5686 | 10.9564 | 10.425 | 9.9341 | 10.4106 | 10.5507 | 10.4689 | 10.9408 | 11.3975 | 11.6094 | 12.0009 | 12.2323 | 12.5986 | 12.9161 | 12.7446 | 12.6036 | 12.4567 | 12.36 | 12.3103 | 12.3145 | 12.3099 | 12.2921
Torrens Island | 9.7986 | 10.1864 | 9.655 | 9.1641 | 9.6406 | 9.7807 | 9.6989 | 10.1708 | 10.6275 | 10.8394 | 11.2309 | 11.4623 | 11.8286 | 12.1461 | 11.9746 | 11.8336 | 11.6867 | 11.59 | 11.5403 | 11.5445 | 11.5399 | 11.5221
Townsville | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
Uranquinty | 9.8886 | 10.2764 | 9.745 | 9.2541 | 9.7306 | 9.8707 | 9.7889 | 10.2608 | 10.7175 | 10.9294 | 11.3209 | 11.5523 | 11.9186 | 12.2361 | 12.0646 | 11.9236 | 11.7767 | 11.68 | 11.6303 | 11.6345 | 11.6299 | 11.6121
Valley Power | 9.6186 | 10.0064 | 9.475 | 8.9841 | 9.4606 | 9.6007 | 9.5189 | 9.9908 | 10.4475 | 10.6594 | 11.0509 | 11.2823 | 11.6486 | 11.9661 | 11.7946 | 11.6536 | 11.5067 | 11.41 | 11.3603 | 11.3645 | 11.3599 | 11.3421
Yarwun | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
QLD new OCGT | 10.3286 | 10.7164 | 10.185 | 9.6941 | 10.1706 | 10.3107 | 10.2289 | 10.7008 | 11.1575 | 11.3694 | 11.7609 | 11.9923 | 12.3586 | 12.6761 | 12.5046 | 12.3636 | 12.2167 | 12.12 | 12.0703 | 12.0745 | 12.0699 | 12.0521
NSW new OCGT | 11.1386 | 11.5264 | 10.995 | 10.5041 | 10.9806 | 11.1207 | 11.0389 | 11.5108 | 11.9675 | 12.1794 | 12.5709 | 12.8023 | 13.1686 | 13.4861 | 13.3146 | 13.1736 | 13.0267 | 12.93 | 12.8803 | 12.8845 | 12.8799 | 12.8621
VIC new OCGT | 10.6186 | 11.0064 | 10.475 | 9.9841 | 10.4606 | 10.6007 | 10.5189 | 10.9908 | 11.4475 | 11.6594 | 12.0509 | 12.2823 | 12.6486 | 12.9661 | 12.7946 | 12.6536 | 12.5067 | 12.41 | 12.3603 | 12.3645 | 12.3599 | 12.3421
SA new OCGT | 10.7986 | 11.1864 | 10.655 | 10.1641 | 10.6406 | 10.7807 | 10.6989 | 11.1708 | 11.6275 | 11.8394 | 12.2309 | 12.4623 | 12.8286 | 13.1461 | 12.9746 | 12.8336 | 12.6867 | 12.59 | 12.5403 | 12.5445 | 12.5399 | 12.5221
TAS new OCGT | 10.5686 | 10.9564 | 10.425 | 9.9341 | 10.4106 | 10.5507 | 10.4689 | 10.9408 | 11.3975 | 11.6094 | 12.0009 | 12.2323 | 12.5986 | 12.9161 | 12.7446 | 12.6036 | 12.4567 | 12.36 | 12.3103 | 12.3145 | 12.3099 | 12.2921
QLD new CCGT | 8.8286 | 9.2164 | 8.685 | 8.1941 | 8.6706 | 8.8107 | 8.7289 | 9.2008 | 9.6575 | 9.8694 | 10.2609 | 10.4923 | 10.8586 | 11.1761 | 11.0046 | 10.8636 | 10.7167 | 10.62 | 10.5703 | 10.5745 | 10.5699 | 10.5521
NSW new CCGT | 9.6386 | 10.0264 | 9.495 | 9.0041 | 9.4806 | 9.6207 | 9.5389 | 10.0108 | 10.4675 | 10.6794 | 11.0709 | 11.3023 | 11.6686 | 11.9861 | 11.8146 | 11.6736 | 11.5267 | 11.43 | 11.3803 | 11.3845 | 11.3799 | 11.3621
VIC new CCGT | 9.3186 | 9.7064 | 9.175 | 8.6841 | 9.1606 | 9.3007 | 9.2189 | 9.6908 | 10.1475 | 10.3594 | 10.7509 | 10.9823 | 11.3486 | 11.6661 | 11.4946 | 11.3536 | 11.2067 | 11.11 | 11.0603 | 11.0645 | 11.0599 | 11.0421
SA new CCGT | 9.7986 | 10.1864 | 9.655 | 9.1641 | 9.6406 | 9.7807 | 9.6989 | 10.1708 | 10.6275 | 10.8394 | 11.2309 | 11.4623 | 11.8286 | 12.1461 | 11.9746 | 11.8336 | 11.6867 | 11.59 | 11.5403 | 11.5445 | 11.5399 | 11.5221
TAS new CCGT | 10.5686 | 10.9564 | 10.425 | 9.9341 | 10.4106 | 10.5507 | 10.4689 | 10.9408 | 11.3975 | 11.6094 | 12.0009 | 12.2323 | 12.5986 | 12.9161 | 12.7446 | 12.6036 | 12.4567 | 12.36 | 12.3103 | 12.3145 | 12.3099 | 12.2921
Slow Change
| 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
Bairnsdale | 8.8591 | 8.5 | 8.5 | 8.5 | 8.75 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Barcaldine | 7.8691 | 7.71 | 7.71 | 7.71 | 7.96 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21
Bell Bay Three | 9.6091 | 9.45 | 9.45 | 9.45 | 9.7 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95
Braemar | 7.8691 | 7.71 | 7.71 | 7.71 | 7.96 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21
Braemar 2 | 7.8691 | 7.71 | 7.71 | 7.71 | 7.96 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21
Colongra | 9.1791 | 9.02 | 9.02 | 9.02 | 9.27 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52
Condamine | 8.1191 | 7.96 | 7.96 | 7.96 | 8.21 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46 | 8.46
Darling Downs | 7.6691 | 7.51 | 7.51 | 7.51 | 7.76 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01 | 8.01
Dry Creek | 8.8391 | 8.68 | 8.68 | 8.68 | 8.93 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18
Hallett | 8.8391 | 8.68 | 8.68 | 8.68 | 8.93 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18
Jeeralang | 8.3591 | 8 | 8 | 8 | 8.25 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
Ladbroke Grove | 8.8391 | 8.68 | 8.68 | 8.68 | 8.93 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18
Laverton North | 8.8591 | 8.5 | 8.5 | 8.5 | 8.75 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Mintaro | 8.8391 | 8.68 | 8.68 | 8.68 | 8.93 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18
Mortlake OCGT | 8.1591 | 7.8 | 7.8 | 7.8 | 8.05 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3
Newport | 8.8591 | 8.5 | 8.5 | 8.5 | 8.75 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Oakey | 8.3691 | 8.21 | 8.21 | 8.21 | 8.46 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71
Osborne | 7.8391 | 7.68 | 7.68 | 7.68 | 7.93 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18 | 8.18
Pelican Point | 8.3391 | 8.18 | 8.18 | 8.18 | 8.43 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68
Quarantine | 8.5891 | 8.43 | 8.43 | 8.43 | 8.68 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93 | 8.93
Roma | 8.3691 | 8.21 | 8.21 | 8.21 | 8.46 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71
Smithfield | 9.1791 | 9.02 | 9.02 | 9.02 | 9.27 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52 | 9.52
Somerton | 8.8591 | 8.5 | 8.5 | 8.5 | 8.75 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Swanbank E | 8.3691 | 8.21 | 8.21 | 8.21 | 8.46 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71 | 8.71
Tallawarra | 8.6791 | 8.52 | 8.52 | 8.52 | 8.77 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02
Tamar Valley | 9.6091 | 9.45 | 9.45 | 9.45 | 9.7 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95
Torrens Island | 8.8391 | 8.68 | 8.68 | 8.68 | 8.93 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18 | 9.18
Townsville | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
Uranquinty | 8.9291 | 8.77 | 8.77 | 8.77 | 9.02 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27 | 9.27
Valley Power | 8.8591 | 8.5 | 8.5 | 8.5 | 8.75 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Yarwun | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
QLD new OCGT | 8.8691 | 8.71 | 8.71 | 8.71 | 8.96 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21 | 9.21
NSW new OCGT | 9.6791 | 9.52 | 9.52 | 9.52 | 9.77 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02 | 10.02
VIC new OCGT | 9.3591 | 9 | 9 | 9 | 9.25 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5
SA new OCGT | 9.3391 | 9.18 | 9.18 | 9.18 | 9.43 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68 | 9.68
TAS new OCGT | 9.6091 | 9.45 | 9.45 | 9.45 | 9.7 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95
QLD new CCGT | 7.8691 | 7.71 | 7.71 | 7.71 | 7.96 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21 | 8.21
NSW new CCGT | 8.6791 | 8.52 | 8.52 | 8.52 | 8.77 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02 | 9.02
VIC new CCGT | 8.3591 | 8 | 8 | 8 | 8.25 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
SA new CCGT | 8.3391 | 8.18 | 8.18 | 8.18 | 8.43 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68 | 8.68
TAS new CCGT | 9.6091 | 9.45 | 9.45 | 9.45 | 9.7 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95
Liquid fuel price | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
Liquid fuel | 37.11 | 36.79 | 36.31 | 35.75 | 35.19 | 34.68 | 34.2 | 33.76 | 33.37 | 33.03 | 32.68 | 32.34 | 32.03 | 31.75 | 31.49 | 31.25 | 31.03 | 30.81 | 30.6 | 30.39 | 30.19 | 29.99

## Refurbishment
Go to Assumptions Summary
Refurbishment
Unit refurbishment is staggered within a power station, one unit at a time at six month intervals. In a power station with 4 units, for example, the fourth unit is not refurbished until 18 months after the given date.
Refurbishment timing
Generator | First refurbishment | Second refurbishment
Bayswater | 2025
Eraring | 2024
Mount Piper | 2023 | 2033
Vales Point | 2022
Callide B | 2028
Callide Power Plant | 2031 | 2041
Kogan Creek | 2037 | 2047
Millmerran | 2032 | 2042
Stanwell | 2026 | 2036
Tarong | 2026
Tarong North | 2033 | 2043
Loy Yang A | 2028 | 2038
Loy Yang B | 2026 | 2036
Yallourn | 2022 | 2032
Refurbishment cost
Generation type | Fuel Type | Refurbishment | Refurbishment cost ($/MW Real 2019)1
Boiler / Steam turbine | Coal | Replace creep affected components and undertaken ancillary works to extend life by 10 years | 375000
OCGT | Natural Gas | Upgrade compressor & turbine blading | 320000
CCGT | Natural Gas | Upgrade compressor & turbine blading | 220000
1. Costs are applied as an additional fixed cost for the duration of the refurbishment event.
2. Refurbishment costs are from the GHD 2018 AEMO costs and technical parameter review
3. Refurbishment costs are applied to Coal, OCGT, and CCGT plants

## Retirement
Go to Assumptions Summary
Retirement
Announced and end-of-technical-life retirement. End of life retirements are determined according to equipment age. Units may be retired earlier by the model if determined as least cost to the power system.
Announced retirement |  | Retirement Costs
Generator | Financial year ending | Generator | Retirement/Rehabilitation Cost (real 2019 $/MW)
Mackay GT1 | 2021 | Black Coal | 160000
Liddell1 | 2022 | Brown Coal | 160000
Bayswater2 | 2035 | OCGT | 45000
Loy Yang A2 | 2048 | CCGT | 130000
1. Data source: AEMO generation information page |  | Pumped hydro | 107501.795
2. Data source: AGL announcement |  | Wind | 10750.1795
https://www.agl.com.au/about-agl/sustainability/rehabilitation |  | Single-axis tracking solar | 21500.359
End of technical life
Generator | Financial year ending
Bayswater | 2035
Eraring | 2034
Mount Piper | 2043
Vales Point | 2028
Callide B | 2038
Callide Power Plant | 2051
Gladstone | 2029
Kogan Creek | 2057
Millmerran | 2052
Stanwell | 2046
Tarong | 2036
Tarong North | 2053
Loy Yang B | 2056
Yallourn1 | 2032
Newport | 2031
Torrens Island A | 2021
1. Assumed retirement upon conclusion of current mine coal supply agreement
2. Coal and CCGT plants will be retired at end of their technical life

## Heat rates
Go to Assumptions Summary
Heat rates
Encapsulates the efficiency of thermal generators (as-generated, HHV)
Existing and committed generators |  | New entrant technologies
Generator | Heat rate (GJ/MWh) | Technology | Heat rates (GJ/MWh)
Bayswater | 9.4488 | Black Coal (supercritical PC) | 8.975
Eraring | 9.5491 | Black Coal (supercritical PC) with CCS | 12.099
Liddell | 10.1408 | Brown Coal (supercritical PC) | 11.337
Mount Piper | 9.2545 | Brown Coal (supercritical PC) with CCS | 14.9453
Vales Point | 9.6774 | OCGT | 11.7497
Callide B | 9.1603 | CCGT | 7.5753
Callide Power Plant | 9.3023 | CCGT with CCS | 8.7837
Gladstone | 9.4737 | Biomass | 13.39
Kogan Creek | 8.802 | Nuclear (SMR) | 8
Millmerran | 9.2072
Stanwell | 9.068
Tarong | 9.2072
Tarong North | 8.6538
Loy Yang A | 12.1622
Loy Yang B | 12.5436
Yallourn | 13.8996
Colongra | 11.1455
Smithfield | 8.3527
Tallawarra | 6.9903
Uranquinty | 11.1455
Barcaldine | 12.7208
Braemar | 11.8812
Condamine | 7.2874
Darling Downs | 7.377
Oakey | 10.9422
Roma | 11.8812
Swanbank E | 7.438
Yabulu (Townsville) | 7.5949
Yarwun | 10.3746
Somerton | 14.876
Bairnsdale | 10.4956
Jeeralang A | 15.2542
Jeeralang B | 15.2542
Laverton North | 11.5016
Mortlake | 11.1455
Newport | 10.2857
Valley Power | 14.876
Hallett GT | 14.876
Barker Inlet | 7.8947
Dry Creek | 13.6882
Ladbroke Grove | 11.8812
Mintaro | 12.7208
Osborne | 8.1633
Pelican Point | 7.3469
Quarantine | 10.7143
Torrens Island A | 11.4286
Torrens Island B | 10.7143
Bell Bay Three | 12.0401
Tamar Valley CCGT | 7.2874
Tamar Valley OCGT | 12.7208
Hunter Valley GT | 12.7208
Mackay GT | 12.7208
Mount Stuart | 11.8812
Angaston | 12.775
Lonsdale | 7.8947
Port Lincoln | 12.8114
Port Lincoln 3 | 12.8114
Port Stanvac | 7.8947
Snuggery | 13.4328

## Auxiliary
Go to Assumptions Summary
Auxiliary load
Auxiliary load is also called "parasitic load" or "self load" and refers to energy generated for use within power stations
Existing generators |  | New entrants
Generator | % auxiliary load | Generator | % auxiliary load
Bayswater | 6 | Black Coal (supercritical PC) | 4
Eraring | 6 | Black Coal (supercritical PC) with CCS | 15.94
Liddell | 5 | Brown Coal (supercritical PC) | 6.01
Mount Piper | 5 | Brown Coal (supercritical PC) with CCS | 24.4
Vales Point | 5 | OCGT | 1.53
Callide B | 9 | CCGT | 2.51
Callide Power Plant | 6 | CCGT with CCS | 9.72
Gladstone | 8 | Biomass | 6.1
Kogan Creek | 9 | Large scale Solar PV | 2
Millmerran | 6 | Solar Thermal (8hrs Storage) | 10
Stanwell | 9 | Nuclear (SMR) | 5
Tarong | 8 | Battery Storage (2hrs storage) | 4
Tarong North | 6 | Wind | 2
Loy Yang A | 9 | Pumped hydro (6 hrs storage) | 1
Loy Yang B | 8
Yallourn | 10
Colongra | 1
Smithfield | 5
Tallawarra | 3
Uranquinty | 1
Barcaldine | 1
Braemar | 1
Condamine | 3
Darling Downs | 6
Oakey | 1
Roma | 1
Swanbank E | 3
Yabulu (Townsville) | 3
Yarwun | 2
Somerton | 1
Bairnsdale | 1
Jeeralang A | 3
Jeeralang B | 3
Laverton North | 3
Mortlake | 1
Newport | 5
Valley Power | 1
Hallett GT | 1
Barker Inlet | 3
Dry Creek | 1
Ladbroke Grove | 1
Mintaro | 1
Osborne | 5
Pelican Point | 2
Quarantine | 5
Torrens Island A | 5
Torrens Island B | 5
Bell Bay Three | 3
Tamar Valley CCGT | 3
Tamar Valley OCGT | 1
Hunter Valley GT | 1
Mackay GT | 1
Mount Stuart | 1
Angaston | 2.5
Lonsdale | 2.5
Port Lincoln | 8
Port Lincoln 3 | 8
Port Stanvac | 2.5
Snuggery | 3
All hydro | 1
All wind | 1
All solar | 1

## Fixed OPEX
Go to Assumptions Summary
Fixed operating cost (real 2019 dollars)
Costs that are incurred regardless of energy generated.
Existing and Committed generators |  | New entrant technologies, after applying regional cost factors
Generator | Fixed OPEX ($/kW/year) | Generator | Fixed OPEX ($/kW/year)
Bayswater | 53.2 |  | Vic low | Vic medium | Vic high | Qld low | Qld medium | Qld high | NSW low | NSW medium | NSW high | SA Low | SA medium | SA high | WA low | WA medium | WA high | NT low | NT medium | NT high | Tas low | Tas medium | Tas high
Eraring | 53.2 | Black Coal (supercritical PC) | 53.2 | 54.796 | 55.86 | 56.924 | 63.84 | 71.288 | 60.116 | 64.904 | 70.224 | 53.732 | 60.116 | 66.5 | 57.456 | 68.628 | 79.8 | 63.308 | 75.544 | 88.312 | 55.86 | 60.648 | 65.436
Liddell | 53.2 | Black Coal (supercritical PC) with CCS | 77.1 | 79.413 | 80.955 | 82.497 | 92.52 | 103.314 | 87.123 | 94.062 | 101.772 | 77.871 | 87.123 | 96.375 | 83.268 | 99.459 | 115.65 | 91.749 | 109.482 | 127.986 | 80.955 | 87.894 | 94.833
Mount Piper | 53.2 | Brown Coal (supercritical PC) | 69 | 71.07 | 72.45 | 73.83 | 82.8 | 92.46 | 77.97 | 84.18 | 91.08 | 69.69 | 77.97 | 86.25 | 74.52 | 89.01 | 103.5 | 82.11 | 97.98 | 114.54 | 72.45 | 78.66 | 84.87
Vales Point | 53.2 | Brown Coal (supercritical PC) with CCS | 101.6 | 104.648 | 106.68 | 108.712 | 121.92 | 136.144 | 114.808 | 123.952 | 134.112 | 102.616 | 114.808 | 127 | 109.728 | 131.064 | 152.4 | 120.904 | 144.272 | 168.656 | 106.68 | 115.824 | 124.968
Callide B | 53.2 | OCGT | 4.2 | 4.326 | 4.41 | 4.494 | 5.04 | 5.628 | 4.746 | 5.124 | 5.544 | 4.242 | 4.746 | 5.25 | 4.536 | 5.418 | 6.3 | 4.998 | 5.964 | 6.972 | 4.41 | 4.788 | 5.166
Callide Power Plant | 53.2 | CCGT | 10.5 | 10.815 | 11.025 | 11.235 | 12.6 | 14.07 | 11.865 | 12.81 | 13.86 | 10.605 | 11.865 | 13.125 | 11.34 | 13.545 | 15.75 | 12.495 | 14.91 | 17.43 | 11.025 | 11.97 | 12.915
Gladstone | 53.2 | CCGT with CCS | 17.9 | 18.437 | 18.795 | 19.153 | 21.48 | 23.986 | 20.227 | 21.838 | 23.628 | 18.079 | 20.227 | 22.375 | 19.332 | 23.091 | 26.85 | 21.301 | 25.418 | 29.714 | 18.795 | 20.406 | 22.017
Kogan Creek | 53.2 | Biomass | 131.6 | 135.548 | 138.18 | 140.812 | 157.92 | 176.344 | 148.708 | 160.552 | 173.712 | 132.916 | 148.708 | 164.5 | 142.128 | 169.764 | 197.4 | 156.604 | 186.872 | 218.456 | 138.18 | 150.024 | 161.868
Millmerran | 53.2 | Large scale Solar PV | 14.44 | 14.8732 | 15.162 | 15.4508 | 17.328 | 19.3496 | 16.3172 | 17.6168 | 19.0608 | 14.5844 | 16.3172 | 18.05 | 15.5952 | 18.6276 | 21.66 | 17.1836 | 20.5048 | 23.9704 | 15.162 | 16.4616 | 17.7612
Stanwell | 53.2 | Solar Thermal (8hrs Storage) | 85 | 87.55 | 89.25 | 90.95 | 102 | 113.9 | 96.05 | 103.7 | 112.2 | 85.85 | 96.05 | 106.25 | 91.8 | 109.65 | 127.5 | 101.15 | 120.7 | 141.1 | 89.25 | 96.9 | 104.55
Tarong | 53.2 | Nuclear (SMR) | 200 | 206 | 210 | 214 | 240 | 268 | 226 | 244 | 264 | 202 | 226 | 250 | 216 | 258 | 300 | 238 | 284 | 332 | 210 | 228 | 246
Tarong North | 53.2 | Battery Storage (2hrs storage) | 8 | 8.24 | 8.4 | 8.56 | 9.6 | 10.72 | 9.04 | 9.76 | 10.56 | 8.08 | 9.04 | 10 | 8.64 | 10.32 | 12 | 9.52 | 11.36 | 13.28 | 8.4 | 9.12 | 9.84
Loy Yang A1 | 145.58 | Wind | 36.02 | 37.1006 | 37.821 | 38.5414 | 43.224 | 48.2668 | 40.7026 | 43.9444 | 47.5464 | 36.3802 | 40.7026 | 45.025 | 38.9016 | 46.4658 | 54.03 | 42.8638 | 51.1484 | 59.7932 | 37.821 | 41.0628 | 44.3046
Loy Yang B1 | 115.07 | Pumped hydro (6 hrs storage) | 16 | 16.48 | 16.8 | 17.12 | 19.2 | 21.44 | 18.08 | 19.52 | 21.12 | 16.16 | 18.08 | 20 | 17.28 | 20.64 | 24 | 19.04 | 22.72 | 26.56 | 16.8 | 18.24 | 19.68
Yallourn1 | 151.23
Colongra | 4.2
Smithfield | 10.5
Tallawarra | 10.5
Uranquinty | 4.2
Barcaldine | 4.2
Braemar | 4.2
Condamine | 10.5
Darling Downs | 10.5
Oakey | 4.2
Roma | 4.2
Swanbank E | 10.5
Yabulu (Townsville) | 10.5
Yarwun | 10.5
Somerton | 4.2
Bairnsdale | 4.2
Jeeralang A | 4.2
Jeeralang B | 4.2
Laverton North | 4.2
Mortlake | 4.2
Newport | 47.1277
Valley Power | 4.2
Barker Inlet | 15.12
Hallett GT | 4.2
Dry Creek | 4.2
Ladbroke Grove | 4.2
Mintaro | 4.2
Osborne | 10.5
Pelican Point | 10.5
Quarantine | 4.2
Torrens Island A | 47.1277
Torrens Island B | 47.1277
Bell Bay Three | 4.2
Tamar Valley CCGT | 10.5
Tamar Valley OCGT | 4.2
Hunter Valley GT | 4.2
Mackay GT | 4.2
Mount Stuart | 4.2
Angaston | 15.12
Lonsdale | 15.12
Port Lincoln | 4.2
Port Lincoln 3 | 4.2
Port Stanvac | 15.12
Snuggery | 4.2
All hydro | 58.25
All wind | 45.1
All solar | 25.7
All batteries | 0
Note: Sourced from GHD with the exception of the brown coal plants, which are from ACIL Allen.

## Variable OPEX
Go to Assumptions Summary
Variable operating cost (real 2019 dollars)
Costs that can be expressed in terms of energy generated, not including fuel costs.
Existing and Committed generators |  | New entrant technologies, after applying regional cost factors
Generator | Variable OPEX ($/MWh)1 | Generator | Variable OPEX ($/MWh)
Bayswater | 4.21 |  | Vic low | Vic medium | Vic high | Qld low | Qld medium | Qld high | NSW low | NSW medium | NSW high | SA Low | SA medium | SA high | WA low | WA medium | WA high | NT low | NT medium | NT high | Tas low | Tas medium | Tas high
Eraring | 4.21 | Black Coal (supercritical PC) | 4.21 | 4.3363 | 4.4205 | 4.5047 | 5.052 | 5.6414 | 4.7573 | 5.1362 | 5.5572 | 4.2521 | 4.7573 | 5.2625 | 4.5468 | 5.4309 | 6.315 | 5.0099 | 5.9782 | 6.9886 | 4.4205 | 4.7994 | 5.1783
Liddell | 4.21 | Black Coal (supercritical PC) with CCS | 9.48 | 9.7644 | 9.954 | 10.1436 | 11.376 | 12.7032 | 10.7124 | 11.5656 | 12.5136 | 9.5748 | 10.7124 | 11.85 | 10.2384 | 12.2292 | 14.22 | 11.2812 | 13.4616 | 15.7368 | 9.954 | 10.8072 | 11.6604
Mount Piper | 4.21 | Brown Coal (supercritical PC) | 5.27 | 5.4281 | 5.5335 | 5.6389 | 6.324 | 7.0618 | 5.9551 | 6.4294 | 6.9564 | 5.3227 | 5.9551 | 6.5875 | 5.6916 | 6.7983 | 7.905 | 6.2713 | 7.4834 | 8.7482 | 5.5335 | 6.0078 | 6.4821
Vales Point | 4.21 | Brown Coal (supercritical PC) with CCS | 11.58 | 11.9274 | 12.159 | 12.3906 | 13.896 | 15.5172 | 13.0854 | 14.1276 | 15.2856 | 11.6958 | 13.0854 | 14.475 | 12.5064 | 14.9382 | 17.37 | 13.7802 | 16.4436 | 19.2228 | 12.159 | 13.2012 | 14.2434
Callide B | 4.21 | OCGT | 10.53 | 10.8459 | 11.0565 | 11.2671 | 12.636 | 14.1102 | 11.8989 | 12.8466 | 13.8996 | 10.6353 | 11.8989 | 13.1625 | 11.3724 | 13.5837 | 15.795 | 12.5307 | 14.9526 | 17.4798 | 11.0565 | 12.0042 | 12.9519
Callide Power Plant | 4.21 | CCGT | 7.37 | 7.5911 | 7.7385 | 7.8859 | 8.844 | 9.8758 | 8.3281 | 8.9914 | 9.7284 | 7.4437 | 8.3281 | 9.2125 | 7.9596 | 9.5073 | 11.055 | 8.7703 | 10.4654 | 12.2342 | 7.7385 | 8.4018 | 9.0651
Gladstone | 4.21 | CCGT with CCS | 12.64 | 13.0192 | 13.272 | 13.5248 | 15.168 | 16.9376 | 14.2832 | 15.4208 | 16.6848 | 12.7664 | 14.2832 | 15.8 | 13.6512 | 16.3056 | 18.96 | 15.0416 | 17.9488 | 20.9824 | 13.272 | 14.4096 | 15.5472
Kogan Creek | 4.21 | Biomass | 8.42 | 8.6726 | 8.841 | 9.0094 | 10.104 | 11.2828 | 9.5146 | 10.2724 | 11.1144 | 8.5042 | 9.5146 | 10.525 | 9.0936 | 10.8618 | 12.63 | 10.0198 | 11.9564 | 13.9772 | 8.841 | 9.5988 | 10.3566
Millmerran | 4.21 | Large scale Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stanwell | 4.21 | Solar Thermal (8hrs Storage) | 5.4 | 5.562 | 5.67 | 5.778 | 6.48 | 7.236 | 6.102 | 6.588 | 7.128 | 5.454 | 6.102 | 6.75 | 5.832 | 6.966 | 8.1 | 6.426 | 7.668 | 8.964 | 5.67 | 6.156 | 6.642
Tarong | 4.21 | Nuclear (SMR) | 20 | 20.6 | 21 | 21.4 | 24 | 26.8 | 22.6 | 24.4 | 26.4 | 20.2 | 22.6 | 25 | 21.6 | 25.8 | 30 | 23.8 | 28.4 | 33.2 | 21 | 22.8 | 24.6
Tarong North | 4.21 | Battery Storage (2hrs storage) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Loy Yang A | 4.21 | Wind | 2.6667 | 2.7467 | 2.8 | 2.8533 | 3.2 | 3.5733 | 3.0133 | 3.2533 | 3.52 | 2.6933 | 3.0133 | 3.3333 | 2.88 | 3.44 | 4 | 3.1733 | 3.7867 | 4.4267 | 2.8 | 3.04 | 3.28
Loy Yang B | 4.21 | Pumped hydro (6 hrs storage) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Yallourn | 4.21
Colongra | 10.53
Smithfield | 7.37
Tallawarra | 7.37
Uranquinty | 10.53
Barcaldine | 10.53
Braemar | 10.53
Condamine | 7.37
Darling Downs | 7.37
Oakey | 10.53
Roma | 10.53
Swanbank E | 7.37
Yabulu (Townsville) | 7.37
Yarwun | 7.37
Somerton | 10.53
Bairnsdale | 10.53
Jeeralang A | 10.53
Jeeralang B | 10.53
Laverton North | 10.53
Mortlake | 10.53
Newport | 2.3287
Valley Power | 10.53
Barker Inlet | 11.18
Hallett GT | 10.53
Dry Creek | 10.53
Ladbroke Grove | 10.53
Mintaro | 10.53
Osborne | 7.37
Pelican Point | 7.37
Quarantine | 10.53
Torrens Island A | 2.3287
Torrens Island B | 2.3287
Bell Bay Three | 10.53
Tamar Valley CCGT | 7.37
Tamar Valley OCGT | 10.53
Hunter Valley GT | 10.53
Mackay GT | 10.53
Mount Stuart | 10.53
Angaston | 11.18
Lonsdale | 11.18
Port Lincoln | 10.53
Port Lincoln 3 | 10.53
Port Stanvac | 11.18
Snuggery | 10.53
All hydro | 7.19
All wind | 2.67
All solar | 0
All batteries | 0
1. In capacity expansion simulations, variable OPEX may be varied by a small amount ($0.01) on a unit-by-unit basis within a power station to encourage model-driven retirement to occur on a per-unit basis

## Emissions
Go to Assumptions Summary
Emissions
Existing generators |  |  |  | Generic new entrant units and committed projects
Generator | Combustion emissions (kg/MWh) | Fugitive emissions (kg/MWh) | Total emissions (kg/MWh) | Generator | Region | Combustion emissions (kg/MWh) | Fugitive emissions (kg/MWh) | Total emissions (kg/MWh)
Bayswater | 865.5122 | 47.1309 | 912.6431 | OCGT | Qld | 624.4845 | 89.2977 | 713.7822
Eraring | 862.3464 | 47.7966 | 910.1431 | OCGT | NSW | 624.4845 | 158.6209 | 783.1054
Liddell | 930 | 50.5917 | 980.5917 | OCGT | VIC | 624.4845 | 45.8238 | 670.3083
Mount Piper | 862.3022 | 46.2162 | 908.5184 | OCGT | SA | 624.4845 | 119.8469 | 744.3314
Vales Point | 860 | 48.3051 | 908.3051 | OCGT | Tas | 624.4845 | 45.8238 | 670.3083
Callide B | 920 | 11.3435 | 931.3435 | CCGT | Qld | 394.6595 | 57.5725 | 452.232
Callide Power Plant | 895.323 | 11.589 | 906.912 | CCGT | NSW | 394.6595 | 102.2669 | 496.9264
Gladstone | 960 | 11.7614 | 971.7614 | CCGT | VIC | 394.6595 | 29.5438 | 424.2033
Kogan Creek | 820 | 11.04 | 831.04 | CCGT | SA | 394.6595 | 77.2684 | 471.9279
Millmerran | 830.1346 | 11.4634 | 841.598 | CCGT | Tas | 394.6595 | 29.5438 | 424.2033
Stanwell | 860.94 | 11.25 | 872.19 | CCGT with CCS | Qld | 55.8643 | 66.7561 | 122.6204
Tarong | 860.0221 | 11.4365 | 871.4586 | CCGT with CCS | NSW | 55.8643 | 118.5799 | 174.4442
Tarong North | 832.9647 | 10.7908 | 843.7555 | CCGT with CCS | VIC | 55.8643 | 34.2564 | 90.1207
Loy Yang A | 1150 | 4.8176 | 1154.8176 | CCGT with CCS | SA | 55.8643 | 89.5937 | 145.458
Loy Yang B | 1136.0409 | 4.9805 | 1141.0214 | CCGT with CCS | Tas | 55.8643 | 34.2564 | 90.1207
Yallourn | 1310 | 5.5149 | 1315.5149 | Black Coal (Supercritical PC) | Qld | 769.5165 | 20.6425 | 790.159
Colongra | 640 | 142.56 | 782.56 | Black Coal (Supercritical PC) | NSW | 769.5165 | 82.57 | 852.0865
Smithfield | 480.9688 | 106.7707 | 587.7395 | Black Coal (Supercritical PC) | VIC | - | - | -
Tallawarra | 358.1395 | 89.3952 | 447.5347 | Black Coal (Supercritical PC) | SA | - | - | -
Uranquinty | 581.7116 | 142.56 | 724.2716 | Black Coal (Supercritical PC) | Tas | - | - | -
Barcaldine | 999.9566 | 99.2829 | 1099.2394 | Black Coal (Supercritical PC) with CCS | Qld | 74.8928 | 27.8277 | 102.7205
Braemar | 570.4776 | 92.664 | 663.1416 | Black Coal (Supercritical PC) with CCS | NSW | 74.8928 | 111.3108 | 186.2036
Condamine | 454.3237 | 56.745 | 511.0687 | Black Coal (Supercritical PC) with CCS | VIC | - | - | -
Darling Downs | 420.2045 | 57.3809 | 477.5854 | Black Coal (Supercritical PC) with CCS | SA | - | - | -
Oakey | 760 | 85.2736 | 845.2736 | Black Coal (Supercritical PC) with CCS | Tas | - | - | -
Roma | 663.8544 | 92.664 | 756.5184 | Brown Coal (Supercritical PC) | Qld | - | - | -
Swanbank E | 370 | 57.9523 | 427.9523 | Brown Coal (Supercritical PC) | NSW | - | - | -
Yabulu | 450 | 59.2122 | 509.2122 | Brown Coal (Supercritical PC) | VIC | 959.3369 | 4.5348 | 963.8717
Yabulu Steam Turbine | 450 | 59.2122 | 509.2122 | Brown Coal (Supercritical PC) | SA | - | - | -
Yarwun | 532.3129 | 80.9365 | 613.2494 | Brown Coal (Supercritical PC) | Tas | - | - | -
Somerton | 760 | 57.915 | 817.915 | Brown Coal (Supercritical PC) with CCS | Qld | - | - | -
Bairnsdale | 524.3273 | 40.8812 | 565.2085 | Brown Coal (Supercritical PC) with CCS | NSW | - | - | -
Jeeralang A | 819.9338 | 59.4707 | 879.4045 | Brown Coal (Supercritical PC) with CCS | VIC | 80.107 | 5.9781 | 86.0852
Jeeralang B | 819.9338 | 59.4707 | 879.4045 | Brown Coal (Supercritical PC) with CCS | SA | - | - | -
Laverton North | 745.3812 | 44.7987 | 790.1799 | Brown Coal (Supercritical PC) with CCS | Tas | - | - | -
Mortlake | 530 | 43.4362 | 573.4362 | Biomass | Qld | 1351.051 | - | 1351.051
Newport | 530 | 40.0541 | 570.0541 | Biomass | NSW | 1351.051 | - | 1351.051
Valley Power | 813.6315 | 57.915 | 871.5465 | Biomass | VIC | 1351.051 | - | 1351.051
Hallett GT | 1020 | 154.44 | 1174.44 | Biomass | SA | 1351.051 | - | 1351.051
Dry Creek | 1200 | 142.56 | 1342.56 | Biomass | Tas | 1351.051 | - | 1351.051
Ladbroke Grove | 530 | 123.552 | 653.552 | Barker Inlet | SA | 422.5737 | 80.5263 | 503.1
Mintaro | 820 | 132.3771 | 952.3771
Osborne | 460 | 84.6857 | 544.6857 | 1 Generic new entrant units and committed projects emissions are calculated based on unit's heat rates and fuel emissions details given in the GHD 2018 AEMO costs and technical parameter review.
Pelican Point | 397.2675 | 76.44 | 473.7075
Quarantine | 688.8094 | 111.15 | 799.9594
Torrens Island A | 590 | 118.56 | 708.56
Torrens Island B | 570 | 111.15 | 681.15
Bell Bay Three | 617.7228 | 46.9614 | 664.6841
Tamar Valley OCGT | 652.9757 | 49.6414 | 702.6171
Tamar Valley CCGT | 410.3827 | 28.3725 | 438.7552 | 1
Hunter Valley GT | 887.1814 | 45.8229 | 933.0043
Mackay GT | 1000 | 45.8229 | 1045.8229
Mount Stuart | 955.8648 | 42.768 | 998.6328
Angaston1 | 940.2 | 73.4 | 1013.6
Lonsdale1 | 1442 | 49.8 | 1491.8
Port Lincoln | 1400 | 45.8585 | 1445.8585
Port Lincoln 3 | 1400 | 45.8585 | 1445.8585
Port Stanvac | 1442 | 49.8 | 1491.8
Snuggery | 1400 | 48.3508 | 1448.3508
All hydro | 0 | 0 | 0
All wind | 0 | 0 | 0
All solar | 0 | 0 | 0

## MLF
Go to Assumptions Summary
Marginal Loss Factors (MLFs)
Marginal loss factors represent the impact of network losses on spot prices. No impacts on long term generation expansion, however, marginal loss factors do impact the short term dispatch modelling.
See https://www.aemo.com.au/-/media/Files/Electricity/NEM/Security_and_Reliability/Loss_Factors_and_Regional_Boundaries/2018/Marginal-Loss-Factors-for-the-2018-19-Financial-Year---updated-11-July-2018.pdf
Existing generators |  | Committed and advanced projects |  |  | Generic new entrant units |  |  |  |  | VRET Projects 1 |  |  | Existing and Committed Battery
Generator | Marginal loss factor | Generator | Marginal loss factor | Shadow connection point | Generator | Marginal loss factor | Shadow connection point | Technology | Region | Generator | Marginal loss factor | Shadow connection point | Battery | Marginal loss factor -Generation | Marginal loss factor - Load | Shadow connection point
Bayswater units 1,2 | 0.9538 | Barker Inlet | 1.0009 | Torrens Island PS A Unit 1 | Barcaldine solar | 0.8934 | Barcaldine Solar | Solar | QLD | Carwarp Solar | 1.0062 | Bannerton Solar Farm | Kennedy Energy Park | 0.9754 | 0.9754 | Woree
Bayswater units 3,4 | 0.9555 | Bodangora WF | 0.9819 |  | Barcaldine wind | 0.9206 | Gladstone | Wind | QLD | Cohuna Solar | 1.0062 | Bannerton Solar Farm | Hornsdale | 0.9771 | 0.9853
Eraring units 1,2 | 0.9828 | Crookwell 2 WF | 0.9959 | Gullen Range Wind Farm | Broken Hill wind | 1.0062 | Silverton WF | Wind | QLD | Winton Solar | 1.0062 | Bannerton Solar Farm | ESCRI Dalrymple | 0.888 | 0.9326
Eraring units 3,4 | 0.9853 | Mt Emerald WF | 0.9754 | Woree | Central NSW Tablelands solar | 0.9824 | Nyngan Solar | Solar | NSW | Dundonnel WF | 0.9691 | Ararat WF | Ballarat | 1.0016 | 1.0016 | Ballarat 66kV
Liddell | 0.9537 | Coopers Gap WF | 0.9812 | Darling Downs Solar Farm | Central NSW Tablelands wind | 0.9819 | Bodangora WF | Wind | NSW | Mortlake South WF | 0.9691 | Ararat WF | Bulgana | 0.9784 | 0.9784 | Waubra Wind Farm
Mount Piper | 0.9738 | Kennedy Energy Park WF | 0.9754 | Woree | Central West NSW solar | 0.9824 | Nyngan Solar | Solar | NSW | Berrybank WF | 0.9971 | Macarthur WF | Gannawarra Energy Storage System | 0.9729 | 0.9729
Vales Point | 0.9851 | Crudine Ridge WF | 0.9819 | Bodangora Wind Farm | Central West NSW wind | 0.9819 | Bodangora WF | Wind | NSW
Callide B | 0.9069 | Crowlands WF | 0.9784 | Waubra WF | Darling Downs solar | 0.9812 | Darling Downs Solar | Solar | QLD | 1. Successful projects for the Victorian Renewable Energy Auction Scheme (VREAS) as announced on Tuesday 11 September, 2018.
Callide Power Plant | 0.908 | Lincoln Gap WF | 1.0068 | Starfish Hill Wind Farm | Darling Downs wind | 0.9709 | Darling Downs | Wind | QLD
Gladstone units 1,2,5,6 | 0.924 | Willogoleche WF | 0.9715 | Hallett Hill WF | Eastern Eyre Peninsula solar | 0.97 | Bungala one Solar | Solar | SA
Gladstone units 3,4 | 0.9206 | Cattle Hill WF | 0.8952 | Bluff Point WF | Eastern Eyre Peninsula wind | 0.9055 | Mount Millar WF | Wind | SA
Kogan Creek | 0.9743 | Granville Harbour WF | 0.9729 | Gannawarra Solar Farm | Fitzroy solar | 0.9206 | Gladstone | Solar | QLD
Millmerran | 0.9812 | Mt Gellibrand WF | 0.9971 | MacArthur Wind Farm | Fitzroy wind | 0.9206 | Gladstone | Wind | QLD
Stanwell | 0.9075 | Murra Warra WF | 0.9691 | Ararat WF | Gippsland wind | 0.9879 | Morwell TS | Wind | VIC
Tarong | 0.9752 | Bulgana WF | 0.9784 | Waubra Wind Farm | Isaac solar | 0.8727 | Clare Solar | Solar | QLD
Tarong North | 0.9755 | Cherry Tree WF | 0.9909 | Mt Mercer Windfarm | Isaac wind | 0.9346 | Yabulu | Wind | QLD
Loy Yang A | 0.9798 | Lal Lal Elaine WF | 0.9909 | Mt Mercer Windfarm | King Island wind | 0.8952 | Bluff Point WF | Wind | TAS
Loy Yang B | 0.9798 | Lal Lal Yendon WF | 0.9909 | Mt Mercer Windfarm | Leigh Creek solar | 0.97 | Bungala one Solar | Solar | SA
Yallourn unit 1 | 0.9696 | Moorabool WF | 0.9909 | Mt Mercer Windfarm | Leigh Creek wind | 0.9941 | Davenport | Wind | SA
Yallourn units 2,3,4 | 0.9573 | Stockyard Hill WF | 0.9784 | Waubra Wind Farm | Mid-North SA wind | 0.9744 | Hornsdale S1 WF | Wind | SA
Blowering | 0.99 | Bomen Solar | 0.9824 | Nyngan Solar Farm | Moyne wind | 0.9971 | Macarthur WF | Wind | VIC
Guthega | 0.9537 | Daydream Solar | 0.8842 | Ross River Solar Farm | Murray River solar | 0.9789 | Broken Hill Solar | Solar | NSW
Hume (NSW) | 1.0675 | Darlington Point Solar | 0.9824 | Nyngan Solar Farm | Murray River solar | 1.0062 | Bannerton Solar | Solar | VIC
Hume (Vic) | 0.9498 | Finley Solar | 0.9824 | Nyngan Solar Farm | Murray River wind | 1.0062 | Silverton WF | Wind | NSW
Shoalhaven | 0.9981 | Hayman Solar | 0.8741 | Whitsunday Solar Farm | Murray River wind | 0.9691 | Ararat WF | Wind | VIC
Tumut 1 | 1.0112 | Brigalow Solar | 0.9818 | Oakey 110 kV | North East Tasmania wind | 0.9105 | Musselroe WF | Wind | TAS
Tumut 2 | 1.0438 | Childers Solar | 0.9818 | Oakey 110 kV | North QLD Clean Energy Hub solar | 0.8842 | Hughenden Solar | Solar | QLD
Tumut 3 | 0.9954 | Clermont Solar | 0.8842 | Ross River Solar Farm | North QLD Clean Energy Hub wind | 0.9754 | Woree | Wind | QLD
Barron Gorge | 0.9346 | Collinsville Solar | 0.8741 | Hamilton Solar Farm | North West New South Wales solar | 0.9612 | Moree | Solar | NSW
Kareeya | 0.9523 | Haughton Solar | 0.8842 | Ross River Solar Farm | North West New South Wales wind | 0.8413 | White Rock WF | Wind | NSW
Wivenhoe | 0.9939 | Kennedy Energy Park Solar | 0.8842 | Kidston Solar Farm | North West Tasmania wind | 0.8952 | Bluff Point WF | Wind | TAS
McKay Creek / Bogong PS | 0.9265 | Lilyvale Solar | 0.9029 | Barcaldine PS – Lilyvale | Northern NSW Tablelands solar | 0.9612 | Moree | Solar | NSW
Dartmouth | 0.9249 | Limondale 1 Solar | 0.9824 | Nyngan Solar Farm | Northern NSW Tablelands wind | 0.8821 | Sapphire WF | Wind | NSW
Eildon | 0.9782 | Limondale 2 Solar | 0.9824 | Nyngan Solar Farm | Northern QLD solar | 1.0092 | Sun Metals Solar | Solar | QLD
Murray | 0.9069 | Oakey Solar | 0.9818 | Oakey 110 kV | Northern SA solar | 0.97 | Bungala one Solar | Solar | SA
West Kiewa | 0.9607 | Oakey 2 Solar | 0.9818 | Oakey 110 kV | Northern SA wind | 0.9941 | Davenport | Wind | SA
Bastyan | 0.941 | Rugby Run Solar | 0.9029 | Barcaldine PS – Lilyvale | NSW pumped hydro | - | - | Pumped Hydro | NSW
Catagunya | 0.9977 | Susan River Solar | 0.9818 | Oakey 110 kV | NSW thermal generation | - | - | thermal | NSW
Cethana | 0.9628 | Teebar Solar | 0.9764 | Teebar Creek | QLD pumped hydro | - | - | Pumped Hydro | QLD
Devils Gate | 0.9692 | Yarranlea Solar | 0.9818 | Oakey 110 kV | QLD thermal generation | - | - | thermal | QLD
Fisher | 0.966 | Warwick Solar | 0.8741 | Whitsunday Solar Farm | Riverland solar | 0.9789 | Broken Hill Solar | Solar | NSW
Gordon | 0.9868 | Beryl Solar | 0.9905 | Manildra Solar Farm | Riverland solar | 0.97 | Bungala one Solar | Solar | SA
John Butters | 0.9365 | Nevertire Solar | 0.9824 | Nyngan Solar Farm | Riverland wind | 1.0062 | Silverton WF | Wind | NSW
Liapootah | 0.9977 | Sunraysia Solar | 0.9789 | Broken Hill Solar Farm | Riverland wind | 0.9712 | Waterloo WF | Wind | SA
Lake Echo | 0.9385 | Bungala 2 Solar | 0.97 | Bungala one Solar Farm | Roxby Downs solar | 0.97 | Bungala one Solar | Solar | SA
Lemonthyme | 0.9701 | Bannerton Solar | 1.0062 | Bannerton Solar Farm | SA pumped hydro | - | - | Pumped Hydro | SA
Mackintosh | 0.9282 | Kiamal Solar | 1.0062 | Bannerton Solar Farm | SA thermal generation | - | - | thermal | SA
Meadowbank | 0.9773 | Karadoc Solar | 1.0062 | Bannerton Solar Farm | South East SA wind | 0.9144 | Lake Bonney 1 WF | Wind | SA
Poatina units 1,2 | 0.9799 | Numurkah Solar | 0.9729 | Gannawarra Solar Farm | Southern NSW Tablelands solar | 1.0266 | Royalla Solar | Solar | NSW
Poatina units 3,4,5,6 | 0.9912 | Tailem Bend Solar | 0.97 | Bungala one Solar | Southern NSW Tablelands wind | 1.01 | Capital WF | Wind | NSW
Reece unit 1 | 0.935 | Yatpool Solar | 1.0062 | Bannerton Solar Farm | TAS pumped hydro | - | - | Pumped Hydro | TAS
Reece unit 2 | 0.9264 | Wemen Solar | 0.9729 | Gannawarra Solar Farm | TAS thermal generation | - | - | thermal | TAS
Tarraleah | 0.9405 |  |  |  | Tasmania Midlands wind | 0.9385 | Lake Echo | Wind | TAS
Trevallyn | 0.9909 |  |  |  | VIC pumped hydro | - | - | Pumped Hydro | VIC
Tribute | 0.9377 |  |  |  | VIC thermal generation | - | - | thermal | VIC
Tungatinah | 0.9184 |  |  |  | Western Eyre Peninsula solar | 0.97 | Bungala one Solar | Solar | SA
Wilmot | 0.9701 |  |  |  | Western Eyre Peninsula wind | 0.9055 | Mount Millar WF | Wind | SA
Wayatinah | 0.9977 |  |  |  | Western Victoria wind | 0.9691 | Ararat WF | Wind | VIC
Colongra | 0.9827 |  |  |  | Yorke Peninsula wind | 0.8279 | Wattle Point WF | Wind | SA
Smithfield | 1
Tallawarra | 1.0001
Uranquinty | 0.9609
Barcaldine | 0.9029
Braemar | 0.9709
Condamine | 0.9882
Darling Downs | 0.9709
Oakey | 0.9562
Roma | 0.9729
Swanbank E | 1.0009
Yabulu | 0.9346
Yabulu Steam Turbine | 0.9495
Yarwun | 0.9245
Somerton | 0.9963
Bairnsdale | 0.9866
Jeeralang A | 0.9783
Jeeralang B | 0.9783
Laverton North | 1.0018
Mortlake | 0.9961
Newport | 0.9962
Valley Power | 0.9798
Hallett GT | 0.9715
Dry Creek | 1.003
Ladbroke Grove | 0.9474
Mintaro | 0.9942
Osborne | 0.9992
Pelican Point | 1.0005
Quarantine | 0.9854
Torrens Island A | 1.0009
Torrens Island B | 1.0009
Bell Bay Three | 1.0003
Tamar Valley | 0.9999
Hunter Valley GT | 0.9596
Mackay GT | 0.8863
Mount Stuart | 0.8842
Angaston | 1.0087
Lonsdale | 1.0068
Port Lincoln | 0.9691
Port Lincoln 3 | 1.0383
Port Stanvac | 1.0068
Snuggery | 0.9325
Boco Rock WF | 1.0068
Capital WF | 1.01
Cullerin Range WF | 1.0054
Gullen Range WF | 0.9959
Gunning WF | 1.0054
Silverton WF | 0.9977
Sapphire WF | 0.8821
Taralga WF | 0.9977
White Rock WF | 0.8413
Woodlawn WF | 1.01
Canunda WF | 0.9237
Cathedral Rocks WF | 0.886
Clements Gap WF | 0.9683
Hallett 1 Brown Hill WF | 0.9715
Hallett 2 Hallett Hill WF | 0.9715
Hallett 3 North Brown Hill WF | 0.9674
Hallett 4 The Bluff WF | 0.9715
Hornsdale S1 WF | 0.9744
Hornsdale S2 WF | 0.9744
Hornsdale S3 WF | 0.9744
Lake Bonney 1 WF | 0.9144
Lake Bonney 2 WF | 0.9144
Lake Bonney 3 WF | 0.9144
Mount Millar WF | 0.9055
Snowtown WF | 0.9203
Snowtown S2 WF | 0.9813
Starfish Hill WF | 1.0068
Waterloo WF | 0.9712
Wattle Point WF | 0.8279
Bluff Point WF | 0.8952
Musselroe WF | 0.9105
Woolnorth WF | 1
Ararat WF | 0.9691
Bald Hills WF | 0.9879
Challicum Hills WF | 1
Kiata WF | 0.9911
Macarthur WF | 0.9971
Mortons Lane WF | 1.0149
Mount Mercer WF | 0.9909
Oaklands Hill WF | 1.0149
Portland WF | 1
Salt Creek WF | 1.0076
Waubra WF | 0.9784
Yambuk WF | 1.0149
Yaloak South WF | 1.0016
Broken Hill Solar | 0.9789
Coleambally Solar | 1
Griffith Solar | 1.0603
Manildra Solar | 0.9905
Moree Solar | 0.8988
Nyngan Solar | 0.9824
Parkes Solar | 0.9964
Clare Solar | 0.8727
Darling Downs Solar | 0.9812
Hamilton Solar | 0.8741
Hughenden Solar | 0.8842
Kidston Solar | 0.8842
Longreach Solar | 0.8934
Ross River Solar | 0.8842
Sun Metals Solar | 1.0092
Gannawarra Solar | 0.9729
Bungala one Solar | 0.97
Whitsunday Solar | 0.9905