## New England SF
Generator name | Capacity (MW) | (1) Ancillary service requirements | (2) Level and pattern of network congestion | (3) Impact on timing of expenditure on the network | (4) Impact on interconnector power transfer capability
New England SF (GS1 and GS2) | 200 MW (GS1) 200 MW (GS2) | There were no new ancillary service contracts in Northern NSW in the 12 months prior to, or following, the commissioning of the New England SF. | The connection of New England SF GS1 and GS2 has increased the generation capacity in Northern NSW. When New England SF is generating, it has the potential to increase the utilisation of surrounding Northern NSW 330 and 132 kV network lines. In the 12 months prior to the connection of New England SF, the constraint equation for avoiding overload on line 964/2 during trip of line 84 constrained for 807.2 hours and in the 12 months following for approx 640 hours. Additionally, the constraint equations for avoiding overloading of line 85 (or 86) during the trip of line 86 (or 85) constrained for approximately 38 (71.6) hours, and in the 12 months following for approx 76 (61.9) hours. There are many factors that impact line 85 overloading constraint equation: - the relative operation of the existing generating units in Northern NSW - NEM dispatch price in NSW. - network outages (planned and unplanned) significantly impact the power transfer limits. Connection of New England SF has had a material impact on network congestion in the 330 kV network around Tamworth and Armidale. Output of New England SF has a direct influence on overloading of line 85 and surrounding lines in the 330 kV network. Possible congestion of the 330 kV lines surrounding New England SF is managed by constraint equation in NEMDE. | No project timings have been affected by the inclusion of New England SF. | New England SF has positive contribution factor in constraint equation for overloading of line 85, which means it will increase loading on this line. New England SF is in Northern area of NSW and has a minimal impact on Queensland interconnector transfer capacity.