## Broken Hill BESS
Generator name | Capacity (MW) | (1) Ancillary service requirements | (2) Level and pattern of network congestion | (3) Impact on timing of expenditure on the network | (4) Impact on interconnector power transfer capability
Broken Hill BESS | 50 | There were no new ancillary service contracts in Central West NSW in the 12 months prior to, or following, the commissioning of the Broken Hill BESS. | The connection of Broken Hill BESS in June 2024 has become a significant network support asset mainly for Broken Hill in Western NSW. When Broken Hill BESS is charging/ discharging, it influences the power flows in Western NSW, primarily the X2 line from Broken Hill to Buronga, surrounding 220 kV network elements, and upstream network flows through the Buronga substation that connect western NSW with the broader NSW, South Australia and Victorian transmission systems. In the 12 months prior to the connection of Broken Hill BESS, the constraint equation associated with the Network Support Agreement for islanded operation of the Broken Hill region following an outage of the X2 (Broken Hill to Buronga) 220 kV transmission line was not binding. In the 12 months following the connection of Broken Hill BESS, the constraint equation was binding for approximately 92.4 hours. This reflects the introduction of Broken Hill BESS as a network support asset and its role in maintaining security of supply to the Broken Hill region during islanded operation following an X2 transmission line outage. Constraints associated with operation with a single Broken Hill 220/22 kV transformer in service were collectively binding for approximately 42.2 hours in 2024 compared with 32.5 hours in 2025. These constraints are primarily driven by network topology, local demand and generation conditions during transformer outage scenarios. Although the charging and discharging operation of Broken Hill BESS can influence local power flows and transformer loading, the constraint outcomes cannot be attributed solely to the BESS. There are a number of factors that can affect the binding of transformer, Broken Hill Solar Farm and X2-related constraint equations, including: - the relative operation of the existing generating units in Central NSW - NEM dispatch price in NSW. - network outages (planned and unplanned) significantly impact the power transfer limits. These factors generally have a greater influence on network utilisation than the output of any individual generator. Constraint outcomes in NEMDE reflect the combined impact of many generators and network conditions and therefore cannot be attributed solely to a single generating unit. Broken Hill BESS has become an important network support asset for the Broken Hill region. In addition to supporting system security during outages of the X2 transmission line, the charging and discharging operation of the BESS can influence transmission flows, transformer loading, and network conditions across the wider western NSW transmission network.There are no remedial action schemes currently applied for Broken Hill BESS. | No project timings have been affected by the inclusion of the Broken Hill BESS. | Broken Hill BESS participates in constraint equations associated with the Balranald to Buronga (X3) corridor, indicating that its charging and discharging operation can influence power flows between western NSW and the broader NSW-Victorian-South Australian transmission network. As a load when charging and a source of generation when discharging, the BESS can influence power flows through the Broken Hill and Buronga network hub and associated transmission lines. The constraint equation, which manages loading on the Balranald to Buronga (X3) 220 kV transmission line, was binding for approximately 0.5 hours in 2024, compared to approximately 2.33 hours in 2025. The constraint includes a Broken Hill BESS participation factor, demonstrating that operation of the BESS can influence loading on the Balranald to Buronga (X3) 220 kV transmission corridor. Other X3-related constraint equations associated with outages of the Ararat-Waubra and Ararat-Crowlands 220 kV transmission lines were binding for limited periods. However, the occurrence of these constraints is influenced by a range of factors including interconnector flows, generation dispatch, regional demand and network outages. Accordingly, the binding of these constraints cannot be attributed solely to operation of the Broken Hill BESS.
Note on D1: Dragana Hele: Compare it with constraint spreadsheet