## Overview of the model
Transgrid System Strength MCC assessment
| Creation Date | 2026-08-24
| Client | Transgrid
| Description | System strength MCC model
| Scenario | Proponent advised coal retirement date scenario
Creators
Cell legend applied throughout the model
Table Row Name
Input Cell
Calculation cell
Parameter Cell
Output Cell

## R1 Interface and results
R1 Interface and results
Interface for scenario settings and key results
Scenario settings
Parameters
| General parameters |  |  |  | Unit | Value
| Commercial discount rate |  |  |  | Percent | 7% | Source: 2025 Inputs, Assumptions and Scenarios Report, AEMO, August 2025
| Weighted Average Cost of Capital (regulated) | Network Synchronous Condensers |  |  | Percent | 3% | Source: 2025 Inputs, Assumptions and Scenarios Report, AEMO, August 2025
| Weighted Average Cost of Capital (BESS) | ISP-modelled battery, converted to grid-forming |  |  | Percent | 8% | Source: 2025 Inputs, Assumptions and Scenarios Report, AEMO, August 2025
Headline NPV chart: Including grid-forming BESS for the minimum level
NPV
| Net present value ($m, PV) | Total benefit |  | Incremental benefit of acceleration |  | Total benefit |  | Grid-forming BESS included. Net present value breakdown ($m, PV)
| Portfolio | Assumed synchronous condenser timing |  | Accelerated synchronous condenser timing |  | Accelerated synchronous condenser timing (total) |  | Portfolio | Capex | Opex | Avoided involuntary load shedding | Avoided fuel costs | Avoided cost for non-RIT-T proponent parties | Avoided value of greenhouse gas emissions | Total
| Portfolio option 3b - assumed timing | 37515.0177 | Portfolio option 3b - accelerated timing | 442.0255 | Portfolio option 3b - accelerated timing | 37957.0432 |  | Accelerated Portfolio option 4a (No GFM BESS) | -423.4442 | -58.7269 | 37149.5553 | 298.6069 | 477.4672 | 401.1195 | 37844.5779
| Portfolio option 4b - assumed timing | 37444.9337 | Portfolio option 4b - accelerated timing | 412.6143 | Portfolio option 4b - accelerated timing | 37857.548 |  | Portfolio option 3b - accelerated timing | -349.8548 | -44.0452 | 37149.5553 | 298.6069 | 501.6615 | 401.1195 | 37957.0432
| Portfolio option 5b - assumed timing | 37365.3756 | Portfolio option 5b - accelerated timing | 384.7718 | Portfolio option 5b - accelerated timing | 37750.1474 |  | Portfolio option 3b compared to Portfolio option 4a | 73.5894 | 14.6817 | 0 | 0 | 24.1942 | 0 | 112.4654
[10 empty] | Portfolio option 4a to the base case |  |  | Portfolio option 3b to Portfolio option 4a
Labels
Portfolio Option 3b
Portfolio Option 4b
Portfolio Option 5b
[9 empty] | Capex | Opex | Avoided involuntary load curtailment | Avoided fuel costs | Avoided cost for non-RIT-T proponent parties | Avoided value of greenhouse gas emissions
Headline NPV chart: Excluding grid-forming BESS for the minimum level
| Net present value ($m, PV) | Total benefit |  | Incremental benefit of acceleration |  | Total benefit
| Portfolio | Assumed synchronous condenser timing |  | Accelerated synchronous condenser timing |  | Accelerated synchronous condenser timing (total)
| Assumed Portfolio option 1a (No GFM BESS) | 622.2636 | Accelerated Portfolio option 1a (No GFM BESS) | 494.1527 | Accelerated (total benefits) | 1116.4163
| Assumed Portfolio option 2a (No GFM BESS) | 20241.4546 | Accelerated Portfolio option 2a (No GFM BESS) | 473.6297 | Accelerated (total benefits) | 20715.0843
| Assumed Portfolio option 3a (No GFM BESS) | 37212.0997 | Accelerated Portfolio option 3a (No GFM BESS) | 444.4928 | Accelerated (total benefits) | 37656.5924
| Assumed Portfolio option 4a (No GFM BESS) | 37429.9456 | Accelerated Portfolio option 4a (No GFM BESS) | 414.6323 | Accelerated (total benefits) | 37844.5779
| Assumed Portfolio option 5a (No GFM BESS) | 37365.3756 | Accelerated Portfolio option 5a (No GFM BESS) | 384.7718 | Accelerated (total benefits) | 37750.1474
Label
Portfolio option 1a
Portfolio option 2a
Portfolio option 3a
Portfolio option 4a
Portfolio option 5a
30% lower synchronous condenser cost sensitivity
| Net present value ($m) | Total benefit |  | Incremental benefit of acceleration |  | Total benefit
| Portfolio | Assumed synchronous condenser timing |  | Accelerated synchronous condenser timing |  | Accelerated synchronous condenser timing (total)
| Portfolio option 3b - assumed timing | 37596.6318 | Portfolio option 3b - accelerated timing | 468.8999 | Portfolio option 3b - accelerated timing | 38065.5317
| Portfolio option 4b - assumed timing | 37553.7525 | Portfolio option 4b - accelerated timing | 448.4469 | Portfolio option 4b - accelerated timing | 38002.1993
| Portfolio option 5b - assumed timing | 37501.3991 | Portfolio option 5b - accelerated timing | 429.5625 | Portfolio option 5b - accelerated timing | 37930.9616
| Labels | Labels
| Portfolio Option 3b | Portfolio Option 3b
| Portfolio Option 4b | Portfolio Option 4b
| Portfolio Option 5b | Portfolio Option 5b
40% higher synchronous condenser cost sensitivity
| Net present value ($m) | Total benefit |  | Incremental benefit of acceleration |  | Total benefit
| Portfolio | Assumed synchronous condenser timing |  | Accelerated synchronous condenser timing |  | Accelerated synchronous condenser timing (total)
| Portfolio option 3b - assumed timing | 37406.199 | Portfolio option 3b - accelerated timing | 406.1929 | Portfolio option 3b - accelerated timing | 37812.3919
| Portfolio option 4b - assumed timing | 37299.842 | Portfolio option 4b - accelerated timing | 364.8375 | Portfolio option 4b - accelerated timing | 37664.6796
| Portfolio option 5b - assumed timing | 37184.011 | Portfolio option 5b - accelerated timing | 325.0508 | Portfolio option 5b - accelerated timing | 37509.0619
Labels
Portfolio Option 3b
Portfolio Option 4b
Portfolio Option 5b
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.
This chart isn't available in your version of Excel. Editing this shape or saving this workbook into a different file format will permanently break the chart.

## R2 Tables for report
R2 Tables for report
Outputs
Summary tables for report
Summary expenditure table (NPV $m)
| Item | Expenditure | Portfolio option 3b - accelerated timing | Portfolio option 3b - assumed timing | Portfolio option 4b - accelerated timing | Portfolio option 4b - assumed timing | Portfolio option 5b - accelerated timing | Portfolio option 5b - assumed timing
| Network Synchronous Condensers | CAPEX | 317.5832 | 238.9124 | 423.4442 | 318.5499 | 529.3053 | 398.1874
| Network Synchronous Condensers | OPEX | 44.0452 | 33.1344 | 58.7269 | 44.1793 | 73.4086 | 55.2241
|  | Total | 361.6283 | 272.0469 | 482.1711 | 362.7292 | 602.7139 | 453.4115
| ISP-modelled battery, converted to grid-forming | CAPEX | 32.2717 | 32.2717 | 10.7572 | 10.7572 | 0 | 0
| ISP-modelled battery, converted to grid-forming | OPEX | 0 | 0 | 0 | 0 | 0 | 0
|  | Total | 32.2717 | 32.2717 | 10.7572 | 10.7572 | 0 | 0
| Re-dispatch from synchronous generators | OPEX | 2.9435 | 534.5504 | 3.4104 | 535.4666 | 1.0254 | 535.0996
| Total | CAPEX | 349.8548 | 271.1841 | 434.2014 | 329.3072 | 529.3053 | 398.1874
| Total | OPEX | 46.9886 | 567.6848 | 62.1373 | 579.6458 | 74.434 | 590.3237
| Total | Total | 396.8434 | 838.8689 | 496.3387 | 908.953 | 603.7393 | 988.5111

## I1 General Inputs
I1 General Inputs
Inputs and parameters for System Strength MCC assessment
General parameter and Portfolio inputs
General parameters
| Parameter | Unit | Value | Note
| First year of analysis | Year | 2026 | Earliest initiation of project portfolios
| Base year for dollar inputs | Year | 2025 | All costs are based in 30 June 2025 dollars as per Draft 2026 Integrated System Plan
| Analysis period | Years | 25
| Years for synchronous condenser capex | Years | 3
Option descriptions
| Option name | Short description
| Base case | No synchronous condenser or grid-forming BESS for the minimum level
| Assumed Portfolio option 1a (No GFM BESS) | 1 synchronous condenser in FY34, no grid-forming BESS for the minimum level
| Assumed Portfolio option 2a (No GFM BESS) | 2 synchronous condensers in FY34, no grid-forming BESS for the minimum level
| Assumed Portfolio option 3a (No GFM BESS) | 3 synchronous condensers in FY34, no grid-forming BESS for the minimum level
| Assumed Portfolio option 4a (No GFM BESS) | 4 synchronous condensers in FY34, no grid-forming BESS for the minimum level
| Assumed Portfolio option 5a (No GFM BESS) | 5 synchronous condensers in FY34, no grid-forming BESS for the minimum level
| Accelerated Portfolio option 1a (No GFM BESS) | 1 synchronous condenser in FY31, no grid-forming BESS for the minimum level
| Accelerated Portfolio option 2a (No GFM BESS) | 2 synchronous condensers in FY31, no grid-forming BESS for the minimum level
| Accelerated Portfolio option 3a (No GFM BESS) | 3 synchronous condensers in FY31, no grid-forming BESS for the minimum level
| Accelerated Portfolio option 4a (No GFM BESS) | 4 synchronous condensers in FY31, no grid-forming BESS for the minimum level
| Accelerated Portfolio option 5a (No GFM BESS) | 5 synchronous condensers in FY31, no grid-forming BESS for the minimum level
| Portfolio option 3b - assumed timing | 3 synchronous condensers in FY34, 900 MW grid-forming BESS for the minimum level
| Portfolio option 4b - assumed timing | 4 synchronous condensers in FY34, 400 MW grid-forming BESS for the minimum level
| Portfolio option 5b - assumed timing | 5 synchronous condensers in FY34, 0 MW grid-forming BESS for the minimum level
| Portfolio option 3b - accelerated timing | 3 synchronous condensers in FY31, 900 MW grid-forming BESS for the minimum level
| Portfolio option 4b - accelerated timing | 4 synchronous condensers in FY31, 400 MW grid-forming BESS for the minimum level
| Portfolio option 5b - accelerated timing | 5 synchronous condensers in FY31, 0 MW grid-forming BESS for the minimum level
Cost and benefit categories
Cost categories
Capital cost
Operating cost
| Benefit categories |  |  | Benefit input category
| Avoided involuntary load shedding |  |  | Involuntary load shedding
| Avoided fuel consumption from generation dispatch |  |  | Fuel costs
| Avoided costs for non RIT-T proponent parties |  |  | Cost for non-RIT-T proponent parties
| Value of avoided greenhouse gas emissions |  |  | Value of greenhouse gas emissions
RIT market benefits
| NER | RIT-T market benefits
| 5.15A.2(c)(4)(i) | changes in fuel consumption arising through different patterns of generation dispatch
| 5.15A.2(c)(4)(ii) | changes in voluntary load curtailment
| 5.15A.2(c)(4)(iii) | changes in involuntary load shedding
| 5.15A.2(c)(4)(iv) | changes in costs for parties, other than the RIT-T proponent
| 5.15A.2(c)(4)(v) | differences in the timing of expenditure
| 5.15A.2(c)(4)(vi) | changes in network losses
| 5.15A.2(c)(4)(vii) | changes in ancillary services costs
| 5.15A.2(c)(4)(viii) | competition benefits
| 5.15A.2(c)(4)(ix) | any additional option value

## I2 Benefits - no GFM BESS
Benefits - Portfolios excluding grid-forming BESS contribution to the minimum level
Summary of benefits under the assumed synchronous condenser timing and accelerated synchronous condenser timing scenarios
Avoided costs ($2024/25)
Assumed synchronous condenser timing scenario
Avoided involuntary load shedding
| Portfolio name | Unit | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
Avoided involuntary load shedding | Base case | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoided involuntary load shedding | Assumed Portfolio option 1a (No GFM BESS) | $, real | 705187517.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90711256.7258 | 90711256.7258 | 90711256.7258 | 90711256.7258 | 90711256.7258 | 90711256.7258 | 90711256.7258 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213
Avoided involuntary load shedding | Assumed Portfolio option 2a (No GFM BESS) | $, real | 20357123463.1011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3470683998.9451 | 2772781333.944 | 2772781333.944 | 2772781333.944 | 2772781333.944 | 2772781333.944 | 2772781333.944 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396
Avoided involuntary load shedding | Assumed Portfolio option 3a (No GFM BESS) | $, real | 37149555343.6687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7207480482.1104 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491
Avoided involuntary load shedding | Assumed Portfolio option 4a (No GFM BESS) | $, real | 37149555343.6687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7207480482.1104 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491
Avoided involuntary load shedding | Assumed Portfolio option 5a (No GFM BESS) | $, real | 37149555343.6687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7207480482.1104 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491
Avoided fuel costs
| Portfolio name | Unit | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
Avoided fuel costs | Base case | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoided fuel costs | Assumed Portfolio option 1a (No GFM BESS) | $, real | -2.7105e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9802e-08 | -5.9605e-08 | -2.9802e-08 | 0 | -5.9605e-08 | -5.9605e-08 | -2.9802e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08
Avoided fuel costs | Assumed Portfolio option 2a (No GFM BESS) | $, real | -1.6278e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.4703e-08 | -5.2154e-08 | 0 | 0 | -5.2154e-08 | -3.7253e-08 | 0 | -2.9802e-08 | -2.9802e-08 | -2.9802e-08 | -2.9802e-08 | -2.9802e-08 | -2.9802e-08 | -2.9802e-08 | -2.9802e-08 | -2.9802e-08 | -2.9802e-08
Avoided fuel costs | Assumed Portfolio option 3a (No GFM BESS) | $, real | 60136480.8254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6778877.0941 | 13824514.4476 | 13570716.1519 | 12789602.4899 | 13426767.8101 | 13680658.582 | 14402504.0519 | 8327121.2764 | 8327121.2764 | 8327121.2764 | 8327121.2764 | 8327121.2764 | 8327121.2764 | 8327121.2764 | 8327121.2764 | 8327121.2764 | 8327121.2764
Avoided fuel costs | Assumed Portfolio option 4a (No GFM BESS) | $, real | 110714112.8738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18295287.0608 | 19151233.3979 | 18799644.1674 | 17717559.8665 | 18600231.139 | 18951948.4778 | 19951927.9796 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565
Avoided fuel costs | Assumed Portfolio option 5a (No GFM BESS) | $, real | 110714112.8738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18295287.0608 | 19151233.3979 | 18799644.1674 | 17717559.8665 | 18600231.139 | 18951948.4778 | 19951927.9796 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565
Avoided cost for non-RIT-T proponent parties
| Portfolio name | Unit | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
Avoided cost for non-RIT-T proponent parties | Base case | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoided cost for non-RIT-T proponent parties | Assumed Portfolio option 1a (No GFM BESS) | $, real | 7758394.9931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2353703.5687 | 2498623.746 | 2498623.746 | 2498623.746 | 2498623.746 | 2498623.746 | 2498623.746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoided cost for non-RIT-T proponent parties | Assumed Portfolio option 2a (No GFM BESS) | $, real | 65695722.7683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29403869.9959 | 19170098.9117 | 19170098.9117 | 19170098.9117 | 19170098.9117 | 19170098.9117 | 19170098.9117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoided cost for non-RIT-T proponent parties | Assumed Portfolio option 3a (No GFM BESS) | $, real | 224315643.4947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40600368.905 | 42359077.6084 | 42359077.6084 | 42359077.6084 | 42359077.6084 | 42359077.6084 | 42359077.6084 | 36300131.2706 | 36300131.2706 | 36300131.2706 | 36300131.2706 | 36300131.2706 | 36300131.2706 | 36300131.2706 | 36300131.2706 | 36300131.2706 | 36300131.2706
Avoided cost for non-RIT-T proponent parties | Assumed Portfolio option 4a (No GFM BESS) | $, real | 438784535.2149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71469224.6174 | 67270550.4254 | 67270550.4254 | 67270550.4254 | 67270550.4254 | 67270550.4254 | 67270550.4254 | 88581378.108 | 88581378.108 | 88581378.108 | 88581378.108 | 88581378.108 | 88581378.108 | 88581378.108 | 88581378.108 | 88581378.108 | 88581378.108
Avoided cost for non-RIT-T proponent parties | Assumed Portfolio option 5a (No GFM BESS) | $, real | 464896838.4251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84665245.659 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282
Avoided value of greenhouse gas emissions
| Portfolio name | Unit | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
Avoided value of greenhouse gas emissions | Base case | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoided value of greenhouse gas emissions | Assumed Portfolio option 1a (No GFM BESS) | $, real | -5.9841e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9802e-08 | -1.4901e-08 | -1.4901e-08 | -1.4901e-08 | 0 | -2.9802e-08 | -2.9802e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoided value of greenhouse gas emissions | Assumed Portfolio option 2a (No GFM BESS) | $, real | -2.3792e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.4703e-08 | -1.4901e-08 | -2.2352e-08 | -2.2352e-08 | -1.4901e-08 | -2.2352e-08 | -5.2154e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08
Avoided value of greenhouse gas emissions | Assumed Portfolio option 3a (No GFM BESS) | $, real | 50139098.8856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4338463.8451 | 9113955.3586 | 9805773.7521 | 10527671.2062 | 11279647.721 | 12061703.2963 | 12873837.9322 | 7773462.6606 | 7773462.6606 | 7773462.6606 | 7773462.6606 | 7773462.6606 | 7773462.6606 | 7773462.6606 | 7773462.6606 | 7773462.6606 | 7773462.6606
Avoided value of greenhouse gas emissions | Assumed Portfolio option 4a (No GFM BESS) | $, real | 93620812.0989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11708936.5018 | 12625650.3916 | 13584033.0946 | 14584084.6108 | 15625804.9402 | 16709194.0827 | 17834252.0384 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204
Avoided value of greenhouse gas emissions | Assumed Portfolio option 5a (No GFM BESS) | $, real | 93620812.0989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11708936.5018 | 12625650.3916 | 13584033.0946 | 14584084.6108 | 15625804.9402 | 16709194.0827 | 17834252.0384 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204
Accelerated synchronous condenser timing scenario
Avoided involuntary load shedding
| Portfolio name | Unit | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Base case | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoided involuntary load shedding | Accelerated Portfolio option 1a (No GFM BESS) | $, real | 705187517.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90711256.7258 | 90711256.7258 | 90711256.7258 | 90711256.7258 | 90711256.7258 | 90711256.7258 | 90711256.7258 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213
Avoided involuntary load shedding | Accelerated Portfolio option 2a (No GFM BESS) | $, real | 20357123463.1011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3470683998.9451 | 2772781333.944 | 2772781333.944 | 2772781333.944 | 2772781333.944 | 2772781333.944 | 2772781333.944 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396
Avoided involuntary load shedding | Accelerated Portfolio option 3a (No GFM BESS) | $, real | 37149555343.6687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7207480482.1104 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491
Avoided involuntary load shedding | Accelerated Portfolio option 4a (No GFM BESS) | $, real | 37149555343.6687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7207480482.1104 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491
Avoided involuntary load shedding | Accelerated Portfolio option 5a (No GFM BESS) | $, real | 37149555343.6687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7207480482.1104 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491
Avoided fuel costs
| Portfolio name | Unit | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Base case | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoided fuel costs | Accelerated Portfolio option 1a (No GFM BESS) | $, real | 187248953.371 | 0 | 0 | 0 | 0 | 0 | 107859936.2111 | 97720323.616 | 93678976.6328 | -2.9802e-08 | -5.9605e-08 | -2.9802e-08 | 0 | -5.9605e-08 | -5.9605e-08 | -2.9802e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08
Avoided fuel costs | Accelerated Portfolio option 2a (No GFM BESS) | $, real | 187892748.7604 | 0 | 0 | 0 | 0 | 0 | 108311622.5823 | 98009904.5197 | 93958149.6801 | -4.4703e-08 | -5.2154e-08 | 0 | 0 | -5.2154e-08 | -3.7253e-08 | 0 | -2.9802e-08 | -2.9802e-08 | -2.9802e-08 | -2.9802e-08 | -2.9802e-08 | -2.9802e-08 | -2.9802e-08 | -2.9802e-08 | -2.9802e-08 | -2.9802e-08
Avoided fuel costs | Accelerated Portfolio option 3a (No GFM BESS) | $, real | 248029229.5858 | 0 | 0 | 0 | 0 | 0 | 108311622.5823 | 98009904.5197 | 93958149.6801 | 6778877.0941 | 13824514.4476 | 13570716.1519 | 12789602.4899 | 13426767.8101 | 13680658.582 | 14402504.0519 | 8327121.2764 | 8327121.2764 | 8327121.2764 | 8327121.2764 | 8327121.2764 | 8327121.2764 | 8327121.2764 | 8327121.2764 | 8327121.2764 | 8327121.2764
Avoided fuel costs | Accelerated Portfolio option 4a (No GFM BESS) | $, real | 298606861.6342 | 0 | 0 | 0 | 0 | 0 | 108311622.5823 | 98009904.5197 | 93958149.6801 | 18295287.0608 | 19151233.3979 | 18799644.1674 | 17717559.8665 | 18600231.139 | 18951948.4778 | 19951927.9796 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565
Avoided fuel costs | Accelerated Portfolio option 5a (No GFM BESS) | $, real | 298606861.6342 | 0 | 0 | 0 | 0 | 0 | 108311622.5823 | 98009904.5197 | 93958149.6801 | 18295287.0608 | 19151233.3979 | 18799644.1674 | 17717559.8665 | 18600231.139 | 18951948.4778 | 19951927.9796 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565
Avoided cost for non-RIT-T proponent parties
| Portfolio name | Unit | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Base case | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoided cost for non-RIT-T proponent parties | Accelerated Portfolio option 1a (No GFM BESS) | $, real | 37345507.1464 | 0 | 0 | 0 | 0 | 0 | 17878150.9112 | 14720746.8013 | 14616273.1474 | 2353703.5687 | 2498623.746 | 2498623.746 | 2498623.746 | 2498623.746 | 2498623.746 | 2498623.746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoided cost for non-RIT-T proponent parties | Accelerated Portfolio option 2a (No GFM BESS) | $, real | 103654882.2234 | 0 | 0 | 0 | 0 | 0 | 25052139.8191 | 17702020.2651 | 17597546.6112 | 29403869.9959 | 19170098.9117 | 19170098.9117 | 19170098.9117 | 19170098.9117 | 19170098.9117 | 19170098.9117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoided cost for non-RIT-T proponent parties | Accelerated Portfolio option 3a (No GFM BESS) | $, real | 262998355.2771 | 0 | 0 | 0 | 0 | 0 | 25899041.7624 | 17834184.3107 | 17729710.6567 | 40600368.905 | 42359077.6084 | 42359077.6084 | 42359077.6084 | 42359077.6084 | 42359077.6084 | 42359077.6084 | 36300131.2706 | 36300131.2706 | 36300131.2706 | 36300131.2706 | 36300131.2706 | 36300131.2706 | 36300131.2706 | 36300131.2706 | 36300131.2706 | 36300131.2706
Avoided cost for non-RIT-T proponent parties | Accelerated Portfolio option 4a (No GFM BESS) | $, real | 477467246.9973 | 0 | 0 | 0 | 0 | 0 | 25899041.7624 | 17834184.3107 | 17729710.6567 | 71469224.6174 | 67270550.4254 | 67270550.4254 | 67270550.4254 | 67270550.4254 | 67270550.4254 | 67270550.4254 | 88581378.108 | 88581378.108 | 88581378.108 | 88581378.108 | 88581378.108 | 88581378.108 | 88581378.108 | 88581378.108 | 88581378.108 | 88581378.108
Avoided cost for non-RIT-T proponent parties | Accelerated Portfolio option 5a (No GFM BESS) | $, real | 503579550.2075 | 0 | 0 | 0 | 0 | 0 | 25899041.7624 | 17834184.3107 | 17729710.6567 | 84665245.659 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282
Avoided value of greenhouse gas emissions
| Portfolio name | Unit | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Base case | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoided value of greenhouse gas emissions | Accelerated Portfolio option 1a (No GFM BESS) | $, real | 307177120.3538 | 0 | 0 | 0 | 0 | 0 | 164420115.5948 | 163480542.6539 | 164618711.9683 | -2.9802e-08 | -1.4901e-08 | -1.4901e-08 | -1.4901e-08 | 0 | -2.9802e-08 | -2.9802e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoided value of greenhouse gas emissions | Accelerated Portfolio option 2a (No GFM BESS) | $, real | 307498728.8693 | 0 | 0 | 0 | 0 | 0 | 164626180.8766 | 163627263.9898 | 164778379.3044 | -4.4703e-08 | -1.4901e-08 | -2.2352e-08 | -2.2352e-08 | -1.4901e-08 | -2.2352e-08 | -5.2154e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08 | -5.9605e-08
Avoided value of greenhouse gas emissions | Accelerated Portfolio option 3a (No GFM BESS) | $, real | 357637827.7549 | 0 | 0 | 0 | 0 | 0 | 164626180.8766 | 163627263.9898 | 164778379.3044 | 4338463.8451 | 9113955.3586 | 9805773.7521 | 10527671.2062 | 11279647.721 | 12061703.2963 | 12873837.9322 | 7773462.6606 | 7773462.6606 | 7773462.6606 | 7773462.6606 | 7773462.6606 | 7773462.6606 | 7773462.6606 | 7773462.6606 | 7773462.6606 | 7773462.6606
Avoided value of greenhouse gas emissions | Accelerated Portfolio option 4a (No GFM BESS) | $, real | 401119540.9682 | 0 | 0 | 0 | 0 | 0 | 164626180.8766 | 163627263.9898 | 164778379.3044 | 11708936.5018 | 12625650.3916 | 13584033.0946 | 14584084.6108 | 15625804.9402 | 16709194.0827 | 17834252.0384 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204
Avoided value of greenhouse gas emissions | Accelerated Portfolio option 5a (No GFM BESS) | $, real | 401119540.9682 | 0 | 0 | 0 | 0 | 0 | 164626180.8766 | 163627263.9898 | 164778379.3044 | 11708936.5018 | 12625650.3916 | 13584033.0946 | 14584084.6108 | 15625804.9402 | 16709194.0827 | 17834252.0384 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204

## I3 Benefits - with GFM BESS
Benefits - Portfolios including grid-forming BESS contribution to the minimum level
Summary of benefits under the assumed synchronous condenser timing and accelerated synchronous condenser timing scenarios
Avoided costs ($2024/25)
Avoided involuntary load shedding
| Portfolio name | Unit | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Base case | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 3b - assumed timing | $, real | 37149555343.6687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7207480482.1104 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491
| Portfolio option 4b - assumed timing | $, real | 37149555343.6687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7207480482.1104 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491
| Portfolio option 5b - assumed timing | $, real | 37149555343.6687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7207480482.1104 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491
| Portfolio option 3b - accelerated timing | $, real | 37149555343.6687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7207480482.1104 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491
| Portfolio option 4b - accelerated timing | $, real | 37149555343.6687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7207480482.1104 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491
| Portfolio option 5b - accelerated timing | $, real | 37149555343.6687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7207480482.1104 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491
Avoided fuel costs
| Portfolio name | Unit | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Base case | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 3b - assumed timing | $, real | 110962110.5792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 426106.2301 | 18295287.0608 | 19151233.3979 | 18799644.1674 | 17717559.8665 | 18600231.139 | 18951948.4778 | 19951927.9796 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565
| Portfolio option 4b - assumed timing | $, real | 110962110.5792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 426106.2301 | 18295287.0608 | 19151233.3979 | 18799644.1674 | 17717559.8665 | 18600231.139 | 18951948.4778 | 19951927.9796 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565
| Portfolio option 5b - assumed timing | $, real | 110714112.8738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18295287.0608 | 19151233.3979 | 18799644.1674 | 17717559.8665 | 18600231.139 | 18951948.4778 | 19951927.9796 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565
| Portfolio option 3b - accelerated timing | $, real | 298606861.6342 | 0 | 0 | 0 | 0 | 0 | 108311622.5823 | 98009904.5197 | 93958149.6801 | 18295287.0608 | 19151233.3979 | 18799644.1674 | 17717559.8665 | 18600231.139 | 18951948.4778 | 19951927.9796 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565
| Portfolio option 4b - accelerated timing | $, real | 298606861.6342 | 0 | 0 | 0 | 0 | 0 | 108311622.5823 | 98009904.5197 | 93958149.6801 | 18295287.0608 | 19151233.3979 | 18799644.1674 | 17717559.8665 | 18600231.139 | 18951948.4778 | 19951927.9796 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565
| Portfolio option 5b - accelerated timing | $, real | 298606861.6342 | 0 | 0 | 0 | 0 | 0 | 108311622.5823 | 98009904.5197 | 93958149.6801 | 18295287.0608 | 19151233.3979 | 18799644.1674 | 17717559.8665 | 18600231.139 | 18951948.4778 | 19951927.9796 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565
Avoided cost for non-RIT-T proponent parties
| Portfolio name | Unit | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Base case | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 3b - assumed timing | $, real | 465056198.9077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3569395.388 | 84597256.7918 | 69399838.1297 | 69399838.1297 | 69399838.1297 | 69399838.1297 | 69399838.1297 | 69399838.1297 | 93111777.479 | 93111777.479 | 93111777.479 | 93111777.479 | 93111777.479 | 93111777.479 | 93111777.479 | 93111777.479 | 93111777.479 | 93111777.479
| Portfolio option 4b - assumed timing | $, real | 464140013.195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2797452.157 | 84603437.5979 | 69341120.4717 | 69341120.4717 | 69341120.4717 | 69341120.4717 | 69341120.4717 | 69341120.4717 | 92986846.2917 | 92986846.2917 | 92986846.2917 | 92986846.2917 | 92986846.2917 | 92986846.2917 | 92986846.2917 | 92986846.2917 | 92986846.2917 | 92986846.2917
| Portfolio option 5b - assumed timing | $, real | 464896838.4251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84665245.659 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282
| Portfolio option 3b - accelerated timing | $, real | 501661490.0765 | 0 | 0 | 0 | 0 | 0 | 25899041.7624 | 17834184.3107 | 17729710.6567 | 84597256.7918 | 69399838.1297 | 69399838.1297 | 69399838.1297 | 69399838.1297 | 69399838.1297 | 69399838.1297 | 93111777.479 | 93111777.479 | 93111777.479 | 93111777.479 | 93111777.479 | 93111777.479 | 93111777.479 | 93111777.479 | 93111777.479 | 93111777.479
| Portfolio option 4b - accelerated timing | $, real | 501194582.3524 | 0 | 0 | 0 | 0 | 0 | 25899041.7624 | 17834184.3107 | 17729710.6567 | 84603437.5979 | 69341120.4717 | 69341120.4717 | 69341120.4717 | 69341120.4717 | 69341120.4717 | 69341120.4717 | 92986846.2917 | 92986846.2917 | 92986846.2917 | 92986846.2917 | 92986846.2917 | 92986846.2917 | 92986846.2917 | 92986846.2917 | 92986846.2917 | 92986846.2917
| Portfolio option 5b - accelerated timing | $, real | 503579550.2075 | 0 | 0 | 0 | 0 | 0 | 25899041.7624 | 17834184.3107 | 17729710.6567 | 84665245.659 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282
Avoided value of greenhouse gas emissions
| Portfolio name | Unit | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Base case | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 3b - assumed timing | $, real | 93762649.3334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243702.7762 | 11708936.5018 | 12625650.3916 | 13584033.0946 | 14584084.6108 | 15625804.9402 | 16709194.0827 | 17834252.0384 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204
| Portfolio option 4b - assumed timing | $, real | 93762649.3334 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243702.7762 | 11708936.5018 | 12625650.3916 | 13584033.0946 | 14584084.6108 | 15625804.9402 | 16709194.0827 | 17834252.0384 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204
| Portfolio option 5b - assumed timing | $, real | 93620812.0989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11708936.5018 | 12625650.3916 | 13584033.0946 | 14584084.6108 | 15625804.9402 | 16709194.0827 | 17834252.0384 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204
| Portfolio option 3b - accelerated timing | $, real | 401119540.9682 | 0 | 0 | 0 | 0 | 0 | 164626180.8766 | 163627263.9898 | 164778379.3044 | 11708936.5018 | 12625650.3916 | 13584033.0946 | 14584084.6108 | 15625804.9402 | 16709194.0827 | 17834252.0384 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204
| Portfolio option 4b - accelerated timing | $, real | 401119540.9682 | 0 | 0 | 0 | 0 | 0 | 164626180.8766 | 163627263.9898 | 164778379.3044 | 11708936.5018 | 12625650.3916 | 13584033.0946 | 14584084.6108 | 15625804.9402 | 16709194.0827 | 17834252.0384 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204
| Portfolio option 5b - accelerated timing | $, real | 401119540.9682 | 0 | 0 | 0 | 0 | 0 | 164626180.8766 | 163627263.9898 | 164778379.3044 | 11708936.5018 | 12625650.3916 | 13584033.0946 | 14584084.6108 | 15625804.9402 | 16709194.0827 | 17834252.0384 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204

## Inputs -->
All following sheets (with exception for the final sheet C1) contain inputs into the net economic benefits assessment for all cost and benefit categories specified on sheet I1 General Inputs

## No GFM BESS assessment -->
The following sheets contain the cost and benefit inputs for portfolios in stage (a) of the MCC assessment (i.e. portfolios which exclude grid-forming BESS towards minimum level requirements)

## No GFM BESS. Capex
CAPEX - Portfolios excluding grid-forming BESS contribution to the minimum level
Capex inputs for System Strength RIT-T assessment
| Capex inputs | [6 empty] | All years refer to financial years
| Transgrid capex inputs | [5 empty] | Calculations
|  | Unit | Value
| Synchronous condenser cost | $ real 2024/25 | 323954597.79
Assumed synchronous condenser timing scenario
| Capital cost ($2024/25) | [5 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Assumed Portfolio option 1a (No GFM BESS) | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Assumed Portfolio option 2a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Assumed Portfolio option 2a (No GFM BESS) | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Assumed Portfolio option 3a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Assumed Portfolio option 3a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Assumed Portfolio option 3a (No GFM BESS) | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Assumed Portfolio option 4a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Assumed Portfolio option 4a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Assumed Portfolio option 4a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Assumed Portfolio option 4a (No GFM BESS) | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Assumed Portfolio option 5a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Assumed Portfolio option 5a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Assumed Portfolio option 5a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Assumed Portfolio option 5a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 4 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Assumed Portfolio option 5a (No GFM BESS) | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
Accelerated synchronous condenser timing scenario
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Accelerated Portfolio option 1a (No GFM BESS) | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Accelerated Portfolio option 2a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Accelerated Portfolio option 2a (No GFM BESS) | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Accelerated Portfolio option 3a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Accelerated Portfolio option 3a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Accelerated Portfolio option 3a (No GFM BESS) | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Accelerated Portfolio option 4a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Accelerated Portfolio option 4a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Accelerated Portfolio option 4a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Accelerated Portfolio option 4a (No GFM BESS) | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Accelerated Portfolio option 5a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Accelerated Portfolio option 5a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Accelerated Portfolio option 5a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Accelerated Portfolio option 5a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 4 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Accelerated Portfolio option 5a (No GFM BESS) | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio | Undiscounted capex ($) | Undiscounted capex ($m) | Discounted capex ($) | Discounted capex ($m)
| Assumed Portfolio option 1a (No GFM BESS) | 323954597.79 | 323.9546 | 79637482.3647 | 79.6375
| Assumed Portfolio option 2a (No GFM BESS) | 647909195.58 | 647.9092 | 159274964.7293 | 159.275
| Assumed Portfolio option 3a (No GFM BESS) | 971863793.37 | 971.8638 | 238912447.094 | 238.9124
| Assumed Portfolio option 4a (No GFM BESS) | 1295818391.16 | 1295.8184 | 318549929.4586 | 318.5499
| Assumed Portfolio option 5a (No GFM BESS) | 1619772988.95 | 1619.773 | 398187411.8233 | 398.1874
| Accelerated Portfolio option 1a (No GFM BESS) | 323954597.79 | 323.9546 | 105861050.3635 | 105.8611
| Accelerated Portfolio option 2a (No GFM BESS) | 647909195.58 | 647.9092 | 211722100.7269 | 211.7221
| Accelerated Portfolio option 3a (No GFM BESS) | 971863793.37 | 971.8638 | 317583151.0904 | 317.5832
| Accelerated Portfolio option 4a (No GFM BESS) | 1295818391.16 | 1295.8184 | 423444201.4539 | 423.4442
| Accelerated Portfolio option 5a (No GFM BESS) | 1619772988.95 | 1619.773 | 529305251.8173 | 529.3053

## No GFM BESS. Opex
OPEX - Portfolios excluding grid-forming BESS contribution to the minimum level
Opex inputs and parameters for System Strength RIT-T assessment
| Operating cost inputs ($2023/24) | [7 empty] | All years refer to financial years
| Transgrid opex inputs | [5 empty] | Calculations
| Assumped opex | Unit | Value
| ISP modelled battery | % | 0% | Per cent of capex
| Network Synchronous Condensers | % | 0.6% | Per cent of capex
| Operating cost ($2024/25) | [7 empty] | Opex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex
| Assumed Portfolio option 1a (No GFM BESS) | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
Assumed synchronous condenser timing scenario
| Operating cost ($2024/25) | [7 empty] | Opex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex
| Assumed Portfolio option 2a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Assumed Portfolio option 2a (No GFM BESS) | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Operating cost ($2024/25) | [7 empty] | Opex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex
| Assumed Portfolio option 3a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Assumed Portfolio option 3a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Assumed Portfolio option 3a (No GFM BESS) | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Operating cost ($2024/25) | [7 empty] | Opex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex
| Assumed Portfolio option 4a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Assumed Portfolio option 4a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Assumed Portfolio option 4a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Assumed Portfolio option 4a (No GFM BESS) | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Operating cost ($2024/25) | [7 empty] | Opex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex
| Assumed Portfolio option 5a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Assumed Portfolio option 5a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Assumed Portfolio option 5a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Assumed Portfolio option 5a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 4 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Assumed Portfolio option 5a (No GFM BESS) | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
Accelerated synchronous condenser timing scenario
| Operating cost ($2024/25) | [7 empty] | Opex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex
| Accelerated Portfolio option 1a (No GFM BESS) | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Operating cost ($2024/25) | [7 empty] | Opex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex
| Accelerated Portfolio option 2a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Accelerated Portfolio option 2a (No GFM BESS) | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Operating cost ($2024/25) | [7 empty] | Opex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex
| Accelerated Portfolio option 3a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Accelerated Portfolio option 3a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Accelerated Portfolio option 3a (No GFM BESS) | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Operating cost ($2024/25) | [7 empty] | Opex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex
| Accelerated Portfolio option 4a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Accelerated Portfolio option 4a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Accelerated Portfolio option 4a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Accelerated Portfolio option 4a (No GFM BESS) | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Operating cost ($2024/25) | [7 empty] | Opex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex
| Accelerated Portfolio option 5a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Accelerated Portfolio option 5a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Accelerated Portfolio option 5a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Accelerated Portfolio option 5a (No GFM BESS) | Sydney/Newcastle Network Synchronous Condenser 4 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Accelerated Portfolio option 5a (No GFM BESS) | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Portfolio | Undiscounted opex ($) | Undiscounted opex ($m) | Discounted opex ($) | Discounted opex ($m)
| Assumed Portfolio option 1a (No GFM BESS) | 16197729.8895 | 16.1977 | 11044813.4728 | 11.0448
| Assumed Portfolio option 2a (No GFM BESS) | 32395459.779 | 32.3955 | 22089626.9455 | 22.0896
| Assumed Portfolio option 3a (No GFM BESS) | 48593189.6685 | 48.5932 | 33134440.4183 | 33.1344
| Assumed Portfolio option 4a (No GFM BESS) | 64790919.558 | 64.7909 | 44179253.891 | 44.1793
| Assumed Portfolio option 5a (No GFM BESS) | 80988649.4475 | 80.9886 | 55224067.3638 | 55.2241
| Accelerated Portfolio option 1a (No GFM BESS) | 16197729.8895 | 16.1977 | 14681724.2406 | 14.6817
| Accelerated Portfolio option 2a (No GFM BESS) | 32395459.779 | 32.3955 | 29363448.4812 | 29.3634
| Accelerated Portfolio option 3a (No GFM BESS) | 48593189.6685 | 48.5932 | 44045172.7218 | 44.0452
| Accelerated Portfolio option 4a (No GFM BESS) | 64790919.558 | 64.7909 | 58726896.9624 | 58.7269
| Accelerated Portfolio option 5a (No GFM BESS) | 80988649.4475 | 80.9886 | 73408621.203 | 73.4086

## No GFM BESS. Inputs
Inputs - Portfolios excluding grid-forming BESS contribution to the minimum level
Market benefit inputs for System Strength RIT-T assessment
Market benefit inputs ($2024/25)
Assumed synchronous condenser timing scenario
Involuntary load shedding
| Portfolio name | Unit | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Base case | $, real | 37149555343.6687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7207480482.1104 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491
| Assumed Portfolio option 1a (No GFM BESS) | $, real | 36444367825.9886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7116769225.3846 | 4324810679.4483 | 4324810679.4483 | 4324810679.4483 | 4324810679.4483 | 4324810679.4483 | 4324810679.4483 | 8390901450.7278 | 8390901450.7278 | 8390901450.7278 | 8390901450.7278 | 8390901450.7278 | 8390901450.7278 | 8390901450.7278 | 8390901450.7278 | 8390901450.7278 | 8390901450.7278
| Assumed Portfolio option 2a (No GFM BESS) | $, real | 16792431880.5676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3736796483.1653 | 1642740602.2301 | 1642740602.2301 | 1642740602.2301 | 1642740602.2301 | 1642740602.2301 | 1642740602.2301 | 4124950211.6095 | 4124950211.6095 | 4124950211.6095 | 4124950211.6095 | 4124950211.6095 | 4124950211.6095 | 4124950211.6095 | 4124950211.6095 | 4124950211.6095 | 4124950211.6095
| Assumed Portfolio option 3a (No GFM BESS) | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Assumed Portfolio option 4a (No GFM BESS) | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Assumed Portfolio option 5a (No GFM BESS) | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fuel costs
| Portfolio name | Unit | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Base case | $, real | 298606861.6342 | 0 | 0 | 0 | 0 | 0 | 108311622.5823 | 98009904.5197 | 93958149.6801 | 18295287.0608 | 19151233.3979 | 18799644.1674 | 17717559.8665 | 18600231.139 | 18951948.4778 | 19951927.9796 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565
| Assumed Portfolio option 1a (No GFM BESS) | $, real | 298606861.6342 | 0 | 0 | 0 | 0 | 0 | 108311622.5823 | 98009904.5197 | 93958149.6801 | 18295287.0608 | 19151233.3979 | 18799644.1674 | 17717559.8665 | 18600231.139 | 18951948.4778 | 19951927.9796 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565
| Assumed Portfolio option 2a (No GFM BESS) | $, real | 298606861.6342 | 0 | 0 | 0 | 0 | 0 | 108311622.5823 | 98009904.5197 | 93958149.6801 | 18295287.0608 | 19151233.3979 | 18799644.1674 | 17717559.8665 | 18600231.139 | 18951948.4778 | 19951927.9796 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565
| Assumed Portfolio option 3a (No GFM BESS) | $, real | 238470380.8087 | 0 | 0 | 0 | 0 | 0 | 108311622.5823 | 98009904.5197 | 93958149.6801 | 11516409.9667 | 5326718.9503 | 5228928.0155 | 4927957.3766 | 5173463.3289 | 5271289.8958 | 5549423.9277 | 12071823.5801 | 12071823.5801 | 12071823.5801 | 12071823.5801 | 12071823.5801 | 12071823.5801 | 12071823.5801 | 12071823.5801 | 12071823.5801 | 12071823.5801
| Assumed Portfolio option 4a (No GFM BESS) | $, real | 187892748.7604 | 0 | 0 | 0 | 0 | 0 | 108311622.5823 | 98009904.5197 | 93958149.6801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Assumed Portfolio option 5a (No GFM BESS) | $, real | 187892748.7604 | 0 | 0 | 0 | 0 | 0 | 108311622.5823 | 98009904.5197 | 93958149.6801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost for non-RIT-T proponent parties
| Portfolio name | Unit | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Base case | $, real | 504604944.6521 | 0 | 0 | 0 | 0 | 0 | 25899041.7624 | 17834184.3107 | 17729710.6567 | 86550391.5221 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282
| Assumed Portfolio option 1a (No GFM BESS) | $, real | 496846549.659 | 0 | 0 | 0 | 0 | 0 | 25899041.7624 | 17834184.3107 | 17729710.6567 | 84196687.9534 | 67136085.0159 | 67136085.0159 | 67136085.0159 | 67136085.0159 | 67136085.0159 | 67136085.0159 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282
| Assumed Portfolio option 2a (No GFM BESS) | $, real | 438909221.8839 | 0 | 0 | 0 | 0 | 0 | 25899041.7624 | 17834184.3107 | 17729710.6567 | 57146521.5262 | 50464609.8502 | 50464609.8502 | 50464609.8502 | 50464609.8502 | 50464609.8502 | 50464609.8502 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282
| Assumed Portfolio option 3a (No GFM BESS) | $, real | 280289301.1574 | 0 | 0 | 0 | 0 | 0 | 25899041.7624 | 17834184.3107 | 17729710.6567 | 45950022.6171 | 27275631.1535 | 27275631.1535 | 27275631.1535 | 27275631.1535 | 27275631.1535 | 27275631.1535 | 57311370.9576 | 57311370.9576 | 57311370.9576 | 57311370.9576 | 57311370.9576 | 57311370.9576 | 57311370.9576 | 57311370.9576 | 57311370.9576 | 57311370.9576
| Assumed Portfolio option 4a (No GFM BESS) | $, real | 65820409.4373 | 0 | 0 | 0 | 0 | 0 | 25899041.7624 | 17834184.3107 | 17729710.6567 | 15081166.9046 | 2364158.3365 | 2364158.3365 | 2364158.3365 | 2364158.3365 | 2364158.3365 | 2364158.3365 | 5030124.1202 | 5030124.1202 | 5030124.1202 | 5030124.1202 | 5030124.1202 | 5030124.1202 | 5030124.1202 | 5030124.1202 | 5030124.1202 | 5030124.1202
| Assumed Portfolio option 5a (No GFM BESS) | $, real | 39708106.227 | 0 | 0 | 0 | 0 | 0 | 25899041.7624 | 17834184.3107 | 17729710.6567 | 1885145.8631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Value of greenhouse gas emissions
| Portfolio name | Unit | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Base case | $, real | 401119540.9682 | 0 | 0 | 0 | 0 | 0 | 164626180.8766 | 163627263.9898 | 164778379.3044 | 11708936.5018 | 12625650.3916 | 13584033.0946 | 14584084.6108 | 15625804.9402 | 16709194.0827 | 17834252.0384 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204
| Assumed Portfolio option 1a (No GFM BESS) | $, real | 401119540.9682 | 0 | 0 | 0 | 0 | 0 | 164626180.8766 | 163627263.9898 | 164778379.3044 | 11708936.5018 | 12625650.3916 | 13584033.0946 | 14584084.6108 | 15625804.9402 | 16709194.0827 | 17834252.0384 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204
| Assumed Portfolio option 2a (No GFM BESS) | $, real | 401119540.9682 | 0 | 0 | 0 | 0 | 0 | 164626180.8766 | 163627263.9898 | 164778379.3044 | 11708936.5018 | 12625650.3916 | 13584033.0946 | 14584084.6108 | 15625804.9402 | 16709194.0827 | 17834252.0384 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204
| Assumed Portfolio option 3a (No GFM BESS) | $, real | 350980442.0826 | 0 | 0 | 0 | 0 | 0 | 164626180.8766 | 163627263.9898 | 164778379.3044 | 7370472.6567 | 3511695.0331 | 3778259.3425 | 4056413.4046 | 4346157.2192 | 4647490.7864 | 4960414.1062 | 11269184.9598 | 11269184.9598 | 11269184.9598 | 11269184.9598 | 11269184.9598 | 11269184.9598 | 11269184.9598 | 11269184.9598 | 11269184.9598 | 11269184.9598
| Assumed Portfolio option 4a (No GFM BESS) | $, real | 307498728.8693 | 0 | 0 | 0 | 0 | 0 | 164626180.8766 | 163627263.9898 | 164778379.3044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Assumed Portfolio option 5a (No GFM BESS) | $, real | 307498728.8693 | 0 | 0 | 0 | 0 | 0 | 164626180.8766 | 163627263.9898 | 164778379.3044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Accelerated synchronous condenser timing scenario
Involuntary load shedding
| Portfolio name | Unit | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Base case | $, real | 37149555343.6687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7207480482.1104 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491
| Accelerated Portfolio option 1a (No GFM BESS) | $, real | 36444367825.9886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7116769225.3846 | 4324810679.4483 | 4324810679.4483 | 4324810679.4483 | 4324810679.4483 | 4324810679.4483 | 4324810679.4483 | 8390901450.7278 | 8390901450.7278 | 8390901450.7278 | 8390901450.7278 | 8390901450.7278 | 8390901450.7278 | 8390901450.7278 | 8390901450.7278 | 8390901450.7278 | 8390901450.7278
| Accelerated Portfolio option 2a (No GFM BESS) | $, real | 16792431880.5676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3736796483.1653 | 1642740602.2301 | 1642740602.2301 | 1642740602.2301 | 1642740602.2301 | 1642740602.2301 | 1642740602.2301 | 4124950211.6095 | 4124950211.6095 | 4124950211.6095 | 4124950211.6095 | 4124950211.6095 | 4124950211.6095 | 4124950211.6095 | 4124950211.6095 | 4124950211.6095 | 4124950211.6095
| Accelerated Portfolio option 3a (No GFM BESS) | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Accelerated Portfolio option 4a (No GFM BESS) | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Accelerated Portfolio option 5a (No GFM BESS) | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fuel costs
| Portfolio name | Unit | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Base case | $, real | 298606861.6342 | 0 | 0 | 0 | 0 | 0 | 108311622.5823 | 98009904.5197 | 93958149.6801 | 18295287.0608 | 19151233.3979 | 18799644.1674 | 17717559.8665 | 18600231.139 | 18951948.4778 | 19951927.9796 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565
| Accelerated Portfolio option 1a (No GFM BESS) | $, real | 111357908.2632 | 0 | 0 | 0 | 0 | 0 | 451686.3712 | 289580.9038 | 279173.0473 | 18295287.0608 | 19151233.3979 | 18799644.1674 | 17717559.8665 | 18600231.139 | 18951948.4778 | 19951927.9796 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565
| Accelerated Portfolio option 2a (No GFM BESS) | $, real | 110714112.8738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18295287.0608 | 19151233.3979 | 18799644.1674 | 17717559.8665 | 18600231.139 | 18951948.4778 | 19951927.9796 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565
| Accelerated Portfolio option 3a (No GFM BESS) | $, real | 50577632.0484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11516409.9667 | 5326718.9503 | 5228928.0155 | 4927957.3766 | 5173463.3289 | 5271289.8958 | 5549423.9277 | 12071823.5801 | 12071823.5801 | 12071823.5801 | 12071823.5801 | 12071823.5801 | 12071823.5801 | 12071823.5801 | 12071823.5801 | 12071823.5801 | 12071823.5801
| Accelerated Portfolio option 4a (No GFM BESS) | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Accelerated Portfolio option 5a (No GFM BESS) | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost for non-RIT-T proponent parties
| Portfolio name | Unit | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Base case | $, real | 504604944.6521 | 0 | 0 | 0 | 0 | 0 | 25899041.7624 | 17834184.3107 | 17729710.6567 | 86550391.5221 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282
| Accelerated Portfolio option 1a (No GFM BESS) | $, real | 467259437.5057 | 0 | 0 | 0 | 0 | 0 | 8020890.8513 | 3113437.5094 | 3113437.5094 | 84196687.9534 | 67136085.0159 | 67136085.0159 | 67136085.0159 | 67136085.0159 | 67136085.0159 | 67136085.0159 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282
| Accelerated Portfolio option 2a (No GFM BESS) | $, real | 400950062.4288 | 0 | 0 | 0 | 0 | 0 | 846901.9434 | 132164.0455 | 132164.0455 | 57146521.5262 | 50464609.8502 | 50464609.8502 | 50464609.8502 | 50464609.8502 | 50464609.8502 | 50464609.8502 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282
| Accelerated Portfolio option 3a (No GFM BESS) | $, real | 241606589.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45950022.6171 | 27275631.1535 | 27275631.1535 | 27275631.1535 | 27275631.1535 | 27275631.1535 | 27275631.1535 | 57311370.9576 | 57311370.9576 | 57311370.9576 | 57311370.9576 | 57311370.9576 | 57311370.9576 | 57311370.9576 | 57311370.9576 | 57311370.9576 | 57311370.9576
| Accelerated Portfolio option 4a (No GFM BESS) | $, real | 27137697.6549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15081166.9046 | 2364158.3365 | 2364158.3365 | 2364158.3365 | 2364158.3365 | 2364158.3365 | 2364158.3365 | 5030124.1202 | 5030124.1202 | 5030124.1202 | 5030124.1202 | 5030124.1202 | 5030124.1202 | 5030124.1202 | 5030124.1202 | 5030124.1202 | 5030124.1202
| Accelerated Portfolio option 5a (No GFM BESS) | $, real | 1025394.4446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1885145.8631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Value of greenhouse gas emissions
| Portfolio name | Unit | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Base case | $, real | 401119540.9682 | 0 | 0 | 0 | 0 | 0 | 164626180.8766 | 163627263.9898 | 164778379.3044 | 11708936.5018 | 12625650.3916 | 13584033.0946 | 14584084.6108 | 15625804.9402 | 16709194.0827 | 17834252.0384 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204
| Accelerated Portfolio option 1a (No GFM BESS) | $, real | 93942420.6144 | 0 | 0 | 0 | 0 | 0 | 206065.2818 | 146721.3359 | 159667.3361 | 11708936.5018 | 12625650.3916 | 13584033.0946 | 14584084.6108 | 15625804.9402 | 16709194.0827 | 17834252.0384 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204
| Accelerated Portfolio option 2a (No GFM BESS) | $, real | 93620812.0989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11708936.5018 | 12625650.3916 | 13584033.0946 | 14584084.6108 | 15625804.9402 | 16709194.0827 | 17834252.0384 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204
| Accelerated Portfolio option 3a (No GFM BESS) | $, real | 43481713.2133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7370472.6567 | 3511695.0331 | 3778259.3425 | 4056413.4046 | 4346157.2192 | 4647490.7864 | 4960414.1062 | 11269184.9598 | 11269184.9598 | 11269184.9598 | 11269184.9598 | 11269184.9598 | 11269184.9598 | 11269184.9598 | 11269184.9598 | 11269184.9598 | 11269184.9598
| Accelerated Portfolio option 4a (No GFM BESS) | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Accelerated Portfolio option 5a (No GFM BESS) | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoided involuntary load shedding
Avoided involuntary load shedding
Avoided involuntary load shedding
Avoided involuntary load shedding
Avoided involuntary load shedding
Avoided fuel costs
Avoided fuel costs
Avoided fuel costs
Avoided fuel costs
Avoided fuel costs
Avoided cost for non-RIT-T proponent parties
Avoided cost for non-RIT-T proponent parties
Avoided cost for non-RIT-T proponent parties
Avoided cost for non-RIT-T proponent parties
Avoided cost for non-RIT-T proponent parties
Avoided value of greenhouse gas emissions
Avoided value of greenhouse gas emissions
Avoided value of greenhouse gas emissions
Avoided value of greenhouse gas emissions
Avoided value of greenhouse gas emissions
Avoided involuntary load curtailment
Avoided involuntary load curtailment
Avoided involuntary load curtailment
Avoided involuntary load curtailment
Avoided involuntary load curtailment
Avoided fuel costs
Avoided fuel costs
Avoided fuel costs
Avoided fuel costs
Avoided fuel costs
Avoided cost for non-RIT-T proponent parties
Avoided cost for non-RIT-T proponent parties
Avoided cost for non-RIT-T proponent parties
Avoided cost for non-RIT-T proponent parties
Avoided cost for non-RIT-T proponent parties
Avoided value of greenhouse gas emissions
Avoided value of greenhouse gas emissions
Avoided value of greenhouse gas emissions
Avoided value of greenhouse gas emissions
Avoided value of greenhouse gas emissions

## With GFM BESS assessment -->
The following sheets contain the cost and benefit inputs for portfolios in stage (b) of the MCC assessment (i.e. portfolios which include grid-forming BESS towards minimum level requirements)

## With GFM BESS. Capex
CAPEX - Portfolios including grid-forming BESS contribution to the minimum level
Capex inputs for System Strength RIT-T assessment
| Capex inputs | [6 empty] | All years refer to financial years
| Transgrid capex inputs | [5 empty] | Calculations
|  | Unit | Value
| Synchronous condenser cost | $ real 2024/25 | 323954597.79
| ISP-modelled battery, converted to grid-forming | $ real 2024/25 | See note below
Assumed synchronous condenser timing scenario
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 3b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio option 3b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio option 3b - assumed timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio option 3b - assumed timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 50580000 | 2033 | 20 | 32271666.5448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223
| Portfolio option 3b - assumed timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 4b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio option 4b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio option 4b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio option 4b - assumed timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio option 4b - assumed timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 16860000 | 2033 | 20 | 10757222.1816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408
| Portfolio option 4b - assumed timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 5b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio option 5b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio option 5b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio option 5b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 4 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio option 5b - assumed timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 79637482.3647 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio option 5b - assumed timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 0 | 2033 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 5b - assumed timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Accelerated synchronous condenser timing scenario
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 3b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio option 3b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio option 3b - accelerated timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio option 3b - accelerated timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 50580000 | 2033 | 20 | 32271666.5448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223
| Portfolio option 3b - accelerated timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 4b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio option 4b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio option 4b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio option 4b - accelerated timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio option 4b - accelerated timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 16860000 | 2033 | 20 | 10757222.1816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408
| Portfolio option 4b - accelerated timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 5b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio option 5b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio option 5b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio option 5b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 4 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio option 5b - accelerated timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 105861050.3635 | 0 | 0 | 0 | 0 | 0 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289 | 14015046.2289
| Portfolio option 5b - accelerated timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 0 | 2033 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 5b - accelerated timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio | Undiscounted capex ($) | Undiscounted capex ($m) | Discounted Capex ($) | Discounted Capex ($m)
| Portfolio option 3b - assumed timing | 1022443793.37 | 1022.4438 | 271184113.6388 | 271.1841
| Portfolio option 4b - assumed timing | 1312678391.16 | 1312.6784 | 329307151.6402 | 329.3072
| Portfolio option 5b - assumed timing | 1619772988.95 | 1619.773 | 398187411.8233 | 398.1874
| Portfolio option 3b - accelerated timing | 1022443793.37 | 1022.4438 | 349854817.6352 | 349.8548
| Portfolio option 4b - accelerated timing | 1312678391.16 | 1312.6784 | 434201423.6355 | 434.2014
| Portfolio option 5b - accelerated timing | 1619772988.95 | 1619.773 | 529305251.8173 | 529.3053
Note: CAPEX for ISP-modelled battery, converted to grid-forming
BESS included under AEMO's Draft 2026 ISP Step Change scenario are modelled in this MCC assessment to have an incremental capital cost of only 5% of the total AEMO 2025 Inputs, Assumptions and Scenarios Report (IASR) project cost, to reflect the potential uplift required to enable protection quality fault current capability. The underlying capital cost and operating costs of the projects themselves are not included in the assessment, as these costs are already assumed to be incurred in the base case given the projects are forecast to enter the market under the Draft 2026 ISP Step Change scenario. This is consistent with the approach adopted in the PACR.

## With GFM BESS. Opex
OPEX - Portfolios including grid-forming BESS contribution to the minimum level
Opex inputs and parameters for System Strength RIT-T assessment
| Operating cost inputs ($2024/25) | [7 empty] | All years refer to financial years
| Transgrid opex inputs | [5 empty] | Calculations
| Assumped opex | Unit | Value
| ISP-modelled battery, converted to grid-forming | % | 0% | Per cent of capex
| Network Synchronous Condensers | % | 0.6% | Per cent of capex
Assumed synchronous condenser timing scenario
| Operating cost ($2024/25) | [7 empty] | Opex
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex ($)
| Portfolio option 3b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Portfolio option 3b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Portfolio option 3b - assumed timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Portfolio option 3b - assumed timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 50580000 | 2033 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 3b - assumed timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating cost ($2024/25) | [7 empty] | Opex
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex ($)
| Portfolio option 4b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Portfolio option 4b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Portfolio option 4b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Portfolio option 4b - assumed timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Portfolio option 4b - assumed timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 16860000 | 2033 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 4b - assumed timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating cost ($2024/25) | [7 empty] | Opex
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex ($)
| Portfolio option 5b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Portfolio option 5b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Portfolio option 5b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Portfolio option 5b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 4 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Portfolio option 5b - assumed timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2034 | 40 | 1943727.5867 | 11044813.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 33043368.9746
| Portfolio option 5b - assumed timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 0 | 2033 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 5b - assumed timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Accelerated synchronous condenser timing scenario
| Operating cost ($2024/25) | [7 empty] | Opex
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex ($)
| Portfolio option 3b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Portfolio option 3b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Portfolio option 3b - accelerated timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Portfolio option 3b - accelerated timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 50580000 | 2033 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 3b - accelerated timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating cost ($2024/25) | [7 empty] | Opex
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex ($)
| Portfolio option 4b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Portfolio option 4b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Portfolio option 4b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Portfolio option 4b - accelerated timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Portfolio option 4b - accelerated timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 16860000 | 2033 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 4b - accelerated timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating cost ($2024/25) | [7 empty] | Opex
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex ($)
| Portfolio option 5b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Portfolio option 5b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Portfolio option 5b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Portfolio option 5b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 4 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Portfolio option 5b - accelerated timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 323954597.79 | 2031 | 40 | 1943727.5867 | 14681724.2406 | 0 | 0 | 0 | 0 | 0 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 1943727.5867 | 38874551.7348
| Portfolio option 5b - accelerated timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 0 | 2033 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 5b - accelerated timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio | Undiscounted opex ($) | Undiscounted opex ($m) | Discounted Opex ($) | Discounted Opex ($m)
| Portfolio option 3b - assumed timing | 99130106.9237 | 99.1301 | 33134440.4183 | 33.1344
| Portfolio option 4b - assumed timing | 132173475.8983 | 132.1735 | 44179253.891 | 44.1793
| Portfolio option 5b - assumed timing | 165216844.8729 | 165.2168 | 55224067.3638 | 55.2241
| Portfolio option 3b - accelerated timing | 116623655.2044 | 116.6237 | 44045172.7218 | 44.0452
| Portfolio option 4b - accelerated timing | 155498206.9392 | 155.4982 | 58726896.9624 | 58.7269
| Portfolio option 5b - accelerated timing | 194372758.674 | 194.3728 | 73408621.203 | 73.4086

## With BESS.Market benefit inputs
Inputs - Portfolios including grid-forming BESS contribution to the minimum level
Market benefit inputs for System Strength RIT-T assessment
Market benefit inputs ($2024/25)
Involuntary load shedding
| Portfolio name | Unit | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Base case | $, real | 37149555343.6687 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7207480482.1104 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 4415521936.1741 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491 | 8556147268.3491
| Portfolio option 3b - assumed timing | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 4b - assumed timing | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 5b - assumed timing | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 3b - accelerated timing | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 4b - accelerated timing | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 5b - accelerated timing | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fuel costs
| Portfolio name | Unit | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Base case | $, real | 298606861.6342 | 0 | 0 | 0 | 0 | 0 | 108311622.5823 | 98009904.5197 | 93958149.6801 | 18295287.0608 | 19151233.3979 | 18799644.1674 | 17717559.8665 | 18600231.139 | 18951948.4778 | 19951927.9796 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565 | 20398944.8565
| Portfolio option 3b - assumed timing | $, real | 187644751.0549 | 0 | 0 | 0 | 0 | 0 | 108311622.5823 | 98009904.5197 | 93532043.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 4b - assumed timing | $, real | 187644751.0549 | 0 | 0 | 0 | 0 | 0 | 108311622.5823 | 98009904.5197 | 93532043.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 5b - assumed timing | $, real | 187892748.7604 | 0 | 0 | 0 | 0 | 0 | 108311622.5823 | 98009904.5197 | 93958149.6801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 3b - accelerated timing | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 4b - accelerated timing | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 5b - accelerated timing | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cost for non-RIT-T proponent parties
| Portfolio name | Unit | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Base case | $, real | 504604944.6521 | 0 | 0 | 0 | 0 | 0 | 25899041.7624 | 17834184.3107 | 17729710.6567 | 86550391.5221 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 69634708.7619 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282 | 93611502.2282
| Portfolio option 3b - assumed timing | $, real | 39548745.7445 | 0 | 0 | 0 | 0 | 0 | 25899041.7624 | 17834184.3107 | 14160315.2687 | 1953134.7303 | 234870.6321 | 234870.6321 | 234870.6321 | 234870.6321 | 234870.6321 | 234870.6321 | 499724.7492 | 499724.7492 | 499724.7492 | 499724.7492 | 499724.7492 | 499724.7492 | 499724.7492 | 499724.7492 | 499724.7492 | 499724.7492
| Portfolio option 4b - assumed timing | $, real | 40464931.4571 | 0 | 0 | 0 | 0 | 0 | 25899041.7624 | 17834184.3107 | 14932258.4997 | 1946953.9242 | 293588.2902 | 293588.2902 | 293588.2902 | 293588.2902 | 293588.2902 | 293588.2902 | 624655.9365 | 624655.9365 | 624655.9365 | 624655.9365 | 624655.9365 | 624655.9365 | 624655.9365 | 624655.9365 | 624655.9365 | 624655.9365
| Portfolio option 5b - assumed timing | $, real | 39708106.227 | 0 | 0 | 0 | 0 | 0 | 25899041.7624 | 17834184.3107 | 17729710.6567 | 1885145.8631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 3b - accelerated timing | $, real | 2943454.5757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1953134.7303 | 234870.6321 | 234870.6321 | 234870.6321 | 234870.6321 | 234870.6321 | 234870.6321 | 499724.7492 | 499724.7492 | 499724.7492 | 499724.7492 | 499724.7492 | 499724.7492 | 499724.7492 | 499724.7492 | 499724.7492 | 499724.7492
| Portfolio option 4b - accelerated timing | $, real | 3410362.2997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1946953.9242 | 293588.2902 | 293588.2902 | 293588.2902 | 293588.2902 | 293588.2902 | 293588.2902 | 624655.9365 | 624655.9365 | 624655.9365 | 624655.9365 | 624655.9365 | 624655.9365 | 624655.9365 | 624655.9365 | 624655.9365 | 624655.9365
| Portfolio option 5b - accelerated timing | $, real | 1025394.4446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1885145.8631 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Value of greenhouse gas emissions
| Portfolio name | Unit | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Base case | $, real | 401119540.9682 | 0 | 0 | 0 | 0 | 0 | 164626180.8766 | 163627263.9898 | 164778379.3044 | 11708936.5018 | 12625650.3916 | 13584033.0946 | 14584084.6108 | 15625804.9402 | 16709194.0827 | 17834252.0384 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204 | 19042647.6204
| Portfolio option 3b - assumed timing | $, real | 307356891.6347 | 0 | 0 | 0 | 0 | 0 | 164626180.8766 | 163627263.9898 | 164534676.5282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 4b - assumed timing | $, real | 307356891.6347 | 0 | 0 | 0 | 0 | 0 | 164626180.8766 | 163627263.9898 | 164534676.5282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 5b - assumed timing | $, real | 307498728.8693 | 0 | 0 | 0 | 0 | 0 | 164626180.8766 | 163627263.9898 | 164778379.3044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 3b - accelerated timing | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 4b - accelerated timing | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 5b - accelerated timing | $, real | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avoided fuel costs
Avoided fuel costs
Avoided fuel costs
Avoided cost for non-RIT-T proponent parties
Avoided cost for non-RIT-T proponent parties
Avoided cost for non-RIT-T proponent parties
Avoided cost for non-RIT-T proponent parties
Avoided cost for non-RIT-T proponent parties
Avoided cost for non-RIT-T proponent parties
Avoided value of greenhouse gas emissions
Avoided value of greenhouse gas emissions
Avoided value of greenhouse gas emissions
Avoided value of greenhouse gas emissions
Avoided value of greenhouse gas emissions
Avoided value of greenhouse gas emissions

## High cost. Capex
Capex - Higher synchronous condenser cost sensitivity
Capex inputs for System Strength RIT-T assessment
| Capex inputs | [6 empty] | All years refer to financial years
| Transgrid capex inputs | [5 empty] | Calculations
|  | Unit | Value
| High capex assumption | % | 140%
Assumed synchronous condenser timing scenario
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 3b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 453536436.906 | 2034 | 40 | 111492475.3105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205
| Portfolio option 3b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 453536436.906 | 2034 | 40 | 111492475.3105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205
| Portfolio option 3b - assumed timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 453536436.906 | 2034 | 40 | 111492475.3105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205
| Portfolio option 3b - assumed timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 50580000 | 2033 | 20 | 32271666.5448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223
| Portfolio option 3b - assumed timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 4b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 453536436.906 | 2034 | 40 | 111492475.3105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205
| Portfolio option 4b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 453536436.906 | 2034 | 40 | 111492475.3105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205
| Portfolio option 4b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 453536436.906 | 2034 | 40 | 111492475.3105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205
| Portfolio option 4b - assumed timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 453536436.906 | 2034 | 40 | 111492475.3105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205
| Portfolio option 4b - assumed timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 16860000 | 2033 | 20 | 10757222.1816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408
| Portfolio option 4b - assumed timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 5b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 453536436.906 | 2034 | 40 | 111492475.3105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205
| Portfolio option 5b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 453536436.906 | 2034 | 40 | 111492475.3105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205
| Portfolio option 5b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 453536436.906 | 2034 | 40 | 111492475.3105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205
| Portfolio option 5b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 4 | Network Synchronous Condensers | 453536436.906 | 2034 | 40 | 111492475.3105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205
| Portfolio option 5b - assumed timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 453536436.906 | 2034 | 40 | 111492475.3105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205
| Portfolio option 5b - assumed timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 0 | 2033 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 5b - assumed timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Accelerated synchronous condenser timing scenario
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 3b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 453536436.906 | 2031 | 40 | 148205470.5089 | 0 | 0 | 0 | 0 | 0 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205
| Portfolio option 3b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 453536436.906 | 2031 | 40 | 148205470.5089 | 0 | 0 | 0 | 0 | 0 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205
| Portfolio option 3b - accelerated timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 453536436.906 | 2031 | 40 | 148205470.5089 | 0 | 0 | 0 | 0 | 0 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205
| Portfolio option 3b - accelerated timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 50580000 | 2033 | 20 | 32271666.5448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223
| Portfolio option 3b - accelerated timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 4b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 453536436.906 | 2031 | 40 | 148205470.5089 | 0 | 0 | 0 | 0 | 0 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205
| Portfolio option 4b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 453536436.906 | 2031 | 40 | 148205470.5089 | 0 | 0 | 0 | 0 | 0 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205
| Portfolio option 4b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 453536436.906 | 2031 | 40 | 148205470.5089 | 0 | 0 | 0 | 0 | 0 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205
| Portfolio option 4b - accelerated timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 453536436.906 | 2031 | 40 | 148205470.5089 | 0 | 0 | 0 | 0 | 0 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205
| Portfolio option 4b - accelerated timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 16860000 | 2033 | 20 | 10757222.1816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408
| Portfolio option 4b - accelerated timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 5b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 453536436.906 | 2031 | 40 | 148205470.5089 | 0 | 0 | 0 | 0 | 0 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205
| Portfolio option 5b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 453536436.906 | 2031 | 40 | 148205470.5089 | 0 | 0 | 0 | 0 | 0 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205
| Portfolio option 5b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 453536436.906 | 2031 | 40 | 148205470.5089 | 0 | 0 | 0 | 0 | 0 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205
| Portfolio option 5b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 4 | Network Synchronous Condensers | 453536436.906 | 2031 | 40 | 148205470.5089 | 0 | 0 | 0 | 0 | 0 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205
| Portfolio option 5b - accelerated timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 453536436.906 | 2031 | 40 | 148205470.5089 | 0 | 0 | 0 | 0 | 0 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205 | 19621064.7205
| Portfolio option 5b - accelerated timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 0 | 2033 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 5b - accelerated timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio | Undiscounted capex ($) | Undiscounted capex ($m) | Discounted Capex ($) | Discounted Capex ($m)
| Portfolio option 3b - assumed timing | 1411189310.718 | 1411.1893 | 366749092.4763 | 366.7491
| Portfolio option 4b - assumed timing | 1831005747.624 | 1831.0057 | 456727123.4237 | 456.7271
| Portfolio option 5b - assumed timing | 2267682184.53 | 2267.6822 | 557462376.5526 | 557.4624
| Portfolio option 3b - accelerated timing | 1411189310.718 | 1411.1893 | 476888078.0713 | 476.8881
| Portfolio option 4b - accelerated timing | 1831005747.624 | 1831.0057 | 603579104.217 | 603.5791
| Portfolio option 5b - accelerated timing | 2267682184.53 | 2267.6822 | 741027352.5443 | 741.0274

## High cost. Opex
Opex - Higher synchronous condener cost sensitivity
Opex inputs and parameters for System Strength RIT-T assessment
| Operating cost inputs ($2024/25) | [7 empty] | All years refer to financial years
| Transgrid opex inputs | [5 empty] | Calculations
| Assumped opex | Unit | Value
| ISP-modelled battery, converted to grid-forming | % | 0% | Per cent of capex
| Network Synchronous Condensers | % | 0.6% | Per cent of capex
Assumed synchronous condenser timing scenario
| Operating cost ($2024/25) | [7 empty] | Opex
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex ($)
| Portfolio option 3b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 453536436.906 | 2034 | 40 | 2721218.6214 | 15462738.8619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 46260716.5644
| Portfolio option 3b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 453536436.906 | 2034 | 40 | 2721218.6214 | 15462738.8619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 46260716.5644
| Portfolio option 3b - assumed timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 453536436.906 | 2034 | 40 | 2721218.6214 | 15462738.8619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 46260716.5644
| Portfolio option 3b - assumed timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 50580000 | 2033 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 3b - assumed timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating cost ($2024/25) | [7 empty] | Opex
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex ($)
| Portfolio option 4b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 453536436.906 | 2034 | 40 | 2721218.6214 | 15462738.8619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 46260716.5644
| Portfolio option 4b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 453536436.906 | 2034 | 40 | 2721218.6214 | 15462738.8619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 46260716.5644
| Portfolio option 4b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 453536436.906 | 2034 | 40 | 2721218.6214 | 15462738.8619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 46260716.5644
| Portfolio option 4b - assumed timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 453536436.906 | 2034 | 40 | 2721218.6214 | 15462738.8619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 46260716.5644
| Portfolio option 4b - assumed timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 16860000 | 2033 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 4b - assumed timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating cost ($2024/25) | [7 empty] | Opex
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex ($)
| Portfolio option 5b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 453536436.906 | 2034 | 40 | 2721218.6214 | 15462738.8619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 46260716.5644
| Portfolio option 5b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 453536436.906 | 2034 | 40 | 2721218.6214 | 15462738.8619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 46260716.5644
| Portfolio option 5b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 453536436.906 | 2034 | 40 | 2721218.6214 | 15462738.8619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 46260716.5644
| Portfolio option 5b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 4 | Network Synchronous Condensers | 453536436.906 | 2034 | 40 | 2721218.6214 | 15462738.8619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 46260716.5644
| Portfolio option 5b - assumed timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 453536436.906 | 2034 | 40 | 2721218.6214 | 15462738.8619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 46260716.5644
| Portfolio option 5b - assumed timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 0 | 2033 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 5b - assumed timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Accelerated synchronous condenser timing scenario
| Operating cost ($2024/25) | [7 empty] | Opex
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex ($)
| Portfolio option 3b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 453536436.906 | 2031 | 40 | 2721218.6214 | 20554413.9369 | 0 | 0 | 0 | 0 | 0 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 54424372.4287
| Portfolio option 3b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 453536436.906 | 2031 | 40 | 2721218.6214 | 20554413.9369 | 0 | 0 | 0 | 0 | 0 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 54424372.4287
| Portfolio option 3b - accelerated timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 453536436.906 | 2031 | 40 | 2721218.6214 | 20554413.9369 | 0 | 0 | 0 | 0 | 0 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 54424372.4287
| Portfolio option 3b - accelerated timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 50580000 | 2033 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 3b - accelerated timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating cost ($2024/25) | [7 empty] | Opex
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex ($)
| Portfolio option 4b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 453536436.906 | 2031 | 40 | 2721218.6214 | 20554413.9369 | 0 | 0 | 0 | 0 | 0 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 54424372.4287
| Portfolio option 4b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 453536436.906 | 2031 | 40 | 2721218.6214 | 20554413.9369 | 0 | 0 | 0 | 0 | 0 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 54424372.4287
| Portfolio option 4b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 453536436.906 | 2031 | 40 | 2721218.6214 | 20554413.9369 | 0 | 0 | 0 | 0 | 0 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 54424372.4287
| Portfolio option 4b - accelerated timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 453536436.906 | 2031 | 40 | 2721218.6214 | 20554413.9369 | 0 | 0 | 0 | 0 | 0 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 54424372.4287
| Portfolio option 4b - accelerated timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 16860000 | 2033 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 4b - accelerated timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating cost ($2024/25) | [7 empty] | Opex
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex ($)
| Portfolio option 5b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 453536436.906 | 2031 | 40 | 2721218.6214 | 20554413.9369 | 0 | 0 | 0 | 0 | 0 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 54424372.4287
| Portfolio option 5b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 453536436.906 | 2031 | 40 | 2721218.6214 | 20554413.9369 | 0 | 0 | 0 | 0 | 0 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 54424372.4287
| Portfolio option 5b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 453536436.906 | 2031 | 40 | 2721218.6214 | 20554413.9369 | 0 | 0 | 0 | 0 | 0 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 54424372.4287
| Portfolio option 5b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 4 | Network Synchronous Condensers | 453536436.906 | 2031 | 40 | 2721218.6214 | 20554413.9369 | 0 | 0 | 0 | 0 | 0 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 54424372.4287
| Portfolio option 5b - accelerated timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 453536436.906 | 2031 | 40 | 2721218.6214 | 20554413.9369 | 0 | 0 | 0 | 0 | 0 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 2721218.6214 | 54424372.4287
| Portfolio option 5b - accelerated timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 0 | 2033 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 5b - accelerated timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio | Undiscounted capex ($) | Undiscounted capex ($m) | Discounted Capex ($) | Discounted Capex ($m)
| Portfolio option 3b - assumed timing | 138782149.6932 | 138.7821 | 46388216.5856 | 46.3882
| Portfolio option 4b - assumed timing | 185042866.2576 | 185.0429 | 61850955.4474 | 61.851
| Portfolio option 5b - assumed timing | 231303582.8221 | 231.3036 | 77313694.3093 | 77.3137
| Portfolio option 3b - accelerated timing | 163273117.2862 | 163.2731 | 61663241.8106 | 61.6632
| Portfolio option 4b - accelerated timing | 217697489.7149 | 217.6975 | 82217655.7474 | 82.2177
| Portfolio option 5b - accelerated timing | 272121862.1436 | 272.1219 | 102772069.6843 | 102.7721

## Low cost. Capex
Capex - Lower synchronous condenser cost sensitivity
Capex inputs for System Strength RIT-T assessment
| Capex inputs | [6 empty] | All years refer to financial years
| Transgrid capex inputs | [5 empty] | Calculations
|  | Unit | Value
| Low capex assumption | % | 70%
Assumed synchronous condenser timing scenario
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 3b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 226768218.453 | 2034 | 40 | 55746237.6553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603
| Portfolio option 3b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 226768218.453 | 2034 | 40 | 55746237.6553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603
| Portfolio option 3b - assumed timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 226768218.453 | 2034 | 40 | 55746237.6553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603
| Portfolio option 3b - assumed timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 50580000 | 2033 | 20 | 32271666.5448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223
| Portfolio option 3b - assumed timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 4b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 226768218.453 | 2034 | 40 | 55746237.6553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603
| Portfolio option 4b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 226768218.453 | 2034 | 40 | 55746237.6553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603
| Portfolio option 4b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 226768218.453 | 2034 | 40 | 55746237.6553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603
| Portfolio option 4b - assumed timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 226768218.453 | 2034 | 40 | 55746237.6553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603
| Portfolio option 4b - assumed timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 16860000 | 2033 | 20 | 10757222.1816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408
| Portfolio option 4b - assumed timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 5b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 226768218.453 | 2034 | 40 | 55746237.6553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603
| Portfolio option 5b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 226768218.453 | 2034 | 40 | 55746237.6553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603
| Portfolio option 5b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 226768218.453 | 2034 | 40 | 55746237.6553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603
| Portfolio option 5b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 4 | Network Synchronous Condensers | 226768218.453 | 2034 | 40 | 55746237.6553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603
| Portfolio option 5b - assumed timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 226768218.453 | 2034 | 40 | 55746237.6553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603
| Portfolio option 5b - assumed timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 0 | 2033 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 5b - assumed timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Accelerated synchronous condenser timing scenario
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 3b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 226768218.453 | 2031 | 40 | 74102735.2544 | 0 | 0 | 0 | 0 | 0 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603
| Portfolio option 3b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 226768218.453 | 2031 | 40 | 74102735.2544 | 0 | 0 | 0 | 0 | 0 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603
| Portfolio option 3b - accelerated timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 226768218.453 | 2031 | 40 | 74102735.2544 | 0 | 0 | 0 | 0 | 0 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603
| Portfolio option 3b - accelerated timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 50580000 | 2033 | 20 | 32271666.5448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223 | 5151684.7223
| Portfolio option 3b - accelerated timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 4b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 226768218.453 | 2031 | 40 | 74102735.2544 | 0 | 0 | 0 | 0 | 0 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603
| Portfolio option 4b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 226768218.453 | 2031 | 40 | 74102735.2544 | 0 | 0 | 0 | 0 | 0 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603
| Portfolio option 4b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 226768218.453 | 2031 | 40 | 74102735.2544 | 0 | 0 | 0 | 0 | 0 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603
| Portfolio option 4b - accelerated timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 226768218.453 | 2031 | 40 | 74102735.2544 | 0 | 0 | 0 | 0 | 0 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603
| Portfolio option 4b - accelerated timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 16860000 | 2033 | 20 | 10757222.1816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408 | 1717228.2408
| Portfolio option 4b - accelerated timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capital cost ($2024/25) | [6 empty] | Annualised capex ($)
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 5b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 226768218.453 | 2031 | 40 | 74102735.2544 | 0 | 0 | 0 | 0 | 0 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603
| Portfolio option 5b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 226768218.453 | 2031 | 40 | 74102735.2544 | 0 | 0 | 0 | 0 | 0 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603
| Portfolio option 5b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 226768218.453 | 2031 | 40 | 74102735.2544 | 0 | 0 | 0 | 0 | 0 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603
| Portfolio option 5b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 4 | Network Synchronous Condensers | 226768218.453 | 2031 | 40 | 74102735.2544 | 0 | 0 | 0 | 0 | 0 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603
| Portfolio option 5b - accelerated timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 226768218.453 | 2031 | 40 | 74102735.2544 | 0 | 0 | 0 | 0 | 0 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603 | 9810532.3603
| Portfolio option 5b - accelerated timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 0 | 2033 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 5b - accelerated timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio | Undiscounted capex ($) | Undiscounted capex ($m) | Discounted Capex ($) | Discounted Capex ($m)
| Portfolio option 3b - assumed timing | 730884655.359 | 730.8847 | 199510379.5106 | 199.5104
| Portfolio option 4b - assumed timing | 923932873.812 | 923.9329 | 233742172.8026 | 233.7422
| Portfolio option 5b - assumed timing | 1133841092.265 | 1133.8411 | 278731188.2763 | 278.7312
| Portfolio option 3b - accelerated timing | 730884655.359 | 730.8847 | 254579872.3081 | 254.5799
| Portfolio option 4b - accelerated timing | 923932873.812 | 923.9329 | 307168163.1993 | 307.1682
| Portfolio option 5b - accelerated timing | 1133841092.265 | 1133.8411 | 370513676.2721 | 370.5137

## Low cost. Opex
Opex - Lower synchronous condenser cost sensitivity
Opex inputs and parameters for System Strength RIT-T assessment
| Operating cost inputs ($2024/25) | [7 empty] | All years refer to financial years
| Transgrid opex inputs | [5 empty] | Calculations
| Assumped opex | Unit | Value
| ISP-modelled battery, converted to grid-forming | % | 0% | Per cent of capex
| Network Synchronous Condensers | % | 0.6% | Per cent of capex
Assumed synchronous condenser timing scenario
| Operating cost ($2024/25) | [7 empty] | Opex
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex ($)
| Portfolio option 3b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 226768218.453 | 2034 | 40 | 1360609.3107 | 7731369.4309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 23130358.2822
| Portfolio option 3b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 226768218.453 | 2034 | 40 | 1360609.3107 | 7731369.4309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 23130358.2822
| Portfolio option 3b - assumed timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 226768218.453 | 2034 | 40 | 1360609.3107 | 7731369.4309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 23130358.2822
| Portfolio option 3b - assumed timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 50580000 | 2033 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 3b - assumed timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating cost ($2024/25) | [7 empty] | Opex
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex ($)
| Portfolio option 4b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 226768218.453 | 2034 | 40 | 1360609.3107 | 7731369.4309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 23130358.2822
| Portfolio option 4b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 226768218.453 | 2034 | 40 | 1360609.3107 | 7731369.4309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 23130358.2822
| Portfolio option 4b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 226768218.453 | 2034 | 40 | 1360609.3107 | 7731369.4309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 23130358.2822
| Portfolio option 4b - assumed timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 226768218.453 | 2034 | 40 | 1360609.3107 | 7731369.4309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 23130358.2822
| Portfolio option 4b - assumed timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 16860000 | 2033 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 4b - assumed timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating cost ($2024/25) | [7 empty] | Opex
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex ($)
| Portfolio option 5b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 226768218.453 | 2034 | 40 | 1360609.3107 | 7731369.4309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 23130358.2822
| Portfolio option 5b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 226768218.453 | 2034 | 40 | 1360609.3107 | 7731369.4309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 23130358.2822
| Portfolio option 5b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 226768218.453 | 2034 | 40 | 1360609.3107 | 7731369.4309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 23130358.2822
| Portfolio option 5b - assumed timing | Sydney/Newcastle Network Synchronous Condenser 4 | Network Synchronous Condensers | 226768218.453 | 2034 | 40 | 1360609.3107 | 7731369.4309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 23130358.2822
| Portfolio option 5b - assumed timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 226768218.453 | 2034 | 40 | 1360609.3107 | 7731369.4309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 23130358.2822
| Portfolio option 5b - assumed timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 0 | 2033 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 5b - assumed timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Accelerated synchronous condenser timing scenario
| Operating cost ($2024/25) | [7 empty] | Opex
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex ($)
| Portfolio option 3b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 226768218.453 | 2031 | 40 | 1360609.3107 | 10277206.9684 | 0 | 0 | 0 | 0 | 0 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 27212186.2144
| Portfolio option 3b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 226768218.453 | 2031 | 40 | 1360609.3107 | 10277206.9684 | 0 | 0 | 0 | 0 | 0 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 27212186.2144
| Portfolio option 3b - accelerated timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 226768218.453 | 2031 | 40 | 1360609.3107 | 10277206.9684 | 0 | 0 | 0 | 0 | 0 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 27212186.2144
| Portfolio option 3b - accelerated timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 50580000 | 2033 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 3b - accelerated timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating cost ($2024/25) | [7 empty] | Opex
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex ($)
| Portfolio option 4b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 226768218.453 | 2031 | 40 | 1360609.3107 | 10277206.9684 | 0 | 0 | 0 | 0 | 0 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 27212186.2144
| Portfolio option 4b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 226768218.453 | 2031 | 40 | 1360609.3107 | 10277206.9684 | 0 | 0 | 0 | 0 | 0 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 27212186.2144
| Portfolio option 4b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 226768218.453 | 2031 | 40 | 1360609.3107 | 10277206.9684 | 0 | 0 | 0 | 0 | 0 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 27212186.2144
| Portfolio option 4b - accelerated timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 226768218.453 | 2031 | 40 | 1360609.3107 | 10277206.9684 | 0 | 0 | 0 | 0 | 0 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 27212186.2144
| Portfolio option 4b - accelerated timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 16860000 | 2033 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 4b - accelerated timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating cost ($2024/25) | [7 empty] | Opex
| Portfolio option | Component | Asset class | Capex ($2024/25) | Commissioning date | Economic life | Annual opex ($2024/25) | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | Undiscounted opex ($)
| Portfolio option 5b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 1 | Network Synchronous Condensers | 226768218.453 | 2031 | 40 | 1360609.3107 | 10277206.9684 | 0 | 0 | 0 | 0 | 0 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 27212186.2144
| Portfolio option 5b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 2 | Network Synchronous Condensers | 226768218.453 | 2031 | 40 | 1360609.3107 | 10277206.9684 | 0 | 0 | 0 | 0 | 0 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 27212186.2144
| Portfolio option 5b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 3 | Network Synchronous Condensers | 226768218.453 | 2031 | 40 | 1360609.3107 | 10277206.9684 | 0 | 0 | 0 | 0 | 0 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 27212186.2144
| Portfolio option 5b - accelerated timing | Sydney/Newcastle Network Synchronous Condenser 4 | Network Synchronous Condensers | 226768218.453 | 2031 | 40 | 1360609.3107 | 10277206.9684 | 0 | 0 | 0 | 0 | 0 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 27212186.2144
| Portfolio option 5b - accelerated timing | Dinawan Network Synchronous Condenser 1 | Network Synchronous Condensers | 226768218.453 | 2031 | 40 | 1360609.3107 | 10277206.9684 | 0 | 0 | 0 | 0 | 0 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 1360609.3107 | 27212186.2144
| Portfolio option 5b - accelerated timing | Grid-forming Battery FY33 | ISP-modelled battery, converted to grid-forming | 0 | 2033 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio option 5b - accelerated timing | Grid-forming Battery FY34 | ISP-modelled battery, converted to grid-forming | 0 | 2034 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Portfolio | Undiscounted capex ($) | Undiscounted capex ($m) | Discounted Capex ($) | Discounted Capex ($m)
| Portfolio option 3b - assumed timing | 69391074.8466 | 69.3911 | 23194108.2928 | 23.1941
| Portfolio option 4b - assumed timing | 92521433.1288 | 92.5214 | 30925477.7237 | 30.9255
| Portfolio option 5b - assumed timing | 115651791.411 | 115.6518 | 38656847.1546 | 38.6568
| Portfolio option 3b - accelerated timing | 81636558.6431 | 81.6366 | 30831620.9053 | 30.8316
| Portfolio option 4b - accelerated timing | 108848744.8574 | 108.8487 | 41108827.8737 | 41.1088
| Portfolio option 5b - accelerated timing | 136060931.0718 | 136.0609 | 51386034.8421 | 51.386

## C1 Calculations
C1 Calculations
Calculating costs, benefits and NPV for each portfolio option
Parameters for C1 Calculations
Parameters
| General parameters |  | Unit | Active | Scenario
| Commercial discount rate |  | Percent | 7% | 7%
Grid-forming BESS excluded. Net present value calculation
Assumed synchronous condenser timing scenario
Net present value for each portfolio
| Portfolio name | Units | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Assumed Portfolio option 1a (No GFM BESS) | $ | 622263616.8358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77106186.4788 | 77251106.6561 | 77251106.6561 | 77251106.6561 | 77251106.6561 | 77251106.6561 | 77251106.6561 | 149287043.8056 | 149287043.8056 | 149287043.8056 | 149287043.8056 | 149287043.8056 | 149287043.8056 | 149287043.8056 | 149287043.8056 | 149287043.8056 | 149287043.8056
| Assumed Portfolio option 2a (No GFM BESS) | $ | 20241454594.1945 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3468170321.3096 | 2760033885.2243 | 2760033885.2243 | 2760033885.2243 | 2760033885.2243 | 2760033885.2243 | 2760033885.2243 | 4399279509.1083 | 4399279509.1083 | 4399279509.1083 | 4399279509.1083 | 4399279509.1083 | 4399279509.1083 | 4399279509.1083 | 4399279509.1083 | 4399279509.1083 | 4399279509.1083
| Assumed Portfolio option 3a (No GFM BESS) | $ | 37212099679.3622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7211321870.5076 | 4432943162.1415 | 4433381182.2394 | 4433321966.0315 | 4434711107.8664 | 4435747054.2137 | 4437281034.3195 | 8560671662.1096 | 8560671662.1096 | 8560671662.1096 | 8560671662.1096 | 8560671662.1096 | 8560671662.1096 | 8560671662.1096 | 8560671662.1096 | 8560671662.1096 | 8560671662.1096
| Assumed Portfolio option 4a (No GFM BESS) | $ | 37429945620.5066 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7245118835.0278 | 4450734275.1262 | 4451341068.5987 | 4451259035.814 | 4453183427.4159 | 4454618533.8972 | 4456743571.3547 | 8620335143.6713 | 8620335143.6713 | 8620335143.6713 | 8620335143.6713 | 8620335143.6713 | 8620335143.6713 | 8620335143.6713 | 8620335143.6713 | 8620335143.6713 | 8620335143.6713
| Assumed Portfolio option 5a (No GFM BESS) | $ | 37365375627.8794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7242356082.2537 | 4437139659.647 | 4437746453.1195 | 4437664420.3348 | 4439588811.9367 | 4441023918.418 | 4443148955.8755 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758
Present value of market benefits for each portfolio
| Portfolio name | Units | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Assumed Portfolio option 1a (No GFM BESS) | $ | 712945912.6732 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93064960.2945 | 93209880.4718 | 93209880.4718 | 93209880.4718 | 93209880.4718 | 93209880.4718 | 93209880.4718 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213
| Assumed Portfolio option 2a (No GFM BESS) | $ | 20422819185.8694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3500087868.941 | 2791951432.8556 | 2791951432.8556 | 2791951432.8556 | 2791951432.8556 | 2791951432.8556 | 2791951432.8556 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396
| Assumed Portfolio option 3a (No GFM BESS) | $ | 37484146566.8744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7259198191.9546 | 4480819483.5886 | 4481257503.6864 | 4481198287.4786 | 4482587429.3135 | 4483623375.6608 | 4485157355.7665 | 8608547983.5566 | 8608547983.5566 | 8608547983.5566 | 8608547983.5566 | 8608547983.5566 | 8608547983.5566 | 8608547983.5566 | 8608547983.5566 | 8608547983.5566 | 8608547983.5566
| Assumed Portfolio option 4a (No GFM BESS) | $ | 37792674803.8562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7308953930.2905 | 4514569370.389 | 4515176163.8615 | 4515094131.0767 | 4517018522.6786 | 4518453629.1599 | 4520578666.6174 | 8684170238.934 | 8684170238.934 | 8684170238.934 | 8684170238.934 | 8684170238.934 | 8684170238.934 | 8684170238.934 | 8684170238.934 | 8684170238.934 | 8684170238.934
| Assumed Portfolio option 5a (No GFM BESS) | $ | 37818787107.0665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7322149951.3321 | 4516933528.7255 | 4517540322.198 | 4517458289.4132 | 4519382681.0151 | 4520817787.4964 | 4522942824.9539 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542
Present value of costs for each portfolio
| Portfolio name | Units | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Assumed Portfolio option 1a (No GFM BESS) | $ | 90682295.8374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157
| Assumed Portfolio option 2a (No GFM BESS) | $ | 181364591.6748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314
| Assumed Portfolio option 3a (No GFM BESS) | $ | 272046887.5122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471
| Assumed Portfolio option 4a (No GFM BESS) | $ | 362729183.3497 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627
| Assumed Portfolio option 5a (No GFM BESS) | $ | 453411479.1871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784
Accelerated synchronous condenser timing scenario
Net present value for each portfolio
| Portfolio name | Units | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Accelerated Portfolio option 1a (No GFM BESS) | $ | 1116416323.9471 | 0 | 0 | 0 | 0 | 0 | 274199428.9014 | 259962839.2554 | 256955187.9328 | 77106186.4788 | 77251106.6561 | 77251106.6561 | 77251106.6561 | 77251106.6561 | 77251106.6561 | 77251106.6561 | 149287043.8056 | 149287043.8056 | 149287043.8056 | 149287043.8056 | 149287043.8056 | 149287043.8056 | 149287043.8056 | 149287043.8056 | 149287043.8056 | 149287043.8056
| Accelerated Portfolio option 2a (No GFM BESS) | $ | 20715084273.746 | 0 | 0 | 0 | 0 | 0 | 266072395.6466 | 247421641.1433 | 244416527.9644 | 3468170321.3096 | 2760033885.2243 | 2760033885.2243 | 2760033885.2243 | 2760033885.2243 | 2760033885.2243 | 2760033885.2243 | 4399279509.1083 | 4399279509.1083 | 4399279509.1083 | 4399279509.1083 | 4399279509.1083 | 4399279509.1083 | 4399279509.1083 | 4399279509.1083 | 4399279509.1083 | 4399279509.1083
| Accelerated Portfolio option 3a (No GFM BESS) | $ | 37656592432.4743 | 0 | 0 | 0 | 0 | 0 | 250960523.7742 | 231595031.3731 | 228589918.1942 | 7211321870.5076 | 4432943162.1415 | 4433381182.2394 | 4433321966.0315 | 4434711107.8664 | 4435747054.2137 | 4437281034.3195 | 8560671662.1096 | 8560671662.1096 | 8560671662.1096 | 8560671662.1096 | 8560671662.1096 | 8560671662.1096 | 8560671662.1096 | 8560671662.1096 | 8560671662.1096 | 8560671662.1096
| Accelerated Portfolio option 4a (No GFM BESS) | $ | 37844577894.852 | 0 | 0 | 0 | 0 | 0 | 235001749.9586 | 215636257.5575 | 212631144.3785 | 7245118835.0278 | 4450734275.1262 | 4451341068.5987 | 4451259035.814 | 4453183427.4159 | 4454618533.8972 | 4456743571.3547 | 8620335143.6713 | 8620335143.6713 | 8620335143.6713 | 8620335143.6713 | 8620335143.6713 | 8620335143.6713 | 8620335143.6713 | 8620335143.6713 | 8620335143.6713 | 8620335143.6713
| Accelerated Portfolio option 5a (No GFM BESS) | $ | 37750147423.4582 | 0 | 0 | 0 | 0 | 0 | 219042976.1429 | 199677483.7418 | 196672370.5628 | 7242356082.2537 | 4437139659.647 | 4437746453.1195 | 4437664420.3348 | 4439588811.9367 | 4441023918.418 | 4443148955.8755 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758
Present value of market benefits for each portfolio
| Portfolio name | Units | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Accelerated Portfolio option 1a (No GFM BESS) | $ | 1236959098.5512 | 0 | 0 | 0 | 0 | 0 | 290158202.717 | 275921613.0711 | 272913961.7485 | 93064960.2945 | 93209880.4718 | 93209880.4718 | 93209880.4718 | 93209880.4718 | 93209880.4718 | 93209880.4718 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213 | 165245817.6213
| Accelerated Portfolio option 2a (No GFM BESS) | $ | 20956169822.9541 | 0 | 0 | 0 | 0 | 0 | 297989943.2779 | 279339188.7747 | 276334075.5957 | 3500087868.941 | 2791951432.8556 | 2791951432.8556 | 2791951432.8556 | 2791951432.8556 | 2791951432.8556 | 2791951432.8556 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396 | 4431197056.7396
| Accelerated Portfolio option 3a (No GFM BESS) | $ | 38018220756.2865 | 0 | 0 | 0 | 0 | 0 | 298836845.2213 | 279471352.8202 | 276466239.6413 | 7259198191.9546 | 4480819483.5886 | 4481257503.6864 | 4481198287.4786 | 4482587429.3135 | 4483623375.6608 | 4485157355.7665 | 8608547983.5566 | 8608547983.5566 | 8608547983.5566 | 8608547983.5566 | 8608547983.5566 | 8608547983.5566 | 8608547983.5566 | 8608547983.5566 | 8608547983.5566 | 8608547983.5566
| Accelerated Portfolio option 4a (No GFM BESS) | $ | 38326748993.2683 | 0 | 0 | 0 | 0 | 0 | 298836845.2213 | 279471352.8202 | 276466239.6413 | 7308953930.2905 | 4514569370.389 | 4515176163.8615 | 4515094131.0767 | 4517018522.6786 | 4518453629.1599 | 4520578666.6174 | 8684170238.934 | 8684170238.934 | 8684170238.934 | 8684170238.934 | 8684170238.934 | 8684170238.934 | 8684170238.934 | 8684170238.934 | 8684170238.934 | 8684170238.934
| Accelerated Portfolio option 5a (No GFM BESS) | $ | 38352861296.4785 | 0 | 0 | 0 | 0 | 0 | 298836845.2213 | 279471352.8202 | 276466239.6413 | 7322149951.3321 | 4516933528.7255 | 4517540322.198 | 4517458289.4132 | 4519382681.0151 | 4520817787.4964 | 4522942824.9539 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542
Present value of costs for each portfolio
| Portfolio name | Units | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Accelerated Portfolio option 1a (No GFM BESS) | $ | 120542774.6041 | 0 | 0 | 0 | 0 | 0 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157 | 15958773.8157
| Accelerated Portfolio option 2a (No GFM BESS) | $ | 241085549.2081 | 0 | 0 | 0 | 0 | 0 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314 | 31917547.6314
| Accelerated Portfolio option 3a (No GFM BESS) | $ | 361628323.8122 | 0 | 0 | 0 | 0 | 0 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471 | 47876321.4471
| Accelerated Portfolio option 4a (No GFM BESS) | $ | 482171098.4163 | 0 | 0 | 0 | 0 | 0 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627 | 63835095.2627
| Accelerated Portfolio option 5a (No GFM BESS) | $ | 602713873.0204 | 0 | 0 | 0 | 0 | 0 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784
Grid-forming BESS included. Net present value calculation
| Net present value for each portfolio |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Portfolio name | Units | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 3b - assumed timing | $ | 37515017748.432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -912480.328 | 7269053956.2956 | 4463670651.924 | 4464277445.3965 | 4464195412.6118 | 4466119804.2136 | 4467554910.6949 | 4469679948.1524 | 8635672632.1357 | 8635672632.1357 | 8635672632.1357 | 8635672632.1357 | 8635672632.1357 | 8635672632.1357 | 8635672632.1357 | 8635672632.1357 | 8635672632.1357 | 8635672632.1357
| Portfolio option 4b - assumed timing | $ | 37444933711.2451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1750032.9226 | 7256535819.7675 | 4451087616.9318 | 4451694410.4043 | 4451612377.6196 | 4453536769.2214 | 4454971875.7027 | 4457096913.1602 | 8623023383.6142 | 8623023383.6142 | 8623023383.6142 | 8623023383.6142 | 8623023383.6142 | 8623023383.6142 | 8623023383.6142 | 8623023383.6142 | 8623023383.6142 | 8623023383.6142
| Portfolio option 5b - assumed timing | $ | 37365375627.8794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7242356082.2537 | 4437139659.647 | 4437746453.1195 | 4437664420.3348 | 4439588811.9367 | 4441023918.418 | 4443148955.8755 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758
| Portfolio option 3b - accelerated timing | $ | 37957043245.9905 | 0 | 0 | 0 | 0 | 0 | 250960523.7742 | 231595031.3731 | 223438233.4719 | 7269053956.2956 | 4463670651.924 | 4464277445.3965 | 4464195412.6118 | 4466119804.2136 | 4467554910.6949 | 4469679948.1524 | 8635672632.1357 | 8635672632.1357 | 8635672632.1357 | 8635672632.1357 | 8635672632.1357 | 8635672632.1357 | 8635672632.1357 | 8635672632.1357 | 8635672632.1357 | 8635672632.1357
| Portfolio option 4b - accelerated timing | $ | 37857548008.0256 | 0 | 0 | 0 | 0 | 0 | 235001749.9586 | 215636257.5575 | 210913916.1378 | 7256535819.7675 | 4451087616.9318 | 4451694410.4043 | 4451612377.6196 | 4453536769.2214 | 4454971875.7027 | 4457096913.1602 | 8623023383.6142 | 8623023383.6142 | 8623023383.6142 | 8623023383.6142 | 8623023383.6142 | 8623023383.6142 | 8623023383.6142 | 8623023383.6142 | 8623023383.6142 | 8623023383.6142
| Portfolio option 5b - accelerated timing | $ | 37750147423.4582 | 0 | 0 | 0 | 0 | 0 | 219042976.1429 | 199677483.7418 | 196672370.5628 | 7242356082.2537 | 4437139659.647 | 4437746453.1195 | 4437664420.3348 | 4439588811.9367 | 4441023918.418 | 4443148955.8755 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758 | 8609406493.9758
Present value of market benefits for each portfolio
| Portfolio name | Units | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 3b - assumed timing | $ | 37819336302.489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4239204.3943 | 7322081962.4649 | 4516698658.0933 | 4517305451.5658 | 4517223418.7811 | 4519147810.383 | 4520582916.8643 | 4522707954.3218 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305
| Portfolio option 4b - assumed timing | $ | 37818420116.7764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3467261.1633 | 7322088143.271 | 4516639940.4353 | 4517246733.9078 | 4517164701.1231 | 4519089092.7249 | 4520524199.2062 | 4522649236.6637 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177
| Portfolio option 5b - assumed timing | $ | 37818787107.0665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7322149951.3321 | 4516933528.7255 | 4517540322.198 | 4517458289.4132 | 4519382681.0151 | 4520817787.4964 | 4522942824.9539 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542
| Portfolio option 3b - accelerated timing | $ | 38350943236.3475 | 0 | 0 | 0 | 0 | 0 | 298836845.2213 | 279471352.8202 | 276466239.6413 | 7322081962.4649 | 4516698658.0933 | 4517305451.5658 | 4517223418.7811 | 4519147810.383 | 4520582916.8643 | 4522707954.3218 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305
| Portfolio option 4b - accelerated timing | $ | 38350476328.6235 | 0 | 0 | 0 | 0 | 0 | 298836845.2213 | 279471352.8202 | 276466239.6413 | 7322088143.271 | 4516639940.4353 | 4517246733.9078 | 4517164701.1231 | 4519089092.7249 | 4520524199.2062 | 4522649236.6637 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177
| Portfolio option 5b - accelerated timing | $ | 38352861296.4785 | 0 | 0 | 0 | 0 | 0 | 298836845.2213 | 279471352.8202 | 276466239.6413 | 7322149951.3321 | 4516933528.7255 | 4517540322.198 | 4517458289.4132 | 4519382681.0151 | 4520817787.4964 | 4522942824.9539 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542
Present value of costs for each portfolio
| Portfolio name | Units | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 3b - assumed timing | $ | 304318554.057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5151684.7223 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693
| Portfolio option 4b - assumed timing | $ | 373486405.5312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1717228.2408 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035
| Portfolio option 5b - assumed timing | $ | 453411479.1871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784
| Portfolio option 3b - accelerated timing | $ | 393899990.357 | 0 | 0 | 0 | 0 | 0 | 47876321.4471 | 47876321.4471 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693 | 53028006.1693
| Portfolio option 4b - accelerated timing | $ | 492928320.5979 | 0 | 0 | 0 | 0 | 0 | 63835095.2627 | 63835095.2627 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035 | 65552323.5035
| Portfolio option 5b - accelerated timing | $ | 602713873.0204 | 0 | 0 | 0 | 0 | 0 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784 | 79793869.0784
High synchronous condenser cost sensitivity. Net present value calculation
| Net present value for each portfolio |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Portfolio name | Units | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 3b - assumed timing | $ | 37406198993.4271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -912480.328 | 7249903427.7167 | 4444520123.3452 | 4445126916.8177 | 4445044884.033 | 4446969275.6348 | 4448404382.1161 | 4450529419.5736 | 8616522103.5569 | 8616522103.5569 | 8616522103.5569 | 8616522103.5569 | 8616522103.5569 | 8616522103.5569 | 8616522103.5569 | 8616522103.5569 | 8616522103.5569 | 8616522103.5569
| Portfolio option 4b - assumed timing | $ | 37299842037.9053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1750032.9226 | 7231001781.6624 | 4425553578.8267 | 4426160372.2992 | 4426078339.5145 | 4428002731.1164 | 4429437837.5976 | 4431562875.0552 | 8597489345.5091 | 8597489345.5091 | 8597489345.5091 | 8597489345.5091 | 8597489345.5091 | 8597489345.5091 | 8597489345.5091 | 8597489345.5091 | 8597489345.5091 | 8597489345.5091
| Portfolio option 5b - assumed timing | $ | 37184011036.2046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7210438534.6223 | 4405222112.0157 | 4405828905.4882 | 4405746872.7034 | 4407671264.3053 | 4409106370.7866 | 4411231408.2441 | 8577488946.3444 | 8577488946.3444 | 8577488946.3444 | 8577488946.3444 | 8577488946.3444 | 8577488946.3444 | 8577488946.3444 | 8577488946.3444 | 8577488946.3444 | 8577488946.3444
| Portfolio option 3b - accelerated timing | $ | 37812391916.4656 | 0 | 0 | 0 | 0 | 0 | 231809995.1954 | 212444502.7943 | 204287704.8931 | 7249903427.7167 | 4444520123.3452 | 4445126916.8177 | 4445044884.033 | 4446969275.6348 | 4448404382.1161 | 4450529419.5736 | 8616522103.5569 | 8616522103.5569 | 8616522103.5569 | 8616522103.5569 | 8616522103.5569 | 8616522103.5569 | 8616522103.5569 | 8616522103.5569 | 8616522103.5569 | 8616522103.5569
| Portfolio option 4b - accelerated timing | $ | 37664679568.6591 | 0 | 0 | 0 | 0 | 0 | 209467711.8535 | 190102219.4524 | 185379878.0327 | 7231001781.6624 | 4425553578.8267 | 4426160372.2992 | 4426078339.5145 | 4428002731.1164 | 4429437837.5976 | 4431562875.0552 | 8597489345.5091 | 8597489345.5091 | 8597489345.5091 | 8597489345.5091 | 8597489345.5091 | 8597489345.5091 | 8597489345.5091 | 8597489345.5091 | 8597489345.5091 | 8597489345.5091
| Portfolio option 5b - accelerated timing | $ | 37509061874.25 | 0 | 0 | 0 | 0 | 0 | 187125428.5115 | 167759936.1104 | 164754822.9315 | 7210438534.6223 | 4405222112.0157 | 4405828905.4882 | 4405746872.7034 | 4407671264.3053 | 4409106370.7866 | 4411231408.2441 | 8577488946.3444 | 8577488946.3444 | 8577488946.3444 | 8577488946.3444 | 8577488946.3444 | 8577488946.3444 | 8577488946.3444 | 8577488946.3444 | 8577488946.3444 | 8577488946.3444
Present value of market benefits for each portfolio
| Portfolio name | Units | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 3b - assumed timing | $ | 37819336302.489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4239204.3943 | 7322081962.4649 | 4516698658.0933 | 4517305451.5658 | 4517223418.7811 | 4519147810.383 | 4520582916.8643 | 4522707954.3218 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305
| Portfolio option 4b - assumed timing | $ | 37818420116.7764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3467261.1633 | 7322088143.271 | 4516639940.4353 | 4517246733.9078 | 4517164701.1231 | 4519089092.7249 | 4520524199.2062 | 4522649236.6637 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177
| Portfolio option 5b - assumed timing | $ | 37818787107.0665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7322149951.3321 | 4516933528.7255 | 4517540322.198 | 4517458289.4132 | 4519382681.0151 | 4520817787.4964 | 4522942824.9539 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542
| Portfolio option 3b - accelerated timing | $ | 38350943236.3475 | 0 | 0 | 0 | 0 | 0 | 298836845.2213 | 279471352.8202 | 276466239.6413 | 7322081962.4649 | 4516698658.0933 | 4517305451.5658 | 4517223418.7811 | 4519147810.383 | 4520582916.8643 | 4522707954.3218 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305
| Portfolio option 4b - accelerated timing | $ | 38350476328.6235 | 0 | 0 | 0 | 0 | 0 | 298836845.2213 | 279471352.8202 | 276466239.6413 | 7322088143.271 | 4516639940.4353 | 4517246733.9078 | 4517164701.1231 | 4519089092.7249 | 4520524199.2062 | 4522649236.6637 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177
| Portfolio option 5b - accelerated timing | $ | 38352861296.4785 | 0 | 0 | 0 | 0 | 0 | 298836845.2213 | 279471352.8202 | 276466239.6413 | 7322149951.3321 | 4516933528.7255 | 4517540322.198 | 4517458289.4132 | 4519382681.0151 | 4520817787.4964 | 4522942824.9539 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542
Present value of costs for each portfolio
| Portfolio name | Units | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 3b - assumed timing | $ | 413137309.0619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5151684.7223 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481
| Portfolio option 4b - assumed timing | $ | 518578078.8711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1717228.2408 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086
| Portfolio option 5b - assumed timing | $ | 634776070.8619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098
| Portfolio option 3b - accelerated timing | $ | 538551319.8819 | 0 | 0 | 0 | 0 | 0 | 67026850.0259 | 67026850.0259 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481 | 72178534.7481
| Portfolio option 4b - accelerated timing | $ | 685796759.9644 | 0 | 0 | 0 | 0 | 0 | 89369133.3678 | 89369133.3678 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086 | 91086361.6086
| Portfolio option 5b - accelerated timing | $ | 843799422.2285 | 0 | 0 | 0 | 0 | 0 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098 | 111711416.7098
Low synchronous condenser cost sensitivity. Net present value calculation
| Net present value for each portfolio |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Portfolio name | Units | NPV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 3b - assumed timing | $ | 37596631814.6857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -912480.328 | 7283416852.7297 | 4478033548.3581 | 4478640341.8306 | 4478558309.0459 | 4480482700.6478 | 4481917807.129 | 4484042844.5866 | 8650035528.5698 | 8650035528.5698 | 8650035528.5698 | 8650035528.5698 | 8650035528.5698 | 8650035528.5698 | 8650035528.5698 | 8650035528.5698 | 8650035528.5698 | 8650035528.5698
| Portfolio option 4b - assumed timing | $ | 37553752466.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1750032.9226 | 7275686348.3463 | 4470238145.5106 | 4470844938.9831 | 4470762906.1984 | 4472687297.8003 | 4474122404.2816 | 4476247441.7391 | 8642173912.1931 | 8642173912.1931 | 8642173912.1931 | 8642173912.1931 | 8642173912.1931 | 8642173912.1931 | 8642173912.1931 | 8642173912.1931 | 8642173912.1931 | 8642173912.1931
| Portfolio option 5b - assumed timing | $ | 37501399071.6355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7266294242.9772 | 4461077820.3706 | 4461684613.8431 | 4461602581.0583 | 4463526972.6602 | 4464962079.1415 | 4467087116.599 | 8633344654.6993 | 8633344654.6993 | 8633344654.6993 | 8633344654.6993 | 8633344654.6993 | 8633344654.6993 | 8633344654.6993 | 8633344654.6993 | 8633344654.6993 | 8633344654.6993
| Portfolio option 3b - accelerated timing | $ | 38065531743.1342 | 0 | 0 | 0 | 0 | 0 | 265323420.2084 | 245957927.8073 | 237801129.906 | 7283416852.7297 | 4478033548.3581 | 4478640341.8306 | 4478558309.0459 | 4480482700.6478 | 4481917807.129 | 4484042844.5866 | 8650035528.5698 | 8650035528.5698 | 8650035528.5698 | 8650035528.5698 | 8650035528.5698 | 8650035528.5698 | 8650035528.5698 | 8650035528.5698 | 8650035528.5698 | 8650035528.5698
| Portfolio option 4b - accelerated timing | $ | 38002199337.5505 | 0 | 0 | 0 | 0 | 0 | 254152278.5374 | 234786786.1363 | 230064444.7166 | 7275686348.3463 | 4470238145.5106 | 4470844938.9831 | 4470762906.1984 | 4472687297.8003 | 4474122404.2816 | 4476247441.7391 | 8642173912.1931 | 8642173912.1931 | 8642173912.1931 | 8642173912.1931 | 8642173912.1931 | 8642173912.1931 | 8642173912.1931 | 8642173912.1931 | 8642173912.1931 | 8642173912.1931
| Portfolio option 5b - accelerated timing | $ | 37930961585.3643 | 0 | 0 | 0 | 0 | 0 | 242981136.8664 | 223615644.4653 | 220610531.2864 | 7266294242.9772 | 4461077820.3706 | 4461684613.8431 | 4461602581.0583 | 4463526972.6602 | 4464962079.1415 | 4467087116.599 | 8633344654.6993 | 8633344654.6993 | 8633344654.6993 | 8633344654.6993 | 8633344654.6993 | 8633344654.6993 | 8633344654.6993 | 8633344654.6993 | 8633344654.6993 | 8633344654.6993
Present value of market benefits for each portfolio
| Portfolio name | Units | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 3b - assumed timing | $ | 37819336302.489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4239204.3943 | 7322081962.4649 | 4516698658.0933 | 4517305451.5658 | 4517223418.7811 | 4519147810.383 | 4520582916.8643 | 4522707954.3218 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305
| Portfolio option 4b - assumed timing | $ | 37818420116.7764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3467261.1633 | 7322088143.271 | 4516639940.4353 | 4517246733.9078 | 4517164701.1231 | 4519089092.7249 | 4520524199.2062 | 4522649236.6637 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177
| Portfolio option 5b - assumed timing | $ | 37818787107.0665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7322149951.3321 | 4516933528.7255 | 4517540322.198 | 4517458289.4132 | 4519382681.0151 | 4520817787.4964 | 4522942824.9539 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542
| Portfolio option 3b - accelerated timing | $ | 38350943236.3475 | 0 | 0 | 0 | 0 | 0 | 298836845.2213 | 279471352.8202 | 276466239.6413 | 7322081962.4649 | 4516698658.0933 | 4517305451.5658 | 4517223418.7811 | 4519147810.383 | 4520582916.8643 | 4522707954.3218 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305 | 8688700638.305
| Portfolio option 4b - accelerated timing | $ | 38350476328.6235 | 0 | 0 | 0 | 0 | 0 | 298836845.2213 | 279471352.8202 | 276466239.6413 | 7322088143.271 | 4516639940.4353 | 4517246733.9078 | 4517164701.1231 | 4519089092.7249 | 4520524199.2062 | 4522649236.6637 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177 | 8688575707.1177
| Portfolio option 5b - accelerated timing | $ | 38352861296.4785 | 0 | 0 | 0 | 0 | 0 | 298836845.2213 | 279471352.8202 | 276466239.6413 | 7322149951.3321 | 4516933528.7255 | 4517540322.198 | 4517458289.4132 | 4519382681.0151 | 4520817787.4964 | 4522942824.9539 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542 | 8689200363.0542
Present value of costs for each portfolio
| Portfolio name | Units | PV | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
| Portfolio option 3b - assumed timing | $ | 222704487.8033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5151684.7223 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352
| Portfolio option 4b - assumed timing | $ | 264667650.5264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1717228.2408 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247
| Portfolio option 5b - assumed timing | $ | 317388035.4309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549
| Portfolio option 3b - accelerated timing | $ | 285411493.2133 | 0 | 0 | 0 | 0 | 0 | 33513425.0129 | 33513425.0129 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352 | 38665109.7352
| Portfolio option 4b - accelerated timing | $ | 348276991.073 | 0 | 0 | 0 | 0 | 0 | 44684566.6839 | 44684566.6839 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247 | 46401794.9247
| Portfolio option 5b - accelerated timing | $ | 421899711.1143 | 0 | 0 | 0 | 0 | 0 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549 | 55855708.3549