## Wellington North SF
Generator name | Capacity (MW) | (1) Ancillary service requirements | (2) Level and pattern of network congestion | (3) Impact on timing of expenditure on the network | (4) Impact on interconnector power transfer capability
Wellington North Solar Farm | 330 | There were no new ancillary service contracts in Central West NSW in the 12 months prior to, or following, the commissioning of the Wellington North SF. | The connection of Wellington North SF in September 2024 has increased the generation capacity in Central West NSW. When Wellington North SF is generating, it has the potential to influence power flows on the Central West NSW transmission network, including the Molong to Orange North (94T) 132 kV line and surrounding 132 kV and 330 kV network elements. In the 12 months prior to the energisation of Wellington North SF, constraint equations associated with the Molong-Orange North 132 kV line (94T , 947, 94K) bound for approximately 1,961 hours. In the 12 months following energisation, the same set of constraint equations bound for approximately 2,357.67 hours. This indicates that congestion on the 94T corridor increased following connection, however, the corridor was already subject to significant congestion prior to the solar farm's connection. In the 12 months prior to energisation, constraint equations associated with the loss of either Bayswater-Liddell 330 kV line (33 or 34) where Welington North Sf has a positive coefficient bound for approximately 259.3 hours. In the 12 months following energisation, the same constraint equations bound for approximately 188.25 hours, indicating decreased congestion under these outage conditions following the energisation of Wellington North SF. However, there are many factors that impact on the Molong-orange North lines and lines 33/34 overloading constraint equations: - the relative operation of the existing generating units in Central NSW - NEM dispatch price in NSW. - network outages (planned and unplanned) significantly impact the power transfer limits. These factors generally have a greater influence on network utilisation than the output of any individual solar farm. Constraint outcomes in NEMDE reflect the combined impact of many generators and network conditions and therefore cannot be attributed solely to a single generating unit. Wellington North SF has had a material influence on power flows within the Parkes, Wellington, Molong and Orange network area. However, congestion on the surrounding 132 kV network is managed through NEMDE constraint equations and associated network operating procedures. Wellington North SF is included in a Low Short Circuit Ratio (SCR) scheme used to manage system strength and voltage stability under specific network outage conditions. Under these conditions, limits may be applied to the number of inverters operating online to maintain system security. | No project timings have been affected by the inclusion of the Wellington North SF. | The Wellington North SF has a small impact on power transfer capability between Queensland and NSW and vice versa via the power flows to the Liddell - Bayswater lines 33/34.
Note on D1: Dragana Hele: Compare it with constraint spreadsheet