## Rye Park Wind Farm
Generator name | Capacity (MW) | (1) Ancillary service requirements | (2) Level and pattern of network congestion | (3) Impact on timing of expenditure on the network | (4) Impact on interconnector power transfer capability
Rye Park Wind Farm | 384 | There were no new ancillary service contracts in Southern NSW in the 12 months prior to, or following, the commissioning of the Rye Park Wind Farm. | The connection of Rye Park WF in October 2024 has increased the generation capacity in Southern NSW. On outage of one of 330 kV lines 3J, 3H, 3L, 3M, 3P, 4, 5, 6, 35, 36 and 61, Rye Park WF output may be constrained. Transfer capability between Snowy - NSW, Yass/Canberra and Bannaby/Marulan can be constrained during outages of parallel 330 kV lines in the vicinity. In the 12 months prior to the connection of Rye Park WF, the constraint equation managing the overloading of the collector-Marulan 330kV line 4 folllowing the trip of Line 61 constrained for approximately 0.9 hours and in the 12 months following for approx 13.75 hours.This indicates that the underlying network condition occurs only occasionally and does not, in isolation, demonstrate a material increase in transmission congestion attributable to Rye Park WF. In the 12 months post connection a constraint equation was introduced to manage the the post contingent loading of the Yass to Collector line 3L, following the trip of the Yass to Marulan Line 5. Rye park WF has a relatively high participation factor, where the constraint was not binding 12 months prior to Rye parks connection and was binding for apporxiamtely 4.83 hours in the following 12 month period. Howver, there are many factors that impact the operation of the surrounding line constraint equations including: - the relative operation of the existing generating units in NSW - NEM dispatch price in NSW and VIC - network outages (planned and unplanned) significantly impact the power transfer limits. All of the above have a far greater impact on the utilisation of Southern NSW network compared to a connection of any single renewable generator in Southern NSW. The constraints in the NEM dispatch system can also not specifically by attributed to any single generator. Therefore, it cannot be said that the connection of Rye Park WF has specifically had a material impact on network congestion in the main 330 kV system network, however it is a contributing factor. | No project timings have been affected by the inclusion of the Rye Park WF. | The Rye Park WF has a small impact on power transfer capability between Victoria and NSW and vice versa.