## Sunraysia SF
Generator name | Capacity (MW) | (1) Ancillary service requirements | (2) Level and pattern of network congestion | (3) Impact on timing of expenditure on the network | (4) Impact on interconnector power transfer capability
Crudine Ridge WF | 138 | There were no new ancillary service contracts in Central NSW in the 12 months prior to, or following, the commissioning of the Crudine Ridge WF. | The connection of Crudine Ridge WF has increased the generation capacity in Central NSW. When Crudine Ridge WF is generating, it has the potential to increase the utilisation of surrounding Central NSW 132kV network lines (e.g. 9ML/1 Crudine Ridge to Ilford, 94M/2 Crudine Ridge to Mudgee, 9ML/3 Crudine Ridge to Mount Piper, 94B Wellington to Beryl). In the 12 months prior to the connection of Crudine Ridge WF, the constraint equation for avoiding overloading on 94B/1 on trip of 9ML constrained for approximately 0 hours, and in the 12 months following for approx 88.7 hours. There are many factors that impact 94B/1 overloading constraint equation: - the relative operation of the existing generating units in Central NSW - NEM dispatch price in NSW. - Load levl in central-west NSW. - network outages (planned and unplanned) significantly impact the power transfer limits. All of the above have a far greater impact on the utilisation of Central NSW network, compared to a connection of any single WF in Central West NSW. The constraints in the NEM dispatch system, can also not specifically by attributed to any single generator. Connection of Crudine Ridge WF has had a material impact on network congestion in the main 132 kV system network between Mount Piper, Beryl, and Wellington. If output of Crudine Ridge WF is close to its installed capacity, all the surrounding lines in the 132 kV network will be loaded above their contingency rating. Possible congestion of the 132 kV lines surrounding Crudine Ridge WF is managed by constraint equation in NEMDE and the following transfer tripping schemes: - Anti-islanding scheme addressing trip of 132 kV lines 94B and 94M. - Runback schemes to prevent overloads of lines 94B, 94M and 9ML in the event of changed system conditions or network contingency. | No project timings have been affected by the inclusion of Crudine Ridge WF. | Crudine Ridge WF has positive contribution factor in constraint equation for overloading of line 94B/1, which means it will increase loading on this line. Crudine Ridge WF is in Central area of NSW and does not have direct influence on either Victoria or Queensland interconnector power capability.
Note on D1: Dragana Hele: Compare it with constraint spreadsheet
Note on D2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Check constraint with Gang
Note on F2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Check with Gang for contribution factor and constraint line