## Bango WF
Generator name | Capacity (MW) | (1) Ancillary service requirements | (2) Level and pattern of network congestion | (3) Impact on timing of expenditure on the network | (4) Impact on interconnector power transfer capability
Bango 973 & Bango 999 | 155 + 83 | There were no new ancillary service contracts in Central NSW in the 12 months prior to, or following, the commissioning of the Bango WF. | The connection of Bango WF has increased the generation capacity in Central NSW. When Bango WF is generating, it has the potential to increase the utilisation of surrounding Central NSW 132kV network lines (e.g. 973 Bango to Cowra, 999 Bango to Cowra, 9GL Bango to Yass, 9GM Bango to Yass). In the 12 months prior to the connection of Bango WF, the constraint equation for avoiding overloading on 9GL on Nil trip constrained for approximately 1.1 hours, and in the 12 months following for approx 16.6 hours. There are other constraint equations on lines 999, 9GM and 973 with an increase in binding hours (lower than the 9GL constraint) following the connection of Bango WF. There are many factors that impact 9GL overloading constraint equation: - Low line rating - the relative operation of the existing generating units in Central NSW - NEM dispatch price in NSW. - Load level in central-west NSW. - network outages (planned and unplanned) significantly impact the power transfer limits. All of the above have a far greater impact on the utilisation of Central NSW network, compared to a connection of any single WF in Central West NSW. The constraints in the NEM dispatch system, can also not specifically by attributed to any single generator. Connection of Bango WF has had a material impact on network congestion in the main 132 kV system network between Yass, Cowra and Forbes. If output of Bango WF is close to its installed capacity, some of the surrounding lines in the 132 kV network will be loaded above their contingency rating. Possible congestion of the 132 kV lines surrounding Bango WF is managed by constraint equation in NEMDE and the following transfer tripping schemes: - Transfer Tripping Scheme. - Runback schemes to prevent overloads of lines 973, 9GL and Yass No.1 and No.2 transformers in the event of changed system conditions or network contingency. | No project timings have been affected by the inclusion of Bango WF. | Bango WF has positive contribution factor in constraint equation for overloading of lines 9GL, 999, 9GM and 973 which means it will increase loading on this line. Bango WF is in Central area of NSW and does not have direct influence on either Victoria or Queensland interconnector power capability.
Note on D1: Dragana Hele: Compare it with constraint spreadsheet